## README
Simulated Polar Research Station Energy Dataset
SIH 26061 — AI-Driven Smart Energy Management System for Polar Research Stations
IMPORTANT — read before using
No public dataset publishes hour-by-hour power/load/fuel data for an actual polar research station. This workbook is a SYNTHETIC dataset, generated with a physics-based model (solar geometry, wind power curve, heating-degree load model, battery dispatch, diesel fuel curve) calibrated to published climate and station-energy literature for an East-Antarctic coastal station (comparable to Maitri/Bharati, ~70.75S). Use it to design, train, and demo your forecasting/optimization models — but say so explicitly in your SIH submission and cite this as simulated data, not measured station telemetry.
Model assumptions & station specs
Assumed location | ~70.75S (East Antarctic coastal station climate profile)
Simulation period | 1 Jan 2025 - 31 Dec 2025, hourly (8,760 rows)
Installed solar PV capacity | 60 kW
Installed wind capacity | 120 kW
Battery bank capacity | 250 kWh usable (15%-95% SOC operating band)
Battery round-trip efficiency | 92%
Diesel generator capacity | 150 kW
Diesel specific fuel consumption | ~0.32 L/kWh, worse at part-load (<30% load factor)
Base electrical load | 35 kW (comms, lighting, instruments, life support)
Heating load model | +1 kW per degree C below 0C, capped at 90 kW
Dispatch priority | Renewables -> Battery -> Diesel backup (mirrors your solution's stated logic)
Wind turbine power curve | Cut-in 3.5 m/s, rated 13 m/s, cut-out (safety shutdown) 28 m/s
Solar model | PV area implied by installed kW at STC (18% panel efficiency), snow/frost derate below -18C
Random seed | NumPy Generator seed=42 (reproducible if you regenerate)
Sheets in this workbook
Hourly_Data | The full 8,760-row simulated time series — your main ML training table.
Monthly_Summary | Auto-computed monthly averages/totals (live formulas pulling from Hourly_Data).
Data_Dictionary | Column-by-column definitions and units.

## Hourly_Data
Timestamp | Day_of_Year | Month | Season | Hour | Daylight_Hours | Temperature_C | Wind_Speed_mps | Cloud_Cover_pct | Solar_Irradiance_Wm2 | Solar_Generation_kW | Wind_Generation_kW | Total_Renewable_kW | Heating_Load_kW | Total_Load_kW | Battery_SOC_pct | Battery_Charge_Discharge_kW | Diesel_Generation_kW | Fuel_Consumption_L | Energy_Deficit_kW | System_Status
2025-01-01 | 1 | 1 | Summer | 0 | 24 | 0.1 | 14.4 | 15.5 | 0 | 0 | 120 | 120 | 0 | 45 | 92.6 | 75 | 0 | 0 | 0 | Normal
2025-01-01 01:00 | 1 | 1 | Summer | 1 | 24 | -3.2 | 12.28 | 52.8 | 51.7 | 3.1 | 94.73 | 97.83 | 3.2 | 45 | 95 | 6.52 | 0 | 0 | 0 | Normal
2025-01-01 02:00 | 1 | 1 | Summer | 2 | 24 | 0.3 | 14.33 | 54.5 | 100.4 | 6.02 | 120 | 126.02 | 0 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-01-01 03:00 | 1 | 1 | Summer | 3 | 24 | 0.3 | 8.67 | 20.5 | 212.4 | 12.74 | 19.34 | 32.08 | 0 | 45 | 89.83 | -12.92 | 0 | 0 | 0 | Battery-supported
2025-01-01 04:00 | 1 | 1 | Summer | 4 | 24 | -6.4 | 4.85 | 31.8 | 249.7 | 14.98 | 0.34 | 15.32 | 6.4 | 45 | 77.96 | -29.68 | 0 | 0 | 0 | Battery-supported
2025-01-01 05:00 | 1 | 1 | Summer | 5 | 24 | -5.3 | 5.06 | 27.1 | 318.1 | 19.09 | 0.53 | 19.62 | 5.3 | 45.59 | 67.57 | -25.97 | 0 | 0 | 0 | Battery-supported
2025-01-01 06:00 | 1 | 1 | Summer | 6 | 24 | -2.4 | 5.92 | 26.6 | 371.3 | 22.28 | 1.98 | 24.26 | 2.4 | 45 | 59.28 | -20.74 | 0 | 0 | 0 | Battery-supported
2025-01-01 07:00 | 1 | 1 | Summer | 7 | 24 | -3.5 | 1.91 | 79.7 | 209.3 | 12.56 | 0 | 12.56 | 3.5 | 45 | 46.3 | -32.44 | 0 | 0 | 0 | Battery-supported
2025-01-01 08:00 | 1 | 1 | Summer | 8 | 24 | -2.9 | 9.59 | 47.9 | 364 | 21.84 | 31.61 | 53.45 | 2.9 | 46.95 | 48.69 | 6.5 | 0 | 0 | 0 | Normal
2025-01-01 09:00 | 1 | 1 | Summer | 9 | 24 | -4.7 | 8.03 | 40.3 | 422.9 | 25.37 | 13.01 | 38.38 | 4.7 | 45 | 46.04 | -6.62 | 0 | 0 | 0 | Battery-supported
2025-01-01 10:00 | 1 | 1 | Summer | 10 | 24 | -0.7 | 6.46 | 63 | 334.5 | 20.07 | 3.63 | 23.7 | 0.7 | 45 | 37.52 | -21.3 | 0 | 0 | 0 | Battery-supported
2025-01-01 11:00 | 1 | 1 | Summer | 11 | 24 | -0.7 | 7.39 | 30.1 | 503.3 | 30.2 | 8.24 | 38.44 | 0.7 | 52.16 | 32.04 | -13.72 | 0 | 0 | 0 | Battery-supported
2025-01-01 12:00 | 1 | 1 | Summer | 12 | 24 | -2 | 5.47 | 95.5 | 185.9 | 11.15 | 1.07 | 12.22 | 2 | 47.25 | 18.02 | -35.03 | 0 | 0 | 0 | Battery-supported
2025-01-01 13:00 | 1 | 1 | Summer | 13 | 24 | 0.7 | 15.98 | 40.3 | 453.8 | 27.23 | 120 | 147.23 | 0 | 53.68 | 52.45 | 93.55 | 0 | 0 | 0 | Normal
2025-01-01 14:00 | 1 | 1 | Summer | 14 | 24 | -0.3 | 2.53 | 77.2 | 266.7 | 16 | 0 | 16 | 0.3 | 45 | 40.85 | -29 | 0 | 0 | 0 | Battery-supported
2025-01-01 15:00 | 1 | 1 | Summer | 15 | 24 | -2.8 | 2.12 | 38.1 | 432.7 | 25.96 | 0 | 25.96 | 2.8 | 54.14 | 29.58 | -28.18 | 0 | 0 | 0 | Battery-supported
2025-01-01 16:00 | 1 | 1 | Summer | 16 | 24 | 0.2 | 11.81 | 78.8 | 232.2 | 13.93 | 80.32 | 94.25 | 0 | 45 | 47.7 | 49.25 | 0 | 0 | 0 | Normal
2025-01-01 17:00 | 1 | 1 | Summer | 17 | 24 | -2.4 | 7.42 | 40.3 | 363 | 21.78 | 8.43 | 30.21 | 2.4 | 48.98 | 40.19 | -18.77 | 0 | 0 | 0 | Battery-supported
2025-01-01 18:00 | 1 | 1 | Summer | 18 | 24 | 1.9 | 13.04 | 44.9 | 307.7 | 18.46 | 120 | 138.46 | 0 | 45 | 74.59 | 93.46 | 0 | 0 | 0 | Normal
2025-01-01 19:00 | 1 | 1 | Summer | 19 | 24 | 0 | 8.78 | 68.1 | 195.4 | 11.72 | 20.6 | 32.32 | 0 | 45 | 69.52 | -12.68 | 0 | 0 | 0 | Battery-supported
2025-01-01 20:00 | 1 | 1 | Summer | 20 | 24 | -0.3 | 10.39 | 14.7 | 291.9 | 17.51 | 45.78 | 63.29 | 0.3 | 45 | 76.25 | 18.29 | 0 | 0 | 0 | Normal
2025-01-01 21:00 | 1 | 1 | Summer | 21 | 24 | -1.4 | 5.96 | 60.8 | 136.5 | 8.19 | 2.08 | 10.27 | 1.4 | 45 | 62.35 | -34.73 | 0 | 0 | 0 | Battery-supported
2025-01-01 22:00 | 1 | 1 | Summer | 22 | 24 | 2.6 | 12.54 | 54.2 | 100.8 | 6.05 | 103.4 | 109.45 | 0 | 45 | 86.07 | 64.45 | 0 | 0 | 0 | Normal
2025-01-01 23:00 | 1 | 1 | Summer | 23 | 24 | -0.6 | 4.08 | 38.5 | 60.9 | 3.65 | 0.03 | 3.68 | 0.6 | 45 | 69.54 | -41.32 | 0 | 0 | 0 | Battery-supported
2025-01-02 | 2 | 1 | Summer | 0 | 24 | -1.5 | 8.26 | 58.7 | 0 | 0 | 15.09 | 15.09 | 1.5 | 45 | 57.58 | -29.91 | 0 | 0 | 0 | Battery-supported
2025-01-02 01:00 | 2 | 1 | Summer | 1 | 24 | -1.7 | 4.79 | 42.8 | 58.1 | 3.49 | 0.3 | 3.79 | 1.7 | 45 | 41.1 | -41.21 | 0 | 0 | 0 | Battery-supported
2025-01-02 02:00 | 2 | 1 | Summer | 2 | 24 | -0.1 | 8.6 | 48.6 | 107.8 | 6.47 | 18.57 | 25.04 | 0.1 | 45 | 33.11 | -19.96 | 0 | 0 | 0 | Battery-supported
2025-01-02 03:00 | 2 | 1 | Summer | 3 | 24 | -0.9 | 16.85 | 74.2 | 111.4 | 6.68 | 120 | 126.68 | 0.9 | 45 | 63.17 | 81.68 | 0 | 0 | 0 | Normal
2025-01-02 04:00 | 2 | 1 | Summer | 4 | 24 | -1.1 | 6.35 | 33.3 | 245.9 | 14.75 | 3.24 | 17.99 | 1.1 | 45 | 52.37 | -27.01 | 0 | 0 | 0 | Battery-supported
2025-01-02 05:00 | 2 | 1 | Summer | 5 | 24 | -1.4 | 6.03 | 63.6 | 208.7 | 12.52 | 2.27 | 14.79 | 1.4 | 45 | 40.28 | -30.21 | 0 | 0 | 0 | Battery-supported
2025-01-02 06:00 | 2 | 1 | Summer | 6 | 24 | 2.1 | 10.28 | 98 | 122.8 | 7.37 | 43.62 | 50.99 | 0 | 45 | 42.49 | 5.99 | 0 | 0 | 0 | Normal
2025-01-02 07:00 | 2 | 1 | Summer | 7 | 24 | -3.6 | 5.64 | 66.7 | 260.2 | 15.61 | 1.37 | 16.98 | 3.6 | 45 | 31.28 | -28.02 | 0 | 0 | 0 | Battery-supported
2025-01-02 08:00 | 2 | 1 | Summer | 8 | 24 | -3.9 | 10.35 | 43.9 | 381.1 | 22.87 | 44.99 | 67.86 | 3.9 | 45.31 | 39.58 | 22.55 | 0 | 0 | 0 | Normal
2025-01-02 09:00 | 2 | 1 | Summer | 9 | 24 | -4.5 | 7.59 | 79.7 | 243.9 | 14.63 | 9.58 | 24.21 | 4.5 | 45 | 31.26 | -20.79 | 0 | 0 | 0 | Battery-supported
2025-01-02 10:00 | 2 | 1 | Summer | 10 | 24 | -1.2 | 1.73 | 53.7 | 378.3 | 22.7 | 0 | 22.7 | 1.2 | 47.94 | 21.16 | -25.24 | 0 | 0 | 0 | Battery-supported
2025-01-02 11:00 | 2 | 1 | Summer | 11 | 24 | 0.1 | 1.91 | 61.3 | 351.3 | 21.08 | 0 | 21.08 | 0 | 46.88 | 15 | -15.41 | 10.39 | 3.784 | 0 | Diesel-backup
2025-01-02 12:00 | 2 | 1 | Summer | 12 | 24 | -2.3 | 2.98 | 47.3 | 423.2 | 25.39 | 0 | 25.39 | 2.3 | 48.31 | 15 | 0 | 22.92 | 7.982 | 0 | Diesel-backup
2025-01-02 13:00 | 2 | 1 | Summer | 13 | 24 | -3.5 | 2.99 | 34.6 | 481.5 | 28.89 | 0 | 28.89 | 3.5 | 45.04 | 15 | 0 | 16.15 | 5.764 | 0 | Diesel-backup
2025-01-02 14:00 | 2 | 1 | Summer | 14 | 24 | -3.1 | 7.27 | 48.2 | 404.5 | 24.27 | 7.5 | 31.77 | 3.1 | 45.28 | 15 | 0 | 13.51 | 4.868 | 0 | Diesel-backup
2025-01-02 15:00 | 2 | 1 | Summer | 15 | 24 | 0.5 | 2.23 | 81.2 | 237.1 | 14.23 | 0 | 14.23 | 0 | 47.99 | 15 | 0 | 33.76 | 11.289 | 0 | Diesel-backup
2025-01-02 16:00 | 2 | 1 | Summer | 16 | 24 | 1.1 | 1.4 | 51.4 | 348.9 | 20.93 | 0 | 20.93 | 0 | 46.21 | 15 | 0 | 25.28 | 8.728 | 0 | Diesel-backup
2025-01-02 17:00 | 2 | 1 | Summer | 17 | 24 | 1 | 4.61 | 51.3 | 320 | 19.2 | 0.19 | 19.39 | 0 | 48.06 | 15 | 0 | 28.67 | 9.774 | 0 | Diesel-backup
2025-01-02 18:00 | 2 | 1 | Summer | 18 | 24 | -1.5 | 13.57 | 50.5 | 288.2 | 17.29 | 120 | 137.29 | 1.5 | 45 | 48.96 | 92.29 | 0 | 0 | 0 | Normal
2025-01-02 19:00 | 2 | 1 | Summer | 19 | 24 | 0.7 | 6.1 | 62.9 | 211.1 | 12.67 | 2.46 | 15.13 | 0 | 45.44 | 36.84 | -30.31 | 0 | 0 | 0 | Battery-supported
2025-01-02 20:00 | 2 | 1 | Summer | 20 | 24 | 0.5 | 8.45 | 74.5 | 144.8 | 8.69 | 16.98 | 25.67 | 0 | 45.66 | 28.84 | -19.99 | 0 | 0 | 0 | Battery-supported
2025-01-02 21:00 | 2 | 1 | Summer | 21 | 24 | 0.6 | 13.17 | 55 | 147.4 | 8.84 | 120 | 128.84 | 0 | 45 | 59.7 | 83.84 | 0 | 0 | 0 | Normal
2025-01-02 22:00 | 2 | 1 | Summer | 22 | 24 | 1.9 | 2.91 | 27.2 | 135.1 | 8.11 | 0 | 8.11 | 0 | 45 | 44.94 | -36.89 | 0 | 0 | 0 | Battery-supported
2025-01-02 23:00 | 2 | 1 | Summer | 23 | 24 | 0.3 | 18.21 | 85.2 | 30.9 | 1.85 | 120 | 121.85 | 0 | 45 | 73.22 | 76.85 | 0 | 0 | 0 | Normal
2025-01-03 | 3 | 1 | Summer | 0 | 24 | 1 | 3.01 | 24.3 | 0 | 0 | 0 | 0 | 0 | 45 | 55.22 | -45 | 0 | 0 | 0 | Battery-supported
2025-01-03 01:00 | 3 | 1 | Summer | 1 | 24 | -0.7 | 5.09 | 50.2 | 53.4 | 3.2 | 0.56 | 3.76 | 0.7 | 45 | 38.72 | -41.24 | 0 | 0 | 0 | Battery-supported
2025-01-03 02:00 | 3 | 1 | Summer | 2 | 24 | -0.6 | 15.14 | 100 | 42.4 | 2.54 | 120 | 122.54 | 0.6 | 45 | 67.26 | 77.54 | 0 | 0 | 0 | Normal
2025-01-03 03:00 | 3 | 1 | Summer | 3 | 24 | -0.3 | 5.26 | 25.6 | 202.9 | 12.17 | 0.76 | 12.93 | 0.3 | 45 | 54.43 | -32.07 | 0 | 0 | 0 | Battery-supported
2025-01-03 04:00 | 3 | 1 | Summer | 4 | 24 | -5.2 | 19.11 | 47.7 | 210.5 | 12.63 | 120 | 132.63 | 5.2 | 45 | 86.68 | 87.63 | 0 | 0 | 0 | Normal
2025-01-03 05:00 | 3 | 1 | Summer | 5 | 24 | -3 | 14.23 | 43.6 | 268.7 | 16.12 | 120 | 136.12 | 3 | 45 | 95 | 22.61 | 0 | 0 | 0 | Normal
2025-01-03 06:00 | 3 | 1 | Summer | 6 | 24 | -3.6 | 4.79 | 44.5 | 309 | 18.54 | 0.3 | 18.84 | 3.6 | 45 | 84.54 | -26.16 | 0 | 0 | 0 | Battery-supported
2025-01-03 07:00 | 3 | 1 | Summer | 7 | 24 | -4.1 | 14.57 | 20.7 | 439.6 | 26.38 | 120 | 146.38 | 4.1 | 45 | 95 | 28.43 | 0 | 0 | 0 | Normal
2025-01-03 08:00 | 3 | 1 | Summer | 8 | 24 | -3.4 | 1.57 | 18.6 | 489 | 29.34 | 0 | 29.34 | 3.4 | 45.32 | 88.61 | -15.98 | 0 | 0 | 0 | Battery-supported
2025-01-03 09:00 | 3 | 1 | Summer | 9 | 24 | 0.6 | 6.22 | 52.4 | 367.8 | 22.07 | 2.82 | 24.89 | 0 | 47.49 | 79.57 | -22.6 | 0 | 0 | 0 | Battery-supported
2025-01-03 10:00 | 3 | 1 | Summer | 10 | 24 | -4.5 | 7.84 | 52.7 | 382.9 | 22.97 | 11.44 | 34.41 | 4.5 | 52.47 | 72.34 | -18.06 | 0 | 0 | 0 | Battery-supported
2025-01-03 11:00 | 3 | 1 | Summer | 11 | 24 | -0.2 | 4.97 | 40.6 | 452.3 | 27.14 | 0.44 | 27.58 | 0.2 | 47.37 | 64.43 | -19.79 | 0 | 0 | 0 | Battery-supported
2025-01-03 12:00 | 3 | 1 | Summer | 12 | 24 | -5.7 | 4.85 | 14.6 | 584.2 | 35.05 | 0.34 | 35.39 | 5.7 | 51.67 | 57.92 | -16.28 | 0 | 0 | 0 | Battery-supported
2025-01-03 13:00 | 3 | 1 | Summer | 13 | 24 | -2.4 | 7.47 | 50.5 | 403.8 | 24.23 | 8.76 | 32.99 | 2.4 | 46.38 | 52.56 | -13.39 | 0 | 0 | 0 | Battery-supported
2025-01-03 14:00 | 3 | 1 | Summer | 14 | 24 | -0.9 | 15.46 | 25.4 | 512.7 | 30.76 | 120 | 150.76 | 0.9 | 45 | 91.48 | 105.76 | 0 | 0 | 0 | Normal
2025-01-03 15:00 | 3 | 1 | Summer | 15 | 24 | 0.4 | 17.1 | 3.3 | 591 | 35.46 | 120 | 155.46 | 0 | 45 | 95 | 9.57 | 0 | 0 | 0 | Normal
2025-01-03 16:00 | 3 | 1 | Summer | 16 | 24 | 1.1 | 4.69 | 45.3 | 375 | 22.5 | 0.24 | 22.74 | 0 | 47.12 | 85.25 | -24.38 | 0 | 0 | 0 | Battery-supported
2025-01-03 17:00 | 3 | 1 | Summer | 17 | 24 | 1.6 | 4.6 | 48.1 | 332.8 | 19.97 | 0.19 | 20.16 | 0 | 47.53 | 74.3 | -27.37 | 0 | 0 | 0 | Battery-supported
2025-01-03 18:00 | 3 | 1 | Summer | 18 | 24 | -0.7 | 10.12 | 67.3 | 229.8 | 13.79 | 40.61 | 54.4 | 0.7 | 45 | 77.76 | 9.4 | 0 | 0 | 0 | Normal
2025-01-03 19:00 | 3 | 1 | Summer | 19 | 24 | -0.8 | 10.07 | 51.4 | 245.3 | 14.72 | 39.69 | 54.41 | 0.8 | 45 | 81.22 | 9.41 | 0 | 0 | 0 | Normal
2025-01-03 20:00 | 3 | 1 | Summer | 20 | 24 | 2.1 | 13.38 | 58.5 | 184 | 11.04 | 120 | 131.04 | 0 | 45 | 95 | 37.44 | 0 | 0 | 0 | Normal
2025-01-03 21:00 | 3 | 1 | Summer | 21 | 24 | -0.2 | 13.58 | 56.6 | 144.4 | 8.66 | 120 | 128.66 | 0.2 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-01-03 22:00 | 3 | 1 | Summer | 22 | 24 | -2.8 | 3.75 | 59.5 | 94 | 5.64 | 0 | 5.64 | 2.8 | 45 | 79.26 | -39.36 | 0 | 0 | 0 | Battery-supported
2025-01-03 23:00 | 3 | 1 | Summer | 23 | 24 | -2.7 | 2.19 | 22.3 | 71.3 | 4.28 | 0 | 4.28 | 2.7 | 45 | 62.97 | -40.72 | 0 | 0 | 0 | Battery-supported
2025-01-04 | 4 | 1 | Summer | 0 | 24 | -2.5 | 9.29 | 81.7 | 0 | 0 | 27.17 | 27.17 | 2.5 | 45 | 55.84 | -17.83 | 0 | 0 | 0 | Battery-supported
2025-01-04 01:00 | 4 | 1 | Summer | 1 | 24 | 0.3 | 7.51 | 45.4 | 56.5 | 3.39 | 9.02 | 12.41 | 0 | 45 | 42.8 | -32.59 | 0 | 0 | 0 | Battery-supported
2025-01-04 02:00 | 4 | 1 | Summer | 2 | 24 | -0.9 | 1.39 | 12.1 | 154.3 | 9.26 | 0 | 9.26 | 0.9 | 45 | 28.5 | -35.74 | 0 | 0 | 0 | Battery-supported
2025-01-04 03:00 | 4 | 1 | Summer | 3 | 24 | -0.1 | 2.15 | 41.3 | 173.3 | 10.4 | 0 | 10.4 | 0.1 | 45 | 15 | -33.76 | 0.84 | 0.316 | 0 | Diesel-backup
2025-01-04 04:00 | 4 | 1 | Summer | 4 | 24 | -2.9 | 9.04 | 62.8 | 173.5 | 10.41 | 23.8 | 34.21 | 2.9 | 45 | 15 | 0 | 10.79 | 3.925 | 0 | Diesel-backup
2025-01-04 05:00 | 4 | 1 | Summer | 5 | 24 | -1.9 | 6.07 | 46.9 | 259 | 15.54 | 2.38 | 17.92 | 1.9 | 45 | 15 | 0 | 27.08 | 9.287 | 0 | Diesel-backup
2025-01-04 06:00 | 4 | 1 | Summer | 6 | 24 | -1.1 | 9.16 | 49.6 | 291.2 | 17.47 | 25.38 | 42.85 | 1.1 | 45 | 15 | 0 | 2.15 | 0.806 | 0 | Diesel-backup
2025-01-04 07:00 | 4 | 1 | Summer | 7 | 24 | -3.3 | 3.14 | 16.4 | 456.2 | 27.37 | 0 | 27.37 | 3.3 | 45 | 15 | 0 | 17.63 | 6.259 | 0 | Diesel-backup
2025-01-04 08:00 | 4 | 1 | Summer | 8 | 24 | -1.7 | 9.54 | 67.5 | 280.3 | 16.82 | 30.84 | 47.66 | 1.7 | 45 | 15.98 | 2.66 | 0 | 0 | 0 | Normal
2025-01-04 09:00 | 4 | 1 | Summer | 9 | 24 | -4.1 | 8.06 | 7.9 | 570.2 | 34.21 | 13.27 | 47.48 | 4.1 | 45.81 | 16.59 | 1.67 | 0 | 0 | 0 | Normal
2025-01-04 10:00 | 4 | 1 | Summer | 10 | 24 | -3.3 | 9.95 | 1.6 | 626.1 | 37.57 | 37.56 | 75.13 | 3.3 | 45 | 27.68 | 30.13 | 0 | 0 | 0 | Normal
2025-01-04 11:00 | 4 | 1 | Summer | 11 | 24 | -3.1 | 4.91 | 18.1 | 561.9 | 33.71 | 0.39 | 34.1 | 3.1 | 48.36 | 21.98 | -14.26 | 0 | 0 | 0 | Battery-supported
2025-01-04 12:00 | 4 | 1 | Summer | 12 | 24 | -4.6 | 4.25 | 20.7 | 554.2 | 33.25 | 0.06 | 33.31 | 4.6 | 53.12 | 15 | -17.44 | 2.37 | 0.887 | 0 | Diesel-backup
2025-01-04 13:00 | 4 | 1 | Summer | 13 | 24 | -0.5 | 2.4 | 49.2 | 410.4 | 24.62 | 0 | 24.62 | 0.5 | 45.59 | 15 | 0 | 20.97 | 7.355 | 0 | Diesel-backup
2025-01-04 14:00 | 4 | 1 | Summer | 14 | 24 | -2.2 | 5.44 | 55 | 372.1 | 22.33 | 1.02 | 23.35 | 2.2 | 46.59 | 15 | 0 | 23.24 | 8.084 | 0 | Diesel-backup
2025-01-04 15:00 | 4 | 1 | Summer | 15 | 24 | -0.8 | 12.02 | 19.9 | 515.7 | 30.94 | 86.56 | 117.5 | 0.8 | 45 | 41.68 | 72.5 | 0 | 0 | 0 | Normal
2025-01-04 16:00 | 4 | 1 | Summer | 16 | 24 | 0.6 | 13.91 | 81.2 | 222 | 13.32 | 120 | 133.32 | 0 | 45 | 74.18 | 88.32 | 0 | 0 | 0 | Normal
2025-01-04 17:00 | 4 | 1 | Summer | 17 | 24 | 0.8 | 2.94 | 20.6 | 440.1 | 26.41 | 0 | 26.41 | 0 | 45.59 | 66.51 | -19.18 | 0 | 0 | 0 | Battery-supported
2025-01-04 18:00 | 4 | 1 | Summer | 18 | 24 | 1.5 | 6.41 | 20.7 | 391.8 | 23.51 | 3.45 | 26.96 | 0 | 47.8 | 58.17 | -20.84 | 0 | 0 | 0 | Battery-supported
2025-01-04 19:00 | 4 | 1 | Summer | 19 | 24 | 0 | 15.58 | 92.4 | 122.6 | 7.36 | 120 | 127.36 | 0 | 45.43 | 88.32 | 81.93 | 0 | 0 | 0 | Normal
2025-01-04 20:00 | 4 | 1 | Summer | 20 | 24 | -0.6 | 16.76 | 19 | 281.3 | 16.88 | 120 | 136.88 | 0.6 | 51.95 | 95 | 18.14 | 0 | 0 | 0 | Normal
2025-01-04 21:00 | 4 | 1 | Summer | 21 | 24 | 0.1 | 5.3 | 55.2 | 147.1 | 8.83 | 0.82 | 9.65 | 0 | 45 | 80.86 | -35.35 | 0 | 0 | 0 | Battery-supported
2025-01-04 22:00 | 4 | 1 | Summer | 22 | 24 | -3.6 | 12.62 | 56.3 | 98.1 | 5.89 | 106.17 | 112.06 | 3.6 | 45 | 95 | 38.42 | 0 | 0 | 0 | Normal
2025-01-04 23:00 | 4 | 1 | Summer | 23 | 24 | -3.3 | 11.42 | 66.2 | 43.1 | 2.59 | 69.53 | 72.12 | 3.3 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-01-05 | 5 | 1 | Summer | 0 | 24 | -3.3 | 10.89 | 35.6 | 0 | 0 | 56.49 | 56.49 | 3.3 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-01-05 01:00 | 5 | 1 | Summer | 1 | 24 | -3 | 1.91 | 37.2 | 61.7 | 3.7 | 0 | 3.7 | 3 | 45 | 78.48 | -41.3 | 0 | 0 | 0 | Battery-supported
2025-01-05 02:00 | 5 | 1 | Summer | 2 | 24 | -0.3 | 4.51 | 81.9 | 65.5 | 3.93 | 0.14 | 4.07 | 0.3 | 45 | 62.11 | -40.93 | 0 | 0 | 0 | Battery-supported
2025-01-05 03:00 | 5 | 1 | Summer | 3 | 24 | -3.6 | 5.98 | 11.3 | 229.8 | 13.79 | 2.13 | 15.92 | 3.6 | 45 | 50.48 | -29.08 | 0 | 0 | 0 | Battery-supported
2025-01-05 04:00 | 5 | 1 | Summer | 4 | 24 | -2.8 | 5.88 | 32.3 | 248.5 | 14.91 | 1.89 | 16.8 | 2.8 | 45 | 39.2 | -28.2 | 0 | 0 | 0 | Battery-supported
2025-01-05 05:00 | 5 | 1 | Summer | 5 | 24 | 0.6 | 6.36 | 63.7 | 208.5 | 12.51 | 3.27 | 15.78 | 0 | 45 | 27.51 | -29.22 | 0 | 0 | 0 | Battery-supported
2025-01-05 06:00 | 5 | 1 | Summer | 6 | 24 | -3.3 | 17.78 | 54.9 | 272.9 | 16.37 | 120 | 136.37 | 3.3 | 45 | 61.13 | 91.37 | 0 | 0 | 0 | Normal
2025-01-05 07:00 | 5 | 1 | Summer | 7 | 24 | -1 | 5.41 | 15.1 | 461.3 | 27.68 | 0.98 | 28.66 | 1 | 45 | 54.6 | -16.34 | 0 | 0 | 0 | Battery-supported
2025-01-05 08:00 | 5 | 1 | Summer | 8 | 24 | -4.7 | 8.28 | 54.7 | 335.1 | 20.11 | 15.29 | 35.4 | 4.7 | 45 | 50.76 | -9.6 | 0 | 0 | 0 | Battery-supported
2025-01-05 09:00 | 5 | 1 | Summer | 9 | 24 | -3.1 | 8.1 | 72.3 | 277.6 | 16.66 | 13.62 | 30.28 | 3.1 | 54.33 | 41.14 | -24.05 | 0 | 0 | 0 | Battery-supported
2025-01-05 10:00 | 5 | 1 | Summer | 10 | 24 | -4.6 | 6.41 | 52.2 | 385.4 | 23.12 | 3.45 | 26.57 | 4.6 | 50.05 | 31.74 | -23.48 | 0 | 0 | 0 | Battery-supported
2025-01-05 11:00 | 5 | 1 | Summer | 11 | 24 | -3 | 3.08 | 15 | 577 | 34.62 | 0 | 34.62 | 3 | 45 | 27.59 | -10.38 | 0 | 0 | 0 | Battery-supported
2025-01-05 12:00 | 5 | 1 | Summer | 12 | 24 | -0.1 | 6.94 | 79.4 | 265.4 | 15.92 | 5.7 | 21.62 | 0.1 | 45 | 18.24 | -23.38 | 0 | 0 | 0 | Battery-supported
2025-01-05 13:00 | 5 | 1 | Summer | 13 | 24 | -5.4 | 1.37 | 12.9 | 587.2 | 35.23 | 0 | 35.23 | 5.4 | 49.44 | 15 | -8.1 | 6.11 | 2.259 | 0 | Diesel-backup
2025-01-05 14:00 | 5 | 1 | Summer | 14 | 24 | -0.2 | 8.77 | 72.1 | 290.8 | 17.45 | 20.49 | 37.94 | 0.2 | 45.1 | 15 | 0 | 7.16 | 2.638 | 0 | Diesel-backup
2025-01-05 15:00 | 5 | 1 | Summer | 15 | 24 | -0.3 | 1.18 | 79.3 | 245.6 | 14.74 | 0 | 14.74 | 0.3 | 45 | 15 | 0 | 30.26 | 10.254 | 0 | Diesel-backup
2025-01-05 16:00 | 5 | 1 | Summer | 16 | 24 | -1.7 | 8.31 | 30.8 | 436.9 | 26.21 | 15.58 | 41.79 | 1.7 | 45 | 15 | 0 | 3.21 | 1.199 | 0 | Diesel-backup
2025-01-05 17:00 | 5 | 1 | Summer | 17 | 24 | -3.3 | 4.35 | 6.7 | 494 | 29.64 | 0.09 | 29.73 | 3.3 | 48.3 | 15 | 0 | 18.57 | 6.571 | 0 | Diesel-backup
2025-01-05 18:00 | 5 | 1 | Summer | 18 | 24 | 0.3 | 3.38 | 77.9 | 193 | 11.58 | 0 | 11.58 | 0 | 45 | 15 | 0 | 33.42 | 11.19 | 0 | Diesel-backup
2025-01-05 19:00 | 5 | 1 | Summer | 19 | 24 | -0.9 | 10.19 | 7.3 | 377.4 | 22.64 | 41.91 | 64.55 | 0.9 | 45 | 22.19 | 19.55 | 0 | 0 | 0 | Normal
2025-01-05 20:00 | 5 | 1 | Summer | 20 | 24 | 0.8 | 5.02 | 34.2 | 243.8 | 14.63 | 0.49 | 15.12 | 0 | 45 | 15 | -17.99 | 11.89 | 4.31 | 0 | Diesel-backup
2025-01-05 21:00 | 5 | 1 | Summer | 21 | 24 | 0.3 | 6.72 | 11.1 | 230.2 | 13.81 | 4.67 | 18.48 | 0 | 45 | 15 | 0 | 26.52 | 9.114 | 0 | Diesel-backup
2025-01-05 22:00 | 5 | 1 | Summer | 22 | 24 | 3.6 | 1.97 | 14.8 | 150.9 | 9.05 | 0 | 9.05 | 0 | 45 | 15 | 0 | 35.95 | 11.92 | 0 | Diesel-backup
2025-01-05 23:00 | 5 | 1 | Summer | 23 | 24 | -0.6 | 14.48 | 12.8 | 77.4 | 4.64 | 120 | 124.64 | 0.6 | 45 | 44.31 | 79.64 | 0 | 0 | 0 | Normal
2025-01-06 | 6 | 1 | Summer | 0 | 24 | -2.6 | 7.12 | 88 | 0 | 0 | 6.64 | 6.64 | 2.6 | 45 | 28.96 | -38.36 | 0 | 0 | 0 | Battery-supported
2025-01-06 01:00 | 6 | 1 | Summer | 1 | 24 | -0.4 | 7.11 | 29 | 67 | 4.02 | 6.58 | 10.6 | 0.4 | 45 | 15.2 | -34.4 | 0 | 0 | 0 | Battery-supported
2025-01-06 02:00 | 6 | 1 | Summer | 2 | 24 | -0.7 | 12.82 | 47.1 | 109.8 | 6.59 | 113.31 | 119.9 | 0.7 | 45 | 42.77 | 74.9 | 0 | 0 | 0 | Normal
2025-01-06 03:00 | 6 | 1 | Summer | 3 | 24 | 1.5 | 8.87 | 41.3 | 173.3 | 10.4 | 21.67 | 32.07 | 0 | 45 | 37.59 | -12.93 | 0 | 0 | 0 | Battery-supported
2025-01-06 04:00 | 6 | 1 | Summer | 4 | 24 | -0.1 | 0.75 | 84 | 121.3 | 7.28 | 0 | 7.28 | 0.1 | 45 | 22.51 | -37.72 | 0 | 0 | 0 | Battery-supported
2025-01-06 05:00 | 6 | 1 | Summer | 5 | 24 | -1.4 | 15.29 | 20.5 | 337.9 | 20.27 | 120 | 140.27 | 1.4 | 45 | 57.57 | 95.27 | 0 | 0 | 0 | Normal
2025-01-06 06:00 | 6 | 1 | Summer | 6 | 24 | 0.8 | 5.28 | 56 | 268.9 | 16.13 | 0.79 | 16.92 | 0 | 45 | 46.33 | -28.08 | 0 | 0 | 0 | Battery-supported
2025-01-06 07:00 | 6 | 1 | Summer | 7 | 24 | -5.2 | 14.78 | 67.9 | 255.3 | 15.32 | 120 | 135.32 | 5.2 | 45 | 79.57 | 90.32 | 0 | 0 | 0 | Normal
2025-01-06 08:00 | 6 | 1 | Summer | 8 | 24 | -4.1 | 5.16 | 85.5 | 203.9 | 12.23 | 0.64 | 12.87 | 4.1 | 45.94 | 66.34 | -33.07 | 0 | 0 | 0 | Battery-supported
2025-01-06 09:00 | 6 | 1 | Summer | 9 | 24 | -4.6 | 4.43 | 56.1 | 351.1 | 21.07 | 0.11 | 21.18 | 4.6 | 46.97 | 56.03 | -25.79 | 0 | 0 | 0 | Battery-supported
2025-01-06 10:00 | 6 | 1 | Summer | 10 | 24 | -3.3 | 8.52 | 16.9 | 553.3 | 33.2 | 17.71 | 50.91 | 3.3 | 45.8 | 57.91 | 5.11 | 0 | 0 | 0 | Normal
2025-01-06 11:00 | 6 | 1 | Summer | 11 | 24 | -5.2 | 19.77 | 69 | 313.9 | 18.83 | 120 | 138.83 | 5.2 | 47.25 | 91.61 | 91.58 | 0 | 0 | 0 | Normal
2025-01-06 12:00 | 6 | 1 | Summer | 12 | 24 | -0.5 | 12.6 | 38.1 | 468.3 | 28.1 | 105.47 | 133.57 | 0.5 | 45 | 95 | 9.21 | 0 | 0 | 0 | Normal
2025-01-06 13:00 | 6 | 1 | Summer | 13 | 24 | -2 | 9.08 | 0.4 | 648.6 | 38.92 | 24.32 | 63.24 | 2 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-01-06 14:00 | 6 | 1 | Summer | 14 | 24 | -4.4 | 8.44 | 37.8 | 453.9 | 27.23 | 16.87 | 44.1 | 4.4 | 46.57 | 94.01 | -2.47 | 0 | 0 | 0 | Battery-supported
2025-01-06 15:00 | 6 | 1 | Summer | 15 | 24 | -3 | 6.89 | 77.4 | 254.3 | 15.26 | 5.45 | 20.71 | 3 | 45 | 84.3 | -24.29 | 0 | 0 | 0 | Battery-supported
2025-01-06 16:00 | 6 | 1 | Summer | 16 | 24 | 0.3 | 14.41 | 24.6 | 463.2 | 27.79 | 120 | 147.79 | 0 | 45 | 95 | 29.09 | 0 | 0 | 0 | Normal
2025-01-06 17:00 | 6 | 1 | Summer | 17 | 24 | 1.8 | 10.33 | 87.3 | 179.7 | 10.78 | 44.59 | 55.37 | 0 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-01-06 18:00 | 6 | 1 | Summer | 18 | 24 | 4.5 | 2.36 | 79.4 | 187.7 | 11.26 | 0 | 11.26 | 0 | 45 | 81.5 | -33.74 | 0 | 0 | 0 | Battery-supported
2025-01-06 19:00 | 6 | 1 | Summer | 19 | 24 | 6.7 | 3.39 | 80.8 | 157.5 | 9.45 | 0 | 9.45 | 0 | 45 | 67.28 | -35.55 | 0 | 0 | 0 | Battery-supported
2025-01-06 20:00 | 6 | 1 | Summer | 20 | 24 | 1.3 | 9.26 | 70.8 | 153.9 | 9.23 | 26.75 | 35.98 | 0 | 45 | 63.68 | -9.02 | 0 | 0 | 0 | Battery-supported
2025-01-06 21:00 | 6 | 1 | Summer | 21 | 24 | -1.9 | 2.99 | 77.6 | 104.9 | 6.29 | 0 | 6.29 | 1.9 | 45 | 48.19 | -38.71 | 0 | 0 | 0 | Battery-supported
2025-01-06 22:00 | 6 | 1 | Summer | 22 | 24 | -4.5 | 7.1 | 79.8 | 68.1 | 4.09 | 6.53 | 10.62 | 4.5 | 45.32 | 34.31 | -34.7 | 0 | 0 | 0 | Battery-supported
2025-01-06 23:00 | 6 | 1 | Summer | 23 | 24 | 0.5 | 10.83 | 49.2 | 54 | 3.24 | 55.12 | 58.36 | 0 | 45 | 39.23 | 13.36 | 0 | 0 | 0 | Normal
2025-01-07 | 7 | 1 | Summer | 0 | 24 | -2.2 | 8.55 | 90.3 | 0 | 0 | 18.03 | 18.03 | 2.2 | 45 | 28.44 | -26.97 | 0 | 0 | 0 | Battery-supported
2025-01-07 01:00 | 7 | 1 | Summer | 1 | 24 | -1.6 | 2.66 | 68 | 42 | 2.52 | 0 | 2.52 | 1.6 | 45 | 15 | -33.6 | 8.88 | 3.252 | 0 | Diesel-backup
2025-01-07 02:00 | 7 | 1 | Summer | 2 | 24 | -2.5 | 3.53 | 88.7 | 56.8 | 3.41 | 0 | 3.41 | 2.5 | 45 | 15 | 0 | 41.59 | 13.49 | 0 | Diesel-backup
2025-01-07 03:00 | 7 | 1 | Summer | 3 | 24 | -1.8 | 8.71 | 39.1 | 177.5 | 10.65 | 19.79 | 30.44 | 1.8 | 45 | 15 | 0 | 14.56 | 5.227 | 0 | Diesel-backup
2025-01-07 04:00 | 7 | 1 | Summer | 4 | 24 | 0.5 | 18.54 | 61.2 | 177.5 | 10.65 | 120 | 130.65 | 0 | 45 | 46.52 | 85.65 | 0 | 0 | 0 | Normal
2025-01-07 05:00 | 7 | 1 | Summer | 5 | 24 | -1.8 | 6.21 | 57 | 228.5 | 13.71 | 2.79 | 16.5 | 1.8 | 45 | 35.12 | -28.5 | 0 | 0 | 0 | Battery-supported
2025-01-07 06:00 | 7 | 1 | Summer | 6 | 24 | -2.8 | 11.04 | 44.3 | 309.7 | 18.58 | 60 | 78.58 | 2.8 | 45 | 47.48 | 33.58 | 0 | 0 | 0 | Normal
2025-01-07 07:00 | 7 | 1 | Summer | 7 | 24 | -4.8 | 8.6 | 60.6 | 283.8 | 17.03 | 18.57 | 35.6 | 4.8 | 45 | 43.72 | -9.4 | 0 | 0 | 0 | Battery-supported
2025-01-07 08:00 | 7 | 1 | Summer | 8 | 24 | -6.3 | 4.31 | 55.1 | 333.5 | 20.01 | 0.07 | 20.08 | 6.3 | 45 | 33.75 | -24.92 | 0 | 0 | 0 | Battery-supported
2025-01-07 09:00 | 7 | 1 | Summer | 9 | 24 | -3.6 | 11.11 | 14.3 | 541.2 | 32.47 | 61.68 | 94.15 | 3.6 | 45 | 51.84 | 49.15 | 0 | 0 | 0 | Normal
2025-01-07 10:00 | 7 | 1 | Summer | 10 | 24 | -2.5 | 1.92 | 61.7 | 340.5 | 20.43 | 0 | 20.43 | 2.5 | 45 | 42.01 | -24.57 | 0 | 0 | 0 | Battery-supported
2025-01-07 11:00 | 7 | 1 | Summer | 11 | 24 | 1.7 | 10.65 | 31.7 | 495.6 | 29.74 | 51.16 | 80.9 | 0 | 45 | 55.22 | 35.9 | 0 | 0 | 0 | Normal
2025-01-07 12:00 | 7 | 1 | Summer | 12 | 24 | -1.6 | 8.91 | 52.7 | 396.7 | 23.8 | 22.16 | 45.96 | 1.6 | 45 | 55.57 | 0.96 | 0 | 0 | 0 | Normal
2025-01-07 13:00 | 7 | 1 | Summer | 13 | 24 | 0.7 | 4.59 | 56.7 | 373.6 | 22.42 | 0.18 | 22.6 | 0 | 45 | 46.61 | -22.4 | 0 | 0 | 0 | Battery-supported
2025-01-07 14:00 | 7 | 1 | Summer | 14 | 24 | -2.2 | 3.18 | 63.5 | 332 | 19.92 | 0 | 19.92 | 2.2 | 45 | 36.58 | -25.08 | 0 | 0 | 0 | Battery-supported
2025-01-07 15:00 | 7 | 1 | Summer | 15 | 24 | -3.3 | 4.86 | 30.2 | 468.9 | 28.13 | 0.35 | 28.48 | 3.3 | 45 | 29.97 | -16.52 | 0 | 0 | 0 | Battery-supported
2025-01-07 16:00 | 7 | 1 | Summer | 16 | 24 | -2.5 | 4.1 | 35.9 | 415.1 | 24.91 | 0.03 | 24.94 | 2.5 | 47.86 | 20.8 | -22.92 | 0 | 0 | 0 | Battery-supported
2025-01-07 17:00 | 7 | 1 | Summer | 17 | 24 | -1.6 | 5.59 | 77.8 | 216.8 | 13.01 | 1.28 | 14.29 | 1.6 | 45 | 15 | -14.51 | 16.2 | 5.781 | 0 | Diesel-backup
2025-01-07 18:00 | 7 | 1 | Summer | 18 | 24 | 4.9 | 5.2 | 43.9 | 311.1 | 18.67 | 0.69 | 19.36 | 0 | 47.1 | 15 | 0 | 27.74 | 9.49 | 0 | Diesel-backup
2025-01-07 19:00 | 7 | 1 | Summer | 19 | 24 | -1.5 | 4.59 | 79 | 162.8 | 9.77 | 0.18 | 9.95 | 1.5 | 45 | 15 | 0 | 35.05 | 11.662 | 0 | Diesel-backup
2025-01-07 20:00 | 7 | 1 | Summer | 20 | 24 | 2.2 | 1.85 | 18.8 | 281.8 | 16.91 | 0 | 16.91 | 0 | 45 | 15 | 0 | 28.09 | 9.597 | 0 | Diesel-backup
2025-01-07 21:00 | 7 | 1 | Summer | 21 | 24 | -1.7 | 2.86 | 39.7 | 176.2 | 10.57 | 0 | 10.57 | 1.7 | 45 | 15 | 0 | 34.43 | 11.483 | 0 | Diesel-backup
2025-01-07 22:00 | 7 | 1 | Summer | 22 | 24 | 2.2 | 12.13 | 0 | 169.8 | 10.19 | 89.96 | 100.15 | 0 | 45 | 35.3 | 55.15 | 0 | 0 | 0 | Normal
2025-01-07 23:00 | 7 | 1 | Summer | 23 | 24 | 0.8 | 4.68 | 90.7 | 27.4 | 1.64 | 0.23 | 1.87 | 0 | 45 | 18.04 | -43.13 | 0 | 0 | 0 | Battery-supported
2025-01-08 | 8 | 1 | Summer | 0 | 24 | -0.7 | 5.66 | 46 | 0 | 0 | 1.41 | 1.41 | 0.7 | 45 | 15 | -7.61 | 35.98 | 11.93 | 0 | Diesel-backup
2025-01-08 01:00 | 8 | 1 | Summer | 1 | 24 | -0.8 | 5.01 | 88.3 | 28.9 | 1.73 | 0.48 | 2.21 | 0.8 | 46.3 | 15 | 0 | 44.09 | 14.16 | 0 | Diesel-backup
2025-01-08 02:00 | 8 | 1 | Summer | 2 | 24 | -2.5 | 14.58 | 65.6 | 86.2 | 5.17 | 120 | 125.17 | 2.5 | 45 | 44.5 | 80.17 | 0 | 0 | 0 | Normal
2025-01-08 03:00 | 8 | 1 | Summer | 3 | 24 | -0.5 | 4.03 | 16.9 | 219.2 | 13.15 | 0.02 | 13.17 | 0.5 | 45 | 31.77 | -31.83 | 0 | 0 | 0 | Battery-supported
2025-01-08 04:00 | 8 | 1 | Summer | 4 | 24 | -2.8 | 3.83 | 87.1 | 113.7 | 6.82 | 0.01 | 6.83 | 2.8 | 45 | 16.5 | -38.17 | 0 | 0 | 0 | Battery-supported
2025-01-08 05:00 | 8 | 1 | Summer | 5 | 24 | -4.8 | 9.02 | 9 | 372.4 | 22.34 | 23.54 | 45.88 | 4.8 | 45 | 16.83 | 0.88 | 0 | 0 | 0 | Normal
2025-01-08 06:00 | 8 | 1 | Summer | 6 | 24 | -5.2 | 7.42 | 73.5 | 208 | 12.48 | 8.43 | 20.91 | 5.2 | 45 | 15 | -4.57 | 19.52 | 6.884 | 0 | Diesel-backup
2025-01-08 07:00 | 8 | 1 | Summer | 7 | 24 | -2.2 | 9.16 | 59 | 290.3 | 17.42 | 25.38 | 42.8 | 2.2 | 45 | 15 | 0 | 2.2 | 0.825 | 0 | Diesel-backup
2025-01-08 08:00 | 8 | 1 | Summer | 8 | 24 | 0.9 | 8.83 | 51.3 | 349.3 | 20.96 | 21.19 | 42.15 | 0 | 45 | 15 | 0 | 2.85 | 1.066 | 0 | Diesel-backup
2025-01-08 09:00 | 8 | 1 | Summer | 9 | 24 | -2.2 | 11.27 | 35.1 | 446.3 | 26.78 | 65.66 | 92.44 | 2.2 | 45 | 32.46 | 47.44 | 0 | 0 | 0 | Normal
2025-01-08 10:00 | 8 | 1 | Summer | 10 | 24 | -2.6 | 2.6 | 85.5 | 227.5 | 13.65 | 0 | 13.65 | 2.6 | 45 | 19.92 | -31.35 | 0 | 0 | 0 | Battery-supported
2025-01-08 11:00 | 8 | 1 | Summer | 11 | 24 | -1.5 | 8.52 | 82.8 | 246.3 | 14.78 | 17.71 | 32.49 | 1.5 | 45 | 15 | -12.29 | 0.22 | 0.081 | 0 | Diesel-backup
2025-01-08 12:00 | 8 | 1 | Summer | 12 | 24 | 1 | 3.85 | 64.7 | 337.8 | 20.27 | 0.01 | 20.28 | 0 | 45 | 15 | 0 | 24.72 | 8.552 | 0 | Diesel-backup
2025-01-08 13:00 | 8 | 1 | Summer | 13 | 24 | -1 | 1.43 | 87.7 | 222.8 | 13.37 | 0 | 13.37 | 1 | 45 | 15 | 0 | 31.63 | 10.663 | 0 | Diesel-backup
2025-01-08 14:00 | 8 | 1 | Summer | 14 | 24 | -2 | 8.79 | 31.3 | 484.8 | 29.09 | 20.72 | 49.81 | 2 | 51.21 | 15 | 0 | 1.4 | 0.526 | 0 | Diesel-backup
2025-01-08 15:00 | 8 | 1 | Summer | 15 | 24 | 1.7 | 8.5 | 45.1 | 400.9 | 24.05 | 17.5 | 41.55 | 0 | 45 | 15 | 0 | 3.45 | 1.287 | 0 | Diesel-backup
2025-01-08 16:00 | 8 | 1 | Summer | 16 | 24 | 0.6 | 6.55 | 22.1 | 473.8 | 28.43 | 3.97 | 32.4 | 0 | 45 | 15 | 0 | 12.6 | 4.555 | 0 | Diesel-backup
2025-01-08 17:00 | 8 | 1 | Summer | 17 | 24 | 3.4 | 11.38 | 84.4 | 191.2 | 11.47 | 68.48 | 79.95 | 0 | 45 | 27.86 | 34.95 | 0 | 0 | 0 | Normal
2025-01-08 18:00 | 8 | 1 | Summer | 18 | 24 | 0.6 | 3.87 | 81 | 182.2 | 10.93 | 0.01 | 10.94 | 0 | 45 | 15 | -32.15 | 1.91 | 0.715 | 0 | Diesel-backup
2025-01-08 19:00 | 8 | 1 | Summer | 19 | 24 | -2.3 | 9.64 | 86.4 | 140.4 | 8.42 | 32.4 | 40.82 | 2.3 | 45 | 15 | 0 | 4.18 | 1.556 | 0 | Diesel-backup
2025-01-08 20:00 | 8 | 1 | Summer | 20 | 24 | -2.6 | 5.98 | 54.7 | 193.4 | 11.6 | 2.13 | 13.73 | 2.6 | 45 | 15 | 0 | 31.27 | 10.556 | 0 | Diesel-backup
2025-01-08 21:00 | 8 | 1 | Summer | 21 | 24 | 4 | 6.27 | 56.7 | 144.3 | 8.66 | 2.97 | 11.63 | 0 | 45 | 15 | 0 | 33.37 | 11.175 | 0 | Diesel-backup
2025-01-08 22:00 | 8 | 1 | Summer | 22 | 24 | 4 | 1.61 | 33.1 | 127.6 | 7.66 | 0 | 7.66 | 0 | 45 | 15 | 0 | 37.34 | 12.315 | 0 | Diesel-backup
2025-01-08 23:00 | 8 | 1 | Summer | 23 | 24 | -0.4 | 11.45 | 82.1 | 32.9 | 1.97 | 70.33 | 72.3 | 0.4 | 45 | 25.05 | 27.3 | 0 | 0 | 0 | Normal
2025-01-09 | 9 | 1 | Summer | 0 | 24 | -1.2 | 8.3 | 16.7 | 0 | 0 | 15.48 | 15.48 | 1.2 | 45 | 15 | -25.12 | 4.4 | 1.638 | 0 | Diesel-backup
2025-01-09 01:00 | 9 | 1 | Summer | 1 | 24 | 2.5 | 9.42 | 84.9 | 31.1 | 1.87 | 29.04 | 30.91 | 0 | 45 | 15 | 0 | 14.09 | 5.066 | 0 | Diesel-backup
2025-01-09 02:00 | 9 | 1 | Summer | 2 | 24 | -3.5 | 3.51 | 35.2 | 125 | 7.5 | 0 | 7.5 | 3.5 | 45 | 15 | 0 | 37.5 | 12.36 | 0 | Diesel-backup
2025-01-09 03:00 | 9 | 1 | Summer | 3 | 24 | -3.4 | 7.74 | 62 | 134.4 | 8.06 | 10.67 | 18.73 | 3.4 | 45 | 15 | 0 | 26.27 | 9.036 | 0 | Diesel-backup
2025-01-09 04:00 | 9 | 1 | Summer | 4 | 24 | -0.4 | 5.97 | 44.1 | 219.5 | 13.17 | 2.11 | 15.28 | 0.4 | 45 | 15 | 0 | 29.72 | 10.092 | 0 | Diesel-backup
2025-01-09 05:00 | 9 | 1 | Summer | 5 | 24 | -3 | 8.56 | 45.7 | 262.3 | 15.74 | 18.13 | 33.87 | 3 | 45 | 15 | 0 | 11.13 | 4.044 | 0 | Diesel-backup
2025-01-09 06:00 | 9 | 1 | Summer | 6 | 24 | -2.4 | 7.53 | 73.3 | 208.8 | 12.53 | 9.16 | 21.69 | 2.4 | 45 | 15 | 0 | 23.31 | 8.106 | 0 | Diesel-backup
2025-01-09 07:00 | 9 | 1 | Summer | 7 | 24 | -2.9 | 16.16 | 7.7 | 490.3 | 29.42 | 120 | 149.42 | 2.9 | 45 | 53.43 | 104.42 | 0 | 0 | 0 | Normal
2025-01-09 08:00 | 9 | 1 | Summer | 8 | 24 | -1.8 | 13.4 | 36.7 | 411.7 | 24.7 | 120 | 144.7 | 1.8 | 45 | 90.12 | 99.7 | 0 | 0 | 0 | Normal
2025-01-09 09:00 | 9 | 1 | Summer | 9 | 24 | 0.6 | 5.55 | 24.5 | 494.8 | 29.69 | 1.21 | 30.9 | 0 | 45 | 84.48 | -14.1 | 0 | 0 | 0 | Battery-supported
2025-01-09 10:00 | 9 | 1 | Summer | 10 | 24 | -2.2 | 8.78 | 16.5 | 555.1 | 33.31 | 20.6 | 53.91 | 2.2 | 45 | 87.76 | 8.91 | 0 | 0 | 0 | Normal
2025-01-09 11:00 | 9 | 1 | Summer | 11 | 24 | -0.7 | 5.26 | 59.1 | 362.1 | 21.73 | 0.76 | 22.49 | 0.7 | 48.54 | 77.34 | -26.05 | 0 | 0 | 0 | Battery-supported
2025-01-09 12:00 | 9 | 1 | Summer | 12 | 24 | -6.3 | 11.21 | 37.3 | 472.6 | 28.36 | 64.15 | 92.51 | 6.3 | 46.26 | 94.36 | 46.25 | 0 | 0 | 0 | Normal
2025-01-09 13:00 | 9 | 1 | Summer | 13 | 24 | -1.6 | 6.12 | 11.1 | 596.3 | 35.78 | 2.52 | 38.3 | 1.6 | 45.75 | 91.38 | -7.45 | 0 | 0 | 0 | Battery-supported
2025-01-09 14:00 | 9 | 1 | Summer | 14 | 24 | -2.9 | 4.81 | 26.2 | 509.2 | 30.55 | 0.31 | 30.86 | 2.9 | 45 | 85.72 | -14.14 | 0 | 0 | 0 | Battery-supported
2025-01-09 15:00 | 9 | 1 | Summer | 15 | 24 | -3.4 | 7.68 | 50.8 | 375.2 | 22.51 | 10.22 | 32.73 | 3.4 | 45.48 | 80.62 | -12.75 | 0 | 0 | 0 | Battery-supported
2025-01-09 16:00 | 9 | 1 | Summer | 16 | 24 | -2.2 | 12.82 | 15.9 | 500.3 | 30.02 | 113.31 | 143.33 | 2.2 | 45 | 95 | 39.08 | 0 | 0 | 0 | Normal
2025-01-09 17:00 | 9 | 1 | Summer | 17 | 24 | -0.7 | 11.7 | 66.9 | 259.3 | 15.56 | 77.17 | 92.73 | 0.7 | 48.58 | 95 | 0 | 0 | 0 | 0 | Normal
2025-01-09 18:00 | 9 | 1 | Summer | 18 | 24 | 2.3 | 4.99 | 100 | 116 | 6.96 | 0.46 | 7.42 | 0 | 45 | 79.97 | -37.58 | 0 | 0 | 0 | Battery-supported
2025-01-09 19:00 | 9 | 1 | Summer | 19 | 24 | -2.5 | 15.37 | 18.4 | 344.3 | 20.66 | 120 | 140.66 | 2.5 | 45 | 95 | 40.85 | 0 | 0 | 0 | Normal
2025-01-09 20:00 | 9 | 1 | Summer | 20 | 24 | 0.5 | 3.66 | 27.7 | 259.8 | 15.59 | 0 | 15.59 | 0 | 45 | 83.24 | -29.41 | 0 | 0 | 0 | Battery-supported
2025-01-09 21:00 | 9 | 1 | Summer | 21 | 24 | -0.7 | 4.44 | 37.2 | 181 | 10.86 | 0.12 | 10.98 | 0.7 | 45 | 69.63 | -34.02 | 0 | 0 | 0 | Battery-supported
2025-01-09 22:00 | 9 | 1 | Summer | 22 | 24 | -0.5 | 10.94 | 28.1 | 134 | 8.04 | 57.64 | 65.68 | 0.5 | 45 | 77.24 | 20.68 | 0 | 0 | 0 | Normal
2025-01-09 23:00 | 9 | 1 | Summer | 23 | 24 | 2.2 | 1.43 | 20.2 | 72.6 | 4.36 | 0 | 4.36 | 0 | 45 | 60.98 | -40.64 | 0 | 0 | 0 | Battery-supported
2025-01-10 | 10 | 1 | Summer | 0 | 24 | 0.9 | 6.71 | 18.6 | 0 | 0 | 4.63 | 4.63 | 0 | 45 | 44.83 | -40.37 | 0 | 0 | 0 | Battery-supported
2025-01-10 01:00 | 10 | 1 | Summer | 1 | 24 | 2.3 | 5.53 | 25.7 | 69.1 | 4.15 | 1.17 | 5.32 | 0 | 45 | 28.96 | -39.68 | 0 | 0 | 0 | Battery-supported
2025-01-10 02:00 | 10 | 1 | Summer | 2 | 24 | -1.4 | 15.87 | 82.9 | 64.2 | 3.85 | 120 | 123.85 | 1.4 | 45 | 57.98 | 78.85 | 0 | 0 | 0 | Normal
2025-01-10 03:00 | 10 | 1 | Summer | 3 | 24 | -3 | 3.22 | 51.1 | 154.9 | 9.29 | 0 | 9.29 | 3 | 45 | 43.7 | -35.71 | 0 | 0 | 0 | Battery-supported
2025-01-10 04:00 | 10 | 1 | Summer | 4 | 24 | -2.3 | 3.47 | 74.1 | 145.8 | 8.75 | 0 | 8.75 | 2.3 | 45 | 29.2 | -36.25 | 0 | 0 | 0 | Battery-supported
2025-01-10 05:00 | 10 | 1 | Summer | 5 | 24 | -1.6 | 17.09 | 51.9 | 243.7 | 14.62 | 120 | 134.62 | 1.6 | 45 | 62.18 | 89.62 | 0 | 0 | 0 | Normal
2025-01-10 06:00 | 10 | 1 | Summer | 6 | 24 | -2 | 5.57 | 41.4 | 319.9 | 19.19 | 1.24 | 20.43 | 2 | 45 | 52.35 | -24.57 | 0 | 0 | 0 | Battery-supported
2025-01-10 07:00 | 10 | 1 | Summer | 7 | 24 | -4.9 | 12.54 | 44.3 | 347.5 | 20.85 | 103.4 | 124.25 | 4.9 | 45 | 81.51 | 79.25 | 0 | 0 | 0 | Normal
2025-01-10 08:00 | 10 | 1 | Summer | 8 | 24 | -2.3 | 5.02 | 45.4 | 374.4 | 22.46 | 0.49 | 22.95 | 2.3 | 45 | 72.69 | -22.05 | 0 | 0 | 0 | Battery-supported
2025-01-10 09:00 | 10 | 1 | Summer | 9 | 24 | -2 | 4.32 | 52.4 | 367.8 | 22.07 | 0.08 | 22.15 | 2 | 45 | 63.55 | -22.85 | 0 | 0 | 0 | Battery-supported
2025-01-10 10:00 | 10 | 1 | Summer | 10 | 24 | 3.2 | 12.89 | 67.3 | 313.9 | 18.83 | 115.88 | 134.71 | 0 | 45 | 95 | 85.46 | 0 | 0 | 0 | Normal
2025-01-10 11:00 | 10 | 1 | Summer | 11 | 24 | 2 | 19.4 | 47.8 | 417.1 | 25.03 | 120 | 145.03 | 0 | 45.74 | 95 | 0 | 0 | 0 | 0 | Normal
2025-01-10 12:00 | 10 | 1 | Summer | 12 | 24 | -3.7 | 13.45 | 38.9 | 464.4 | 27.86 | 120 | 147.86 | 3.7 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-01-10 13:00 | 10 | 1 | Summer | 13 | 24 | -2.1 | 4.82 | 55.4 | 380.2 | 22.81 | 0.32 | 23.13 | 2.1 | 45 | 86.25 | -21.87 | 0 | 0 | 0 | Battery-supported
2025-01-10 14:00 | 10 | 1 | Summer | 14 | 24 | -4.3 | 6.54 | 69.7 | 302.2 | 18.13 | 3.93 | 22.06 | 4.3 | 49.62 | 75.23 | -27.56 | 0 | 0 | 0 | Battery-supported
2025-01-10 15:00 | 10 | 1 | Summer | 15 | 24 | -2 | 3.58 | 86.9 | 210.9 | 12.65 | 0 | 12.65 | 2 | 47.72 | 61.2 | -35.07 | 0 | 0 | 0 | Battery-supported
2025-01-10 16:00 | 10 | 1 | Summer | 16 | 24 | 0.4 | 3.99 | 48 | 363.5 | 21.81 | 0.02 | 21.83 | 0 | 45 | 51.93 | -23.17 | 0 | 0 | 0 | Battery-supported
2025-01-10 17:00 | 10 | 1 | Summer | 17 | 24 | 2.7 | 3.86 | 69.8 | 247.9 | 14.87 | 0.01 | 14.88 | 0 | 45 | 39.88 | -30.12 | 0 | 0 | 0 | Battery-supported
2025-01-10 18:00 | 10 | 1 | Summer | 18 | 24 | -1.3 | 5.1 | 53.8 | 276.7 | 16.6 | 0.57 | 17.17 | 1.3 | 48.1 | 27.51 | -30.93 | 0 | 0 | 0 | Battery-supported
2025-01-10 19:00 | 10 | 1 | Summer | 19 | 24 | -1 | 7.18 | 17.9 | 345.8 | 20.75 | 6.98 | 27.73 | 1 | 45 | 20.6 | -17.27 | 0 | 0 | 0 | Battery-supported
2025-01-10 20:00 | 10 | 1 | Summer | 20 | 24 | -4.3 | 6.7 | 44.9 | 217.6 | 13.06 | 4.59 | 17.65 | 4.3 | 50.34 | 15 | -14.01 | 18.68 | 6.607 | 0 | Diesel-backup
2025-01-10 21:00 | 10 | 1 | Summer | 21 | 24 | 0 | 10.05 | 74.6 | 110.5 | 6.63 | 39.33 | 45.96 | 0 | 45 | 15.35 | 0.96 | 0 | 0 | 0 | Normal
2025-01-10 22:00 | 10 | 1 | Summer | 22 | 24 | -2.1 | 7.4 | 22.1 | 141.7 | 8.5 | 8.3 | 16.8 | 2.1 | 45 | 15 | -0.88 | 27.32 | 9.36 | 0 | Diesel-backup
2025-01-10 23:00 | 10 | 1 | Summer | 23 | 24 | -1.1 | 9.51 | 65.8 | 43.4 | 2.6 | 30.38 | 32.98 | 1.1 | 45 | 15 | 0 | 12.02 | 4.354 | 0 | Diesel-backup
2025-01-11 | 11 | 1 | Summer | 0 | 24 | -2.2 | 10.37 | 57.8 | 0 | 0 | 45.38 | 45.38 | 2.2 | 45 | 15.14 | 0.38 | 0 | 0 | 0 | Normal
2025-01-11 01:00 | 11 | 1 | Summer | 1 | 24 | -0.8 | 4.87 | 80.1 | 34.2 | 2.05 | 0.36 | 2.41 | 0.8 | 45 | 15 | -0.35 | 42.24 | 13.666 | 0 | Diesel-backup
2025-01-11 02:00 | 11 | 1 | Summer | 2 | 24 | -4.9 | 6.04 | 23.6 | 139.8 | 8.39 | 2.29 | 10.68 | 4.9 | 45 | 15 | 0 | 34.32 | 11.452 | 0 | Diesel-backup
2025-01-11 03:00 | 11 | 1 | Summer | 3 | 24 | -4.6 | 30.52 | 29.9 | 194.7 | 11.68 | 0 | 11.68 | 4.6 | 45 | 15 | 0 | 33.32 | 11.161 | 0 | Diesel-backup
2025-01-11 04:00 | 11 | 1 | Summer | 4 | 24 | 2.9 | 4.62 | 66.2 | 165 | 9.9 | 0.2 | 10.1 | 0 | 45 | 15 | 0 | 34.9 | 11.619 | 0 | Diesel-backup
2025-01-11 05:00 | 11 | 1 | Summer | 5 | 24 | -4.9 | 9.82 | 70.8 | 187.3 | 11.24 | 35.33 | 46.57 | 4.9 | 45 | 15.58 | 1.57 | 0 | 0 | 0 | Normal
2025-01-11 06:00 | 11 | 1 | Summer | 6 | 24 | -4.7 | 2.73 | 77.6 | 193.9 | 11.63 | 0 | 11.63 | 4.7 | 45 | 15 | -1.44 | 31.93 | 10.75 | 0 | Diesel-backup
2025-01-11 07:00 | 11 | 1 | Summer | 7 | 24 | 1.6 | 10.54 | 87.2 | 180.2 | 10.81 | 48.83 | 59.64 | 0 | 45 | 20.39 | 14.64 | 0 | 0 | 0 | Normal
2025-01-11 08:00 | 11 | 1 | Summer | 8 | 24 | 3.9 | 4.14 | 70 | 269.7 | 16.18 | 0.04 | 16.22 | 0 | 45 | 15 | -13.47 | 15.31 | 5.481 | 0 | Diesel-backup
2025-01-11 09:00 | 11 | 1 | Summer | 9 | 24 | -5.1 | 6.84 | 88 | 206.2 | 12.37 | 5.21 | 17.58 | 5.1 | 54.99 | 15 | 0 | 37.41 | 12.335 | 0 | Diesel-backup
2025-01-11 10:00 | 11 | 1 | Summer | 10 | 24 | -3.1 | 2.41 | 26.1 | 509.5 | 30.57 | 0 | 30.57 | 3.1 | 45 | 15 | 0 | 14.43 | 5.182 | 0 | Diesel-backup
2025-01-11 11:00 | 11 | 1 | Summer | 11 | 24 | -1.3 | 6.43 | 89.7 | 213 | 12.78 | 3.52 | 16.3 | 1.3 | 45 | 15 | 0 | 28.7 | 9.783 | 0 | Diesel-backup
2025-01-11 12:00 | 11 | 1 | Summer | 12 | 24 | 2 | 6.51 | 51.6 | 401.9 | 24.11 | 3.82 | 27.93 | 0 | 45 | 15 | 0 | 17.07 | 6.073 | 0 | Diesel-backup
2025-01-11 13:00 | 11 | 1 | Summer | 13 | 24 | -3.6 | 5.9 | 57.1 | 371.9 | 22.31 | 1.93 | 24.24 | 3.6 | 45 | 15 | 0 | 20.76 | 7.287 | 0 | Diesel-backup
2025-01-11 14:00 | 11 | 1 | Summer | 14 | 24 | -1.6 | 8.6 | 34 | 472.1 | 28.33 | 18.57 | 46.9 | 1.6 | 46.44 | 15.17 | 0.46 | 0 | 0 | 0 | Normal
2025-01-11 15:00 | 11 | 1 | Summer | 15 | 24 | 1.1 | 12.27 | 80 | 242.2 | 14.53 | 94.41 | 108.94 | 0 | 45 | 38.7 | 63.94 | 0 | 0 | 0 | Normal
2025-01-11 16:00 | 11 | 1 | Summer | 16 | 24 | 0.7 | 3.46 | 22.4 | 472.6 | 28.36 | 0 | 28.36 | 0 | 45 | 32.04 | -16.64 | 0 | 0 | 0 | Battery-supported
2025-01-11 17:00 | 11 | 1 | Summer | 17 | 24 | -0.8 | 5.99 | 64.4 | 269.2 | 16.15 | 2.16 | 18.31 | 0.8 | 45 | 21.37 | -26.69 | 0 | 0 | 0 | Battery-supported
2025-01-11 18:00 | 11 | 1 | Summer | 18 | 24 | 0 | 2.54 | 22.8 | 384.4 | 23.06 | 0 | 23.06 | 0 | 45 | 15 | -15.92 | 6.02 | 2.227 | 0 | Diesel-backup
2025-01-11 19:00 | 11 | 1 | Summer | 19 | 24 | -2.6 | 1.73 | 35.9 | 291.7 | 17.5 | 0 | 17.5 | 2.6 | 45 | 15 | 0 | 27.5 | 9.416 | 0 | Diesel-backup
2025-01-11 20:00 | 11 | 1 | Summer | 20 | 24 | -0.1 | 7.34 | 49 | 207.5 | 12.45 | 7.93 | 20.38 | 0.1 | 45 | 15 | 0 | 24.62 | 8.521 | 0 | Diesel-backup
2025-01-11 21:00 | 11 | 1 | Summer | 21 | 24 | -0.2 | 3.27 | 81.4 | 97.7 | 5.86 | 0 | 5.86 | 0.2 | 45 | 15 | 0 | 39.14 | 12.818 | 0 | Diesel-backup
2025-01-11 22:00 | 11 | 1 | Summer | 22 | 24 | 0.8 | 6.66 | 65.7 | 86.1 | 5.17 | 4.42 | 9.59 | 0 | 45 | 15 | 0 | 35.41 | 11.766 | 0 | Diesel-backup
2025-01-11 23:00 | 11 | 1 | Summer | 23 | 24 | -1.2 | 7.52 | 8.3 | 80.3 | 4.82 | 9.09 | 13.91 | 1.2 | 45 | 15 | 0 | 31.09 | 10.502 | 0 | Diesel-backup
2025-01-12 | 12 | 1 | Summer | 0 | 24 | 0.8 | 1.97 | 83.1 | 0 | 0 | 0 | 0 | 0 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-01-12 01:00 | 12 | 1 | Summer | 1 | 24 | 1.6 | 8.2 | 73.3 | 38.6 | 2.32 | 14.53 | 16.85 | 0 | 45 | 15 | 0 | 28.15 | 9.615 | 0 | Diesel-backup
2025-01-12 02:00 | 12 | 1 | Summer | 2 | 24 | -0.7 | 11.94 | 38.3 | 121 | 7.26 | 84.15 | 91.41 | 0.7 | 45 | 32.08 | 46.41 | 0 | 0 | 0 | Normal
2025-01-12 03:00 | 12 | 1 | Summer | 3 | 24 | -0.6 | 9.3 | 50.7 | 155.6 | 9.34 | 27.31 | 36.65 | 0.6 | 45 | 28.74 | -8.35 | 0 | 0 | 0 | Battery-supported
2025-01-12 04:00 | 12 | 1 | Summer | 4 | 24 | -1.6 | 3.51 | 25.4 | 265.4 | 15.92 | 0 | 15.92 | 1.6 | 45 | 17.11 | -29.08 | 0 | 0 | 0 | Battery-supported
2025-01-12 05:00 | 12 | 1 | Summer | 5 | 24 | -2.1 | 6.4 | 73.5 | 179.3 | 10.76 | 3.41 | 14.17 | 2.1 | 45 | 15 | -5.27 | 25.56 | 8.816 | 0 | Diesel-backup
2025-01-12 06:00 | 12 | 1 | Summer | 6 | 24 | -3.9 | 6.84 | 19.8 | 395 | 23.7 | 5.21 | 28.91 | 3.9 | 45 | 15 | 0 | 16.09 | 5.744 | 0 | Diesel-backup
2025-01-12 07:00 | 12 | 1 | Summer | 7 | 24 | -1.8 | 6.06 | 61.9 | 278.7 | 16.72 | 2.35 | 19.07 | 1.8 | 45 | 15 | 0 | 25.93 | 8.931 | 0 | Diesel-backup
2025-01-12 08:00 | 12 | 1 | Summer | 8 | 24 | -2.7 | 2.63 | 80.5 | 225.1 | 13.51 | 0 | 13.51 | 2.7 | 45.61 | 15 | 0 | 32.1 | 10.802 | 0 | Diesel-backup
2025-01-12 09:00 | 12 | 1 | Summer | 9 | 24 | 2.1 | 3.9 | 65 | 310.4 | 18.62 | 0.01 | 18.63 | 0 | 45 | 15 | 0 | 26.37 | 9.067 | 0 | Diesel-backup
2025-01-12 10:00 | 12 | 1 | Summer | 10 | 24 | 1.1 | 5.73 | 71.4 | 294.5 | 17.67 | 1.55 | 19.22 | 0 | 45 | 15 | 0 | 25.78 | 8.884 | 0 | Diesel-backup
2025-01-12 11:00 | 12 | 1 | Summer | 11 | 24 | -1.2 | 7.46 | 89.4 | 214.2 | 12.85 | 8.69 | 21.54 | 1.2 | 45 | 15 | 0 | 23.46 | 8.154 | 0 | Diesel-backup
2025-01-12 12:00 | 12 | 1 | Summer | 12 | 24 | -3.4 | 4.6 | 60.2 | 360 | 21.6 | 0.19 | 21.79 | 3.4 | 48.88 | 15 | 0 | 27.09 | 9.29 | 0 | Diesel-backup
2025-01-12 13:00 | 12 | 1 | Summer | 13 | 24 | -3.9 | 1.57 | 42.8 | 441.6 | 26.5 | 0 | 26.5 | 3.9 | 53.48 | 15 | 0 | 26.98 | 9.256 | 0 | Diesel-backup
2025-01-12 14:00 | 12 | 1 | Summer | 14 | 24 | 1.6 | 4.78 | 45.5 | 417.4 | 25.04 | 0.29 | 25.33 | 0 | 52.02 | 15 | 0 | 26.69 | 9.166 | 0 | Diesel-backup
2025-01-12 15:00 | 12 | 1 | Summer | 15 | 24 | 0 | 16.13 | 38.4 | 431.3 | 25.88 | 120 | 145.88 | 0 | 46.65 | 51.52 | 99.23 | 0 | 0 | 0 | Normal
2025-01-12 16:00 | 12 | 1 | Summer | 16 | 24 | 0.8 | 8.23 | 76.3 | 243 | 14.58 | 14.81 | 29.39 | 0 | 45 | 45.27 | -15.61 | 0 | 0 | 0 | Battery-supported
2025-01-12 17:00 | 12 | 1 | Summer | 17 | 24 | -3.8 | 7.33 | 18.5 | 448.3 | 26.9 | 7.86 | 34.76 | 3.8 | 50.7 | 38.9 | -15.94 | 0 | 0 | 0 | Battery-supported
2025-01-12 18:00 | 12 | 1 | Summer | 18 | 24 | 2.3 | 3.86 | 37.4 | 333.6 | 20.02 | 0.01 | 20.03 | 0 | 45 | 28.91 | -24.97 | 0 | 0 | 0 | Battery-supported
2025-01-12 19:00 | 12 | 1 | Summer | 19 | 24 | 1.4 | 4.92 | 80.4 | 158.6 | 9.52 | 0.4 | 9.92 | 0 | 45 | 15 | -34.77 | 0.31 | 0.116 | 0 | Diesel-backup
2025-01-12 20:00 | 12 | 1 | Summer | 20 | 24 | -2 | 1.48 | 63.7 | 171.2 | 10.27 | 0 | 10.27 | 2 | 52.81 | 15 | 0 | 42.54 | 13.747 | 0 | Diesel-backup
2025-01-12 21:00 | 12 | 1 | Summer | 21 | 24 | -0.6 | 3.68 | 49.1 | 158.6 | 9.52 | 0 | 9.52 | 0.6 | 45 | 15 | 0 | 35.48 | 11.786 | 0 | Diesel-backup
2025-01-12 22:00 | 12 | 1 | Summer | 22 | 24 | 0.9 | 7.99 | 44.8 | 112.7 | 6.76 | 12.67 | 19.43 | 0 | 45 | 15 | 0 | 25.57 | 8.818 | 0 | Diesel-backup
2025-01-12 23:00 | 12 | 1 | Summer | 23 | 24 | 0.2 | 7.36 | 48.1 | 54.7 | 3.28 | 8.05 | 11.33 | 0 | 45 | 15 | 0 | 33.67 | 11.263 | 0 | Diesel-backup
2025-01-13 | 13 | 1 | Summer | 0 | 24 | -0.9 | 4.32 | 100 | 0 | 0 | 0.08 | 0.08 | 0.9 | 45 | 15 | 0 | 44.92 | 14.379 | 0 | Diesel-backup
2025-01-13 01:00 | 13 | 1 | Summer | 1 | 24 | -0.8 | 6.06 | 91.5 | 26.9 | 1.61 | 2.35 | 3.96 | 0.8 | 45 | 15 | 0 | 41.04 | 13.341 | 0 | Diesel-backup
2025-01-13 02:00 | 13 | 1 | Summer | 2 | 24 | -1.6 | 6.7 | 30.2 | 131.4 | 7.88 | 4.59 | 12.47 | 1.6 | 45 | 15 | 0 | 32.53 | 10.929 | 0 | Diesel-backup
2025-01-13 03:00 | 13 | 1 | Summer | 3 | 24 | -1.1 | 4.47 | 60.7 | 136.8 | 8.21 | 0.13 | 8.34 | 1.1 | 45 | 15 | 0 | 36.66 | 12.123 | 0 | Diesel-backup
2025-01-13 04:00 | 13 | 1 | Summer | 4 | 24 | 1.5 | 8.51 | 60.7 | 178.7 | 10.72 | 17.6 | 28.32 | 0 | 45 | 15 | 0 | 16.68 | 5.942 | 0 | Diesel-backup
2025-01-13 05:00 | 13 | 1 | Summer | 5 | 24 | -7.7 | 7.28 | 19.5 | 340.9 | 20.45 | 7.56 | 28.01 | 7.7 | 45 | 15 | 0 | 16.99 | 6.046 | 0 | Diesel-backup
2025-01-13 06:00 | 13 | 1 | Summer | 6 | 24 | -2.8 | 5.04 | 22 | 387.2 | 23.23 | 0.51 | 23.74 | 2.8 | 45 | 15 | 0 | 21.26 | 7.449 | 0 | Diesel-backup
2025-01-13 07:00 | 13 | 1 | Summer | 7 | 24 | -2.1 | 2.76 | 80.7 | 205.5 | 12.33 | 0 | 12.33 | 2.1 | 45 | 15 | 0 | 32.67 | 10.97 | 0 | Diesel-backup
2025-01-13 08:00 | 13 | 1 | Summer | 8 | 24 | -1.9 | 4.81 | 4.2 | 550.1 | 33.01 | 0.31 | 33.32 | 1.9 | 47.23 | 15 | 0 | 13.91 | 5.005 | 0 | Diesel-backup
2025-01-13 09:00 | 13 | 1 | Summer | 9 | 24 | -3.3 | 4.6 | 29 | 474.1 | 28.45 | 0.19 | 28.64 | 3.3 | 51.35 | 15 | 0 | 22.71 | 7.915 | 0 | Diesel-backup
2025-01-13 10:00 | 13 | 1 | Summer | 10 | 24 | -6.2 | 4.31 | 50.6 | 393 | 23.58 | 0.07 | 23.65 | 6.2 | 45 | 15 | 0 | 21.35 | 7.478 | 0 | Diesel-backup
2025-01-13 11:00 | 13 | 1 | Summer | 11 | 24 | -1.3 | 2.04 | 12.9 | 587.6 | 35.26 | 0 | 35.26 | 1.3 | 50.74 | 15 | 0 | 15.48 | 5.539 | 0 | Diesel-backup
2025-01-13 12:00 | 13 | 1 | Summer | 12 | 24 | 2 | 13.75 | 51.7 | 401.7 | 24.1 | 120 | 144.1 | 0 | 45 | 51.47 | 99.1 | 0 | 0 | 0 | Normal
2025-01-13 13:00 | 13 | 1 | Summer | 13 | 24 | -4.8 | 13.37 | 54.7 | 383.7 | 23.02 | 120 | 143.02 | 4.8 | 49.34 | 85.94 | 93.68 | 0 | 0 | 0 | Normal
2025-01-13 14:00 | 13 | 1 | Summer | 14 | 24 | 0.9 | 5.92 | 59.3 | 352 | 21.12 | 1.98 | 23.1 | 0 | 50.75 | 74.88 | -27.65 | 0 | 0 | 0 | Battery-supported
2025-01-13 15:00 | 13 | 1 | Summer | 15 | 24 | -1.3 | 7.43 | 19.3 | 518.2 | 31.09 | 8.5 | 39.59 | 1.3 | 48.15 | 71.46 | -8.56 | 0 | 0 | 0 | Battery-supported
2025-01-13 16:00 | 13 | 1 | Summer | 16 | 24 | -0.4 | 8.43 | 48.4 | 361.8 | 21.71 | 16.77 | 38.48 | 0.4 | 45 | 68.85 | -6.52 | 0 | 0 | 0 | Battery-supported
2025-01-13 17:00 | 13 | 1 | Summer | 17 | 24 | -2.3 | 5.98 | 67.7 | 256 | 15.36 | 2.13 | 17.49 | 2.3 | 45 | 57.85 | -27.51 | 0 | 0 | 0 | Battery-supported
2025-01-13 18:00 | 13 | 1 | Summer | 18 | 24 | -0.4 | 7.75 | 62.5 | 246.5 | 14.79 | 10.74 | 25.53 | 0.4 | 45 | 50.06 | -19.47 | 0 | 0 | 0 | Battery-supported
2025-01-13 19:00 | 13 | 1 | Summer | 19 | 24 | 3.3 | 9.12 | 59.3 | 221.7 | 13.3 | 24.84 | 38.14 | 0 | 45 | 47.32 | -6.86 | 0 | 0 | 0 | Battery-supported
2025-01-13 20:00 | 13 | 1 | Summer | 20 | 24 | 1.8 | 7.12 | 11.5 | 299.6 | 17.98 | 6.64 | 24.62 | 0 | 48.05 | 37.94 | -23.43 | 0 | 0 | 0 | Battery-supported
2025-01-13 21:00 | 13 | 1 | Summer | 21 | 24 | 4.3 | 10.05 | 8.7 | 234.7 | 14.08 | 39.33 | 53.41 | 0 | 45 | 41.04 | 8.41 | 0 | 0 | 0 | Normal
2025-01-13 22:00 | 13 | 1 | Summer | 22 | 24 | 2.9 | 4.22 | 80.2 | 67.7 | 4.06 | 0.05 | 4.11 | 0 | 45 | 24.68 | -40.89 | 0 | 0 | 0 | Battery-supported
2025-01-13 23:00 | 13 | 1 | Summer | 23 | 24 | 1 | 6.4 | 47 | 55.4 | 3.32 | 3.41 | 6.73 | 0 | 45 | 15 | -24.2 | 14.07 | 5.058 | 0 | Diesel-backup
2025-01-14 | 14 | 1 | Summer | 0 | 24 | 3.6 | 24.67 | 24.3 | 0 | 0 | 120 | 120 | 0 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-01-14 01:00 | 14 | 1 | Summer | 1 | 24 | 0.4 | 11.4 | 83.9 | 31.7 | 1.9 | 69.01 | 70.91 | 0 | 45 | 52.13 | 25.91 | 0 | 0 | 0 | Normal
2025-01-14 02:00 | 14 | 1 | Summer | 2 | 24 | 0.8 | 7.22 | 59.4 | 94.1 | 5.65 | 7.21 | 12.86 | 0 | 45 | 39.28 | -32.14 | 0 | 0 | 0 | Battery-supported
2025-01-14 03:00 | 14 | 1 | Summer | 3 | 24 | -2 | 3.46 | 46 | 164.5 | 9.87 | 0 | 9.87 | 2 | 45 | 25.23 | -35.13 | 0 | 0 | 0 | Battery-supported
2025-01-14 04:00 | 14 | 1 | Summer | 4 | 24 | -1.6 | 6.6 | 8.7 | 306.6 | 18.4 | 4.17 | 22.57 | 1.6 | 45 | 16.25 | -22.43 | 0 | 0 | 0 | Battery-supported
2025-01-14 05:00 | 14 | 1 | Summer | 5 | 24 | -3.6 | 10.97 | 51.3 | 245.6 | 14.74 | 58.34 | 73.08 | 3.6 | 45 | 26.59 | 28.08 | 0 | 0 | 0 | Normal
2025-01-14 06:00 | 14 | 1 | Summer | 6 | 24 | -0.1 | 9.71 | 23.2 | 383 | 22.98 | 33.52 | 56.5 | 0.1 | 45 | 30.82 | 11.5 | 0 | 0 | 0 | Normal
2025-01-14 07:00 | 14 | 1 | Summer | 7 | 24 | -5 | 1.68 | 70.7 | 244.5 | 14.67 | 0 | 14.67 | 5 | 45 | 18.69 | -30.33 | 0 | 0 | 0 | Battery-supported
2025-01-14 08:00 | 14 | 1 | Summer | 8 | 24 | -0.8 | 2.09 | 49.2 | 358.6 | 21.52 | 0 | 21.52 | 0.8 | 49.11 | 15 | -9.22 | 18.37 | 6.504 | 0 | Diesel-backup
2025-01-14 09:00 | 14 | 1 | Summer | 9 | 24 | -2.9 | 2.17 | 71.5 | 281.1 | 16.87 | 0 | 16.87 | 2.9 | 49.91 | 15 | 0 | 33.04 | 11.079 | 0 | Diesel-backup
2025-01-14 10:00 | 14 | 1 | Summer | 10 | 24 | 0.3 | 8.5 | 72.2 | 290.5 | 17.43 | 17.5 | 34.93 | 0 | 45 | 15 | 0 | 10.07 | 3.673 | 0 | Diesel-backup
2025-01-14 11:00 | 14 | 1 | Summer | 11 | 24 | -0.4 | 2.19 | 40.1 | 454.7 | 27.28 | 0 | 27.28 | 0.4 | 45 | 15 | 0 | 17.72 | 6.289 | 0 | Diesel-backup
2025-01-14 12:00 | 14 | 1 | Summer | 12 | 24 | 2.3 | 3.36 | 74.6 | 289.1 | 17.35 | 0 | 17.35 | 0 | 45 | 15 | 0 | 27.65 | 9.462 | 0 | Diesel-backup
2025-01-14 13:00 | 14 | 1 | Summer | 13 | 24 | 0.2 | 5.85 | 28.2 | 512.6 | 30.76 | 1.82 | 32.58 | 0 | 45 | 15 | 0 | 12.42 | 4.492 | 0 | Diesel-backup
2025-01-14 14:00 | 14 | 1 | Summer | 14 | 24 | -4.5 | 12 | 41.9 | 434.6 | 26.08 | 85.95 | 112.03 | 4.5 | 46.5 | 39.12 | 65.53 | 0 | 0 | 0 | Normal
2025-01-14 15:00 | 14 | 1 | Summer | 15 | 24 | -0.8 | 8.74 | 57.9 | 343.1 | 20.59 | 20.14 | 40.73 | 0.8 | 45 | 37.41 | -4.27 | 0 | 0 | 0 | Battery-supported
2025-01-14 16:00 | 14 | 1 | Summer | 16 | 24 | -2.8 | 5.42 | 41.4 | 391.8 | 23.51 | 0.99 | 24.5 | 2.8 | 48.81 | 27.68 | -24.31 | 0 | 0 | 0 | Battery-supported
2025-01-14 17:00 | 14 | 1 | Summer | 17 | 24 | -1.1 | 10.22 | 84.8 | 189.3 | 11.36 | 42.47 | 53.83 | 1.1 | 45 | 30.93 | 8.83 | 0 | 0 | 0 | Normal
2025-01-14 18:00 | 14 | 1 | Summer | 18 | 24 | 3.6 | 18.77 | 13.4 | 417 | 25.02 | 120 | 145.02 | 0 | 47.78 | 66.72 | 97.24 | 0 | 0 | 0 | Normal
2025-01-14 19:00 | 14 | 1 | Summer | 19 | 24 | 1.8 | 6.63 | 73.5 | 179.2 | 10.75 | 4.29 | 15.04 | 0 | 45 | 54.73 | -29.96 | 0 | 0 | 0 | Battery-supported
2025-01-14 20:00 | 14 | 1 | Summer | 20 | 24 | -1 | 2.65 | 39.8 | 230.1 | 13.81 | 0 | 13.81 | 1 | 45 | 42.26 | -31.19 | 0 | 0 | 0 | Battery-supported
2025-01-14 21:00 | 14 | 1 | Summer | 21 | 24 | -1.8 | 3.44 | 58 | 141.7 | 8.5 | 0 | 8.5 | 1.8 | 45 | 27.66 | -36.5 | 0 | 0 | 0 | Battery-supported
2025-01-14 22:00 | 14 | 1 | Summer | 22 | 24 | 0.4 | 3.42 | 65.7 | 86.1 | 5.17 | 0 | 5.17 | 0 | 45 | 15 | -31.64 | 8.19 | 3.006 | 0 | Diesel-backup
2025-01-14 23:00 | 14 | 1 | Summer | 23 | 24 | -2.6 | 3.95 | 44.1 | 57.3 | 3.44 | 0.01 | 3.45 | 2.6 | 45 | 15 | 0 | 41.55 | 13.479 | 0 | Diesel-backup
2025-01-15 | 15 | 1 | Summer | 0 | 24 | -1.7 | 5.19 | 0 | 0 | 0 | 0.68 | 0.68 | 1.7 | 45 | 15 | 0 | 44.32 | 14.221 | 0 | Diesel-backup
2025-01-15 01:00 | 15 | 1 | Summer | 1 | 24 | 0.1 | 7.58 | 65.8 | 43.4 | 2.6 | 9.51 | 12.11 | 0 | 45 | 15 | 0 | 32.89 | 11.035 | 0 | Diesel-backup
2025-01-15 02:00 | 15 | 1 | Summer | 2 | 24 | 1.5 | 2.36 | 23.6 | 139.8 | 8.39 | 0 | 8.39 | 0 | 45 | 15 | 0 | 36.61 | 12.108 | 0 | Diesel-backup
2025-01-15 03:00 | 15 | 1 | Summer | 3 | 24 | 0 | 2.69 | 21.9 | 209.8 | 12.59 | 0 | 12.59 | 0 | 45 | 15 | 0 | 32.41 | 10.893 | 0 | Diesel-backup
2025-01-15 04:00 | 15 | 1 | Summer | 4 | 24 | -6.8 | 9.08 | 38.7 | 232.8 | 13.97 | 24.32 | 38.29 | 6.8 | 49.23 | 15 | 0 | 10.94 | 3.978 | 0 | Diesel-backup
2025-01-15 05:00 | 15 | 1 | Summer | 5 | 24 | -1.4 | 4.62 | 86.7 | 139.8 | 8.39 | 0.2 | 8.59 | 1.4 | 45 | 15 | 0 | 36.41 | 12.052 | 0 | Diesel-backup
2025-01-15 06:00 | 15 | 1 | Summer | 6 | 24 | -2.1 | 3.66 | 56.1 | 268.8 | 16.13 | 0 | 16.13 | 2.1 | 45 | 15 | 0 | 28.87 | 9.834 | 0 | Diesel-backup
2025-01-15 07:00 | 15 | 1 | Summer | 7 | 24 | -1.5 | 5.56 | 64.1 | 270.3 | 16.22 | 1.22 | 17.44 | 1.5 | 45 | 15 | 0 | 27.56 | 9.434 | 0 | Diesel-backup
2025-01-15 08:00 | 15 | 1 | Summer | 8 | 24 | 1.1 | 13.18 | 49.5 | 357.2 | 21.43 | 120 | 141.43 | 0 | 45 | 50.49 | 96.43 | 0 | 0 | 0 | Normal
2025-01-15 09:00 | 15 | 1 | Summer | 9 | 24 | -7 | 9.8 | 20.4 | 513.2 | 30.79 | 35 | 65.79 | 7 | 45.66 | 57.89 | 20.13 | 0 | 0 | 0 | Normal
2025-01-15 10:00 | 15 | 1 | Summer | 10 | 24 | -3.6 | 9.42 | 48 | 405.3 | 24.32 | 29.04 | 53.36 | 3.6 | 47.33 | 60.11 | 6.03 | 0 | 0 | 0 | Normal
2025-01-15 11:00 | 15 | 1 | Summer | 11 | 24 | -0.8 | 15.78 | 34.6 | 481.4 | 28.88 | 120 | 148.88 | 0.8 | 45 | 95 | 94.8 | 0 | 0 | 0 | Normal
2025-01-15 12:00 | 15 | 1 | Summer | 12 | 24 | -5.2 | 7.8 | 76.9 | 277.8 | 16.67 | 11.13 | 27.8 | 5.2 | 50.56 | 85.9 | -22.76 | 0 | 0 | 0 | Battery-supported
2025-01-15 13:00 | 15 | 1 | Summer | 13 | 24 | 1.9 | 16.59 | 76.3 | 278.1 | 16.69 | 120 | 136.69 | 0 | 45 | 95 | 24.74 | 0 | 0 | 0 | Normal
2025-01-15 14:00 | 15 | 1 | Summer | 14 | 24 | -0.2 | 17.34 | 64.4 | 327.8 | 19.67 | 120 | 139.67 | 0.2 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-01-15 15:00 | 15 | 1 | Summer | 15 | 24 | 1.3 | 2.42 | 84.1 | 223.7 | 13.42 | 0 | 13.42 | 0 | 45 | 82.37 | -31.58 | 0 | 0 | 0 | Battery-supported
2025-01-15 16:00 | 15 | 1 | Summer | 16 | 24 | -1.5 | 1.94 | 58.1 | 320.3 | 19.22 | 0 | 19.22 | 1.5 | 45 | 72.06 | -25.78 | 0 | 0 | 0 | Battery-supported
2025-01-15 17:00 | 15 | 1 | Summer | 17 | 24 | 1.9 | 3.26 | 18.2 | 449.5 | 26.97 | 0 | 26.97 | 0 | 45 | 64.84 | -18.03 | 0 | 0 | 0 | Battery-supported
2025-01-15 18:00 | 15 | 1 | Summer | 18 | 24 | 2.6 | 12.45 | 43.2 | 313.6 | 18.82 | 100.34 | 119.16 | 0 | 45 | 92.13 | 74.16 | 0 | 0 | 0 | Normal
2025-01-15 19:00 | 15 | 1 | Summer | 19 | 24 | 1 | 5.63 | 21.5 | 334.8 | 20.09 | 1.35 | 21.44 | 0 | 45 | 82.71 | -23.56 | 0 | 0 | 0 | Battery-supported
2025-01-15 20:00 | 15 | 1 | Summer | 20 | 24 | 1 | 5.2 | 39.9 | 229.9 | 13.79 | 0.69 | 14.48 | 0 | 45 | 70.5 | -30.52 | 0 | 0 | 0 | Battery-supported
2025-01-15 21:00 | 15 | 1 | Summer | 21 | 24 | 1 | 10.37 | 50.3 | 156.3 | 9.38 | 45.38 | 54.76 | 0 | 45 | 74.09 | 9.76 | 0 | 0 | 0 | Normal
2025-01-15 22:00 | 15 | 1 | Summer | 22 | 24 | -1.6 | 4.47 | 37.5 | 122.1 | 7.33 | 0.13 | 7.46 | 1.6 | 45 | 59.08 | -37.54 | 0 | 0 | 0 | Battery-supported
2025-01-15 23:00 | 15 | 1 | Summer | 23 | 24 | -0.3 | 7.21 | 78.8 | 35 | 2.1 | 7.15 | 9.25 | 0.3 | 45 | 44.78 | -35.75 | 0 | 0 | 0 | Battery-supported
2025-01-16 | 16 | 1 | Summer | 0 | 24 | -0.6 | 9.07 | 6.7 | 0 | 0 | 24.19 | 24.19 | 0.6 | 45 | 36.45 | -20.81 | 0 | 0 | 0 | Battery-supported
2025-01-16 01:00 | 16 | 1 | Summer | 1 | 24 | 0.2 | 3.47 | 23.3 | 70.7 | 4.24 | 0 | 4.24 | 0 | 45 | 20.15 | -40.76 | 0 | 0 | 0 | Battery-supported
2025-01-16 02:00 | 16 | 1 | Summer | 2 | 24 | 1.2 | 2.94 | 20.6 | 143.5 | 8.61 | 0 | 8.61 | 0 | 45 | 15 | -12.88 | 23.51 | 8.171 | 0 | Diesel-backup
2025-01-16 03:00 | 16 | 1 | Summer | 3 | 24 | -3.7 | 6.61 | 82.4 | 95.9 | 5.75 | 4.21 | 9.96 | 3.7 | 45 | 15 | 0 | 35.04 | 11.66 | 0 | Diesel-backup
2025-01-16 04:00 | 16 | 1 | Summer | 4 | 24 | -2 | 7.12 | 20.4 | 277.9 | 16.67 | 6.64 | 23.31 | 2 | 45 | 15 | 0 | 21.69 | 7.588 | 0 | Diesel-backup
2025-01-16 05:00 | 16 | 1 | Summer | 5 | 24 | 1.2 | 9.92 | 58.7 | 223.4 | 13.4 | 37.04 | 50.44 | 0 | 45 | 17 | 5.44 | 0 | 0 | 0 | Normal
2025-01-16 06:00 | 16 | 1 | Summer | 6 | 24 | -3.9 | 3.21 | 54 | 276.1 | 16.57 | 0 | 16.57 | 3.9 | 45 | 15 | -5 | 23.43 | 8.143 | 0 | Diesel-backup
2025-01-16 07:00 | 16 | 1 | Summer | 7 | 24 | -4.3 | 4.03 | 21.1 | 437.9 | 26.27 | 0.02 | 26.29 | 4.3 | 45 | 15 | 0 | 18.71 | 6.617 | 0 | Diesel-backup
2025-01-16 08:00 | 16 | 1 | Summer | 8 | 24 | -2.1 | 17.24 | 16 | 500.1 | 30.01 | 120 | 150.01 | 2.1 | 46.3 | 53.17 | 103.71 | 0 | 0 | 0 | Normal
2025-01-16 09:00 | 16 | 1 | Summer | 9 | 24 | -0.6 | 11.25 | 11.8 | 552.3 | 33.14 | 65.15 | 98.29 | 0.6 | 45 | 72.78 | 53.29 | 0 | 0 | 0 | Normal
2025-01-16 10:00 | 16 | 1 | Summer | 10 | 24 | -2.3 | 5.96 | 65.4 | 322.9 | 19.37 | 2.08 | 21.45 | 2.3 | 46.25 | 62.86 | -24.8 | 0 | 0 | 0 | Battery-supported
2025-01-16 11:00 | 16 | 1 | Summer | 11 | 24 | 0.9 | 12.28 | 83.9 | 241.1 | 14.47 | 94.73 | 109.2 | 0 | 45 | 86.48 | 64.2 | 0 | 0 | 0 | Normal
2025-01-16 12:00 | 16 | 1 | Summer | 12 | 24 | 0.1 | 3.21 | 45.2 | 433.7 | 26.02 | 0 | 26.02 | 0 | 47.01 | 78.09 | -20.99 | 0 | 0 | 0 | Battery-supported
2025-01-16 13:00 | 16 | 1 | Summer | 13 | 24 | 0.5 | 5.54 | 37.2 | 468.9 | 28.13 | 1.19 | 29.32 | 0 | 48.55 | 70.39 | -19.23 | 0 | 0 | 0 | Battery-supported
2025-01-16 14:00 | 16 | 1 | Summer | 14 | 24 | 0.2 | 7.09 | 4.1 | 613.9 | 36.83 | 6.48 | 43.31 | 0 | 45 | 69.72 | -1.69 | 0 | 0 | 0 | Battery-supported
2025-01-16 15:00 | 16 | 1 | Summer | 15 | 24 | 4.5 | 5.15 | 66.9 | 302 | 18.12 | 0.63 | 18.75 | 0 | 46.55 | 58.6 | -27.8 | 0 | 0 | 0 | Battery-supported
2025-01-16 16:00 | 16 | 1 | Summer | 16 | 24 | -0.7 | 5.27 | 46.2 | 371.3 | 22.28 | 0.78 | 23.06 | 0.7 | 45 | 49.82 | -21.94 | 0 | 0 | 0 | Battery-supported
2025-01-16 17:00 | 16 | 1 | Summer | 17 | 24 | -4.3 | 9.63 | 15.7 | 459.3 | 27.56 | 32.24 | 59.8 | 4.3 | 45 | 55.27 | 14.8 | 0 | 0 | 0 | Normal
2025-01-16 18:00 | 16 | 1 | Summer | 18 | 24 | 3.8 | 11.34 | 89.6 | 152.2 | 9.13 | 67.45 | 76.58 | 0 | 45 | 66.89 | 31.58 | 0 | 0 | 0 | Normal
2025-01-16 19:00 | 16 | 1 | Summer | 19 | 24 | -0.6 | 4.81 | 34 | 297.6 | 17.86 | 0.31 | 18.17 | 0.6 | 45 | 56.16 | -26.83 | 0 | 0 | 0 | Battery-supported
2025-01-16 20:00 | 16 | 1 | Summer | 20 | 24 | 0.7 | 2.51 | 74.9 | 143.8 | 8.63 | 0 | 8.63 | 0 | 47.23 | 40.72 | -38.6 | 0 | 0 | 0 | Battery-supported
2025-01-16 21:00 | 16 | 1 | Summer | 21 | 24 | 3.3 | 2.14 | 63.1 | 132.1 | 7.93 | 0 | 7.93 | 0 | 45 | 25.89 | -37.07 | 0 | 0 | 0 | Battery-supported
2025-01-16 22:00 | 16 | 1 | Summer | 22 | 24 | -3.2 | 1.35 | 82.4 | 64.9 | 3.89 | 0 | 3.89 | 3.2 | 45 | 15 | -27.22 | 13.89 | 4.997 | 0 | Diesel-backup
2025-01-16 23:00 | 16 | 1 | Summer | 23 | 24 | -2.7 | 15.63 | 26.8 | 68.4 | 4.1 | 120 | 124.1 | 2.7 | 45 | 44.11 | 79.1 | 0 | 0 | 0 | Normal
2025-01-17 | 17 | 1 | Summer | 0 | 24 | -3.8 | 9.66 | 57.8 | 0 | 0 | 32.72 | 32.72 | 3.8 | 45 | 39.2 | -12.28 | 0 | 0 | 0 | Battery-supported
2025-01-17 01:00 | 17 | 1 | Summer | 1 | 24 | -2.4 | 8.46 | 49.2 | 54 | 3.24 | 17.08 | 20.32 | 2.4 | 45 | 29.32 | -24.68 | 0 | 0 | 0 | Battery-supported
2025-01-17 02:00 | 17 | 1 | Summer | 2 | 24 | 0 | 4.42 | 60.2 | 93.1 | 5.59 | 0.11 | 5.7 | 0 | 45 | 15 | -35.81 | 3.49 | 1.301 | 0 | Diesel-backup
2025-01-17 03:00 | 17 | 1 | Summer | 3 | 24 | -0.2 | 4.4 | 28.2 | 197.9 | 11.87 | 0.1 | 11.97 | 0.2 | 45 | 15 | 0 | 33.03 | 11.076 | 0 | Diesel-backup
2025-01-17 04:00 | 17 | 1 | Summer | 4 | 24 | -1.1 | 11.55 | 44.3 | 218.9 | 13.13 | 73.01 | 86.14 | 1.1 | 45 | 30.14 | 41.14 | 0 | 0 | 0 | Normal
2025-01-17 05:00 | 17 | 1 | Summer | 5 | 24 | -5.2 | 1.95 | 31.9 | 303.7 | 18.22 | 0 | 18.22 | 5.2 | 45 | 19.43 | -26.78 | 0 | 0 | 0 | Battery-supported
2025-01-17 06:00 | 17 | 1 | Summer | 6 | 24 | -7.4 | 4.95 | 69.7 | 221.3 | 13.28 | 0.43 | 13.71 | 7.4 | 47.65 | 15 | -11.07 | 22.87 | 7.967 | 0 | Diesel-backup
2025-01-17 07:00 | 17 | 1 | Summer | 7 | 24 | -2.3 | 12.51 | 8.7 | 486.3 | 29.18 | 102.37 | 131.55 | 2.3 | 45 | 46.85 | 86.55 | 0 | 0 | 0 | Normal
2025-01-17 08:00 | 17 | 1 | Summer | 8 | 24 | -3.5 | 4.94 | 33.9 | 423.7 | 25.42 | 0.42 | 25.84 | 3.5 | 49.09 | 37.55 | -23.25 | 0 | 0 | 0 | Battery-supported
2025-01-17 09:00 | 17 | 1 | Summer | 9 | 24 | -1.4 | 9.37 | 8.7 | 566.4 | 33.98 | 28.31 | 62.29 | 1.4 | 45 | 43.91 | 17.29 | 0 | 0 | 0 | Normal
2025-01-17 10:00 | 17 | 1 | Summer | 10 | 24 | -0.8 | 6.11 | 11.2 | 580.2 | 34.81 | 2.49 | 37.3 | 0.8 | 46.43 | 40.26 | -9.13 | 0 | 0 | 0 | Battery-supported
2025-01-17 11:00 | 17 | 1 | Summer | 11 | 24 | -1.8 | 0.67 | 61.1 | 352.1 | 21.13 | 0 | 21.13 | 1.8 | 46.01 | 30.31 | -24.88 | 0 | 0 | 0 | Battery-supported
2025-01-17 12:00 | 17 | 1 | Summer | 12 | 24 | -0.1 | 5.95 | 30.1 | 507.7 | 30.46 | 2.06 | 32.52 | 0.1 | 45 | 25.32 | -12.48 | 0 | 0 | 0 | Battery-supported
2025-01-17 13:00 | 17 | 1 | Summer | 13 | 24 | -0.9 | 6.69 | 68.2 | 317.8 | 19.07 | 4.54 | 23.61 | 0.9 | 45.55 | 16.54 | -21.94 | 0 | 0 | 0 | Battery-supported
2025-01-17 14:00 | 17 | 1 | Summer | 14 | 24 | 0.2 | 5.67 | 2.5 | 621.6 | 37.3 | 1.43 | 38.73 | 0 | 45 | 15 | -3.85 | 2.42 | 0.905 | 0 | Diesel-backup
2025-01-17 15:00 | 17 | 1 | Summer | 15 | 24 | -2.2 | 2.84 | 35 | 446.7 | 26.8 | 0 | 26.8 | 2.2 | 45 | 15 | 0 | 18.2 | 6.448 | 0 | Diesel-backup
2025-01-17 16:00 | 17 | 1 | Summer | 16 | 24 | -0.7 | 5.71 | 11.8 | 517.6 | 31.06 | 1.51 | 32.57 | 0.7 | 45 | 15 | 0 | 12.43 | 4.496 | 0 | Diesel-backup
2025-01-17 17:00 | 17 | 1 | Summer | 17 | 24 | 0.5 | 1.43 | 31.9 | 395.9 | 23.75 | 0 | 23.75 | 0 | 47.58 | 15 | 0 | 23.83 | 8.271 | 0 | Diesel-backup
2025-01-17 18:00 | 17 | 1 | Summer | 18 | 24 | 2.1 | 4.91 | 70.8 | 217.5 | 13.05 | 0.39 | 13.44 | 0 | 45 | 15 | 0 | 31.56 | 10.642 | 0 | Diesel-backup
2025-01-17 19:00 | 17 | 1 | Summer | 19 | 24 | -0.4 | 9.81 | 32.3 | 302.6 | 18.16 | 35.16 | 53.32 | 0.4 | 45 | 18.06 | 8.32 | 0 | 0 | 0 | Normal
2025-01-17 20:00 | 17 | 1 | Summer | 20 | 24 | 1.6 | 15.15 | 52.3 | 199.2 | 11.95 | 120 | 131.95 | 0 | 45 | 50.06 | 86.95 | 0 | 0 | 0 | Normal
2025-01-17 21:00 | 17 | 1 | Summer | 21 | 24 | -0.1 | 13.74 | 47.1 | 162.4 | 9.74 | 120 | 129.74 | 0.1 | 45 | 81.24 | 84.74 | 0 | 0 | 0 | Normal
2025-01-17 22:00 | 17 | 1 | Summer | 22 | 24 | 0 | 3.16 | 20 | 144.3 | 8.66 | 0 | 8.66 | 0 | 45 | 66.71 | -36.34 | 0 | 0 | 0 | Battery-supported
2025-01-17 23:00 | 17 | 1 | Summer | 23 | 24 | 1.9 | 2.22 | 53.8 | 51.1 | 3.07 | 0 | 3.07 | 0 | 45 | 49.94 | -41.93 | 0 | 0 | 0 | Battery-supported
2025-01-18 | 18 | 1 | Summer | 0 | 24 | -4.7 | 7.09 | 50.4 | 0 | 0 | 6.48 | 6.48 | 4.7 | 45 | 34.53 | -38.52 | 0 | 0 | 0 | Battery-supported
2025-01-18 01:00 | 18 | 1 | Summer | 1 | 24 | -3.5 | 6.43 | 71.3 | 39.8 | 2.39 | 3.52 | 5.91 | 3.5 | 45 | 18.89 | -39.09 | 0 | 0 | 0 | Battery-supported
2025-01-18 02:00 | 18 | 1 | Summer | 2 | 24 | -4.3 | 8.97 | 42.3 | 116 | 6.96 | 22.91 | 29.87 | 4.3 | 45 | 15 | -9.73 | 5.4 | 2.002 | 0 | Diesel-backup
2025-01-18 03:00 | 18 | 1 | Summer | 3 | 24 | -6.5 | 4.18 | 59.8 | 138.5 | 8.31 | 0.04 | 8.35 | 6.5 | 45 | 15 | 0 | 36.65 | 12.12 | 0 | Diesel-backup
2025-01-18 04:00 | 18 | 1 | Summer | 4 | 24 | -3.3 | 6.55 | 48.1 | 209.6 | 12.58 | 3.97 | 16.55 | 3.3 | 45 | 15 | 0 | 28.45 | 9.707 | 0 | Diesel-backup
2025-01-18 05:00 | 18 | 1 | Summer | 5 | 24 | -0.4 | 6.34 | 79.1 | 162.4 | 9.74 | 3.21 | 12.95 | 0.4 | 45 | 15 | 0 | 32.05 | 10.787 | 0 | Diesel-backup
2025-01-18 06:00 | 18 | 1 | Summer | 6 | 24 | -2.9 | 5.02 | 76.3 | 198.2 | 11.89 | 0.49 | 12.38 | 2.9 | 45 | 15 | 0 | 32.62 | 10.955 | 0 | Diesel-backup
2025-01-18 07:00 | 18 | 1 | Summer | 7 | 24 | -2 | 1.84 | 88 | 177.1 | 10.63 | 0 | 10.63 | 2 | 45 | 15 | 0 | 34.37 | 11.466 | 0 | Diesel-backup
2025-01-18 08:00 | 18 | 1 | Summer | 8 | 24 | -0.1 | 9.73 | 18.5 | 489.4 | 29.36 | 33.84 | 63.2 | 0.1 | 45 | 21.7 | 18.2 | 0 | 0 | 0 | Normal
2025-01-18 09:00 | 18 | 1 | Summer | 9 | 24 | 0.5 | 7.12 | 78.3 | 250.2 | 15.01 | 6.64 | 21.65 | 0 | 45 | 15 | -16.74 | 6.61 | 2.439 | 0 | Diesel-backup
2025-01-18 10:00 | 18 | 1 | Summer | 10 | 24 | -2.5 | 10.12 | 19.6 | 540.4 | 32.42 | 40.61 | 73.03 | 2.5 | 45 | 25.32 | 28.03 | 0 | 0 | 0 | Normal
2025-01-18 11:00 | 18 | 1 | Summer | 11 | 24 | 0.9 | 11.55 | 52.5 | 394.3 | 23.66 | 73.01 | 96.67 | 0 | 45 | 44.33 | 51.67 | 0 | 0 | 0 | Normal
2025-01-18 12:00 | 18 | 1 | Summer | 12 | 24 | -1.6 | 6 | 42.3 | 448 | 26.88 | 2.19 | 29.07 | 1.6 | 46.13 | 37.51 | -17.06 | 0 | 0 | 0 | Battery-supported
2025-01-18 13:00 | 18 | 1 | Summer | 13 | 24 | -3.2 | 9.76 | 33.6 | 486.5 | 29.19 | 34.33 | 63.52 | 3.2 | 48.43 | 43.06 | 15.09 | 0 | 0 | 0 | Normal
2025-01-18 14:00 | 18 | 1 | Summer | 14 | 24 | -2.3 | 15.36 | 66 | 320 | 19.2 | 120 | 139.2 | 2.3 | 47.23 | 76.9 | 91.97 | 0 | 0 | 0 | Normal
2025-01-18 15:00 | 18 | 1 | Summer | 15 | 24 | -3.9 | 18.19 | 33.7 | 452.9 | 27.17 | 120 | 147.17 | 3.9 | 52.11 | 95 | 49.17 | 0 | 0 | 0 | Normal
2025-01-18 16:00 | 18 | 1 | Summer | 16 | 24 | -2.2 | 7.65 | 49.6 | 356.6 | 21.4 | 10 | 31.4 | 2.2 | 47.94 | 88.38 | -16.54 | 0 | 0 | 0 | Battery-supported
2025-01-18 17:00 | 18 | 1 | Summer | 17 | 24 | -0.7 | 8.01 | 54.5 | 307.9 | 18.47 | 12.84 | 31.31 | 0.7 | 51.72 | 80.22 | -20.41 | 0 | 0 | 0 | Battery-supported
2025-01-18 18:00 | 18 | 1 | Summer | 18 | 24 | 2.1 | 7.57 | 37.3 | 334.1 | 20.05 | 9.44 | 29.49 | 0 | 47.13 | 73.16 | -17.64 | 0 | 0 | 0 | Battery-supported
2025-01-18 19:00 | 18 | 1 | Summer | 19 | 24 | 4.2 | 8.79 | 64.1 | 207.3 | 12.44 | 20.72 | 33.16 | 0 | 47 | 67.63 | -13.84 | 0 | 0 | 0 | Battery-supported
2025-01-18 20:00 | 18 | 1 | Summer | 20 | 24 | -2.6 | 11.26 | 60.6 | 178.9 | 10.73 | 65.4 | 76.13 | 2.6 | 45 | 79.08 | 31.13 | 0 | 0 | 0 | Normal
2025-01-18 21:00 | 18 | 1 | Summer | 21 | 24 | 1.3 | 7.48 | 83.9 | 93.2 | 5.59 | 8.82 | 14.41 | 0 | 45 | 66.85 | -30.59 | 0 | 0 | 0 | Battery-supported
2025-01-18 22:00 | 18 | 1 | Summer | 22 | 24 | -2 | 17.59 | 13 | 153.2 | 9.19 | 120 | 129.19 | 2 | 45 | 95 | 76.5 | 0 | 0 | 0 | Normal
2025-01-18 23:00 | 18 | 1 | Summer | 23 | 24 | 1.1 | 16.19 | 17.7 | 74.2 | 4.45 | 120 | 124.45 | 0 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-01-19 | 19 | 1 | Summer | 0 | 24 | -0.6 | 6.68 | 37.3 | 0 | 0 | 4.5 | 4.5 | 0.6 | 45 | 78.8 | -40.5 | 0 | 0 | 0 | Battery-supported
2025-01-19 01:00 | 19 | 1 | Summer | 1 | 24 | -4.7 | 6.66 | 72.6 | 39 | 2.34 | 4.42 | 6.76 | 4.7 | 45 | 63.5 | -38.24 | 0 | 0 | 0 | Battery-supported
2025-01-19 02:00 | 19 | 1 | Summer | 2 | 24 | 1 | 4.78 | 40.6 | 118 | 7.08 | 0.29 | 7.37 | 0 | 45 | 48.45 | -37.63 | 0 | 0 | 0 | Battery-supported
2025-01-19 03:00 | 19 | 1 | Summer | 3 | 24 | -2.7 | 9.07 | 40.4 | 175 | 10.5 | 24.19 | 34.69 | 2.7 | 45 | 44.33 | -10.31 | 0 | 0 | 0 | Battery-supported
2025-01-19 04:00 | 19 | 1 | Summer | 4 | 24 | -3 | 5.3 | 88.8 | 109.4 | 6.56 | 0.82 | 7.38 | 3 | 45 | 29.28 | -37.62 | 0 | 0 | 0 | Battery-supported
2025-01-19 05:00 | 19 | 1 | Summer | 5 | 24 | -4.4 | 4.64 | 3.8 | 387.8 | 23.27 | 0.21 | 23.48 | 4.4 | 45 | 20.67 | -21.52 | 0 | 0 | 0 | Battery-supported
2025-01-19 06:00 | 19 | 1 | Summer | 6 | 24 | -3.8 | 8.95 | 32.6 | 350.6 | 21.04 | 22.66 | 43.7 | 3.8 | 45 | 20.15 | -1.3 | 0 | 0 | 0 | Battery-supported
2025-01-19 07:00 | 19 | 1 | Summer | 7 | 24 | -1.5 | 3.04 | 46.8 | 337.9 | 20.27 | 0 | 20.27 | 1.5 | 45 | 15 | -12.88 | 11.85 | 4.295 | 0 | Diesel-backup
2025-01-19 08:00 | 19 | 1 | Summer | 8 | 24 | -2.9 | 11.38 | 0 | 568.1 | 34.09 | 68.48 | 102.57 | 2.9 | 54.15 | 32.82 | 48.42 | 0 | 0 | 0 | Normal
2025-01-19 09:00 | 19 | 1 | Summer | 9 | 24 | -1.8 | 9.17 | 88.9 | 201.8 | 12.11 | 25.51 | 37.62 | 1.8 | 46.82 | 29.14 | -9.2 | 0 | 0 | 0 | Battery-supported
2025-01-19 10:00 | 19 | 1 | Summer | 10 | 24 | -1.5 | 15.71 | 95.4 | 180.2 | 10.81 | 120 | 130.81 | 1.5 | 45 | 60.72 | 85.81 | 0 | 0 | 0 | Normal
2025-01-19 11:00 | 19 | 1 | Summer | 11 | 24 | 0.8 | 7.73 | 11.9 | 592.2 | 35.53 | 10.59 | 46.12 | 0 | 45 | 61.13 | 1.12 | 0 | 0 | 0 | Normal
2025-01-19 12:00 | 19 | 1 | Summer | 12 | 24 | -2.5 | 10.01 | 28.8 | 514.1 | 30.85 | 38.61 | 69.46 | 2.5 | 45 | 70.13 | 24.46 | 0 | 0 | 0 | Normal
2025-01-19 13:00 | 19 | 1 | Summer | 13 | 24 | -4.7 | 0.96 | 59 | 362.7 | 21.76 | 0 | 21.76 | 4.7 | 45.21 | 60.75 | -23.45 | 0 | 0 | 0 | Battery-supported
2025-01-19 14:00 | 19 | 1 | Summer | 14 | 24 | 1.3 | 10.77 | 69.8 | 302 | 18.12 | 53.78 | 71.9 | 0 | 45 | 70.65 | 26.9 | 0 | 0 | 0 | Normal
2025-01-19 15:00 | 19 | 1 | Summer | 15 | 24 | -1.4 | 13.13 | 39.3 | 427.3 | 25.64 | 120 | 145.64 | 1.4 | 45 | 95 | 66.17 | 0 | 0 | 0 | Normal
2025-01-19 16:00 | 19 | 1 | Summer | 16 | 24 | 2.2 | 7.22 | 86.5 | 199.7 | 11.98 | 7.21 | 19.19 | 0 | 45 | 84.68 | -25.81 | 0 | 0 | 0 | Battery-supported
2025-01-19 17:00 | 19 | 1 | Summer | 17 | 24 | 0.9 | 4.76 | 73.9 | 231.8 | 13.91 | 0.28 | 14.19 | 0 | 45 | 72.35 | -30.81 | 0 | 0 | 0 | Battery-supported
2025-01-19 18:00 | 19 | 1 | Summer | 18 | 24 | 0 | 7.84 | 78.5 | 190.7 | 11.44 | 11.44 | 22.88 | 0 | 45 | 63.5 | -22.12 | 0 | 0 | 0 | Battery-supported
2025-01-19 19:00 | 19 | 1 | Summer | 19 | 24 | 1.2 | 11.37 | 65.4 | 203.6 | 12.22 | 68.22 | 80.44 | 0 | 45 | 76.55 | 35.44 | 0 | 0 | 0 | Normal
2025-01-19 20:00 | 19 | 1 | Summer | 20 | 24 | 4.8 | 12.25 | 46.2 | 214.3 | 12.86 | 93.76 | 106.62 | 0 | 45 | 95 | 50.15 | 0 | 0 | 0 | Normal
2025-01-19 21:00 | 19 | 1 | Summer | 21 | 24 | 5 | 1.86 | 13.9 | 224.8 | 13.49 | 0 | 13.49 | 0 | 45 | 82.4 | -31.51 | 0 | 0 | 0 | Battery-supported
2025-01-19 22:00 | 19 | 1 | Summer | 22 | 24 | 0.4 | 26.9 | 46.6 | 110.4 | 6.62 | 120 | 126.62 | 0 | 45 | 95 | 34.25 | 0 | 0 | 0 | Normal
2025-01-19 23:00 | 19 | 1 | Summer | 23 | 24 | 0.4 | 4.65 | 65.1 | 43.8 | 2.63 | 0.21 | 2.84 | 0 | 45 | 78.14 | -42.16 | 0 | 0 | 0 | Battery-supported
2025-01-20 | 20 | 1 | Summer | 0 | 24 | 2.1 | 10.11 | 30.7 | 0 | 0 | 40.42 | 40.42 | 0 | 45 | 76.3 | -4.58 | 0 | 0 | 0 | Battery-supported
2025-01-20 01:00 | 20 | 1 | Summer | 1 | 24 | -2.5 | 13.98 | 12 | 77.9 | 4.67 | 120 | 124.67 | 2.5 | 45 | 95 | 50.8 | 0 | 0 | 0 | Normal
2025-01-20 02:00 | 20 | 1 | Summer | 2 | 24 | -0.3 | 6.31 | 30.3 | 131.2 | 7.87 | 3.11 | 10.98 | 0.3 | 45 | 81.39 | -34.02 | 0 | 0 | 0 | Battery-supported
2025-01-20 03:00 | 20 | 1 | Summer | 3 | 24 | -1.5 | 12.53 | 67.8 | 123.3 | 7.4 | 103.06 | 110.46 | 1.5 | 45 | 95 | 36.98 | 0 | 0 | 0 | Normal
2025-01-20 04:00 | 20 | 1 | Summer | 4 | 24 | -1.1 | 1.85 | 89.6 | 107.7 | 6.46 | 0 | 6.46 | 1.1 | 45 | 79.58 | -38.54 | 0 | 0 | 0 | Battery-supported
2025-01-20 05:00 | 20 | 1 | Summer | 5 | 24 | -3.9 | 1.32 | 30.6 | 307.6 | 18.46 | 0 | 18.46 | 3.9 | 45 | 68.97 | -26.54 | 0 | 0 | 0 | Battery-supported
2025-01-20 06:00 | 20 | 1 | Summer | 6 | 24 | -5.8 | 12.79 | 57.8 | 262.8 | 15.77 | 112.22 | 127.99 | 5.8 | 45 | 95 | 70.74 | 0 | 0 | 0 | Normal
2025-01-20 07:00 | 20 | 1 | Summer | 7 | 24 | -7.1 | 11.9 | 71.9 | 239.9 | 14.39 | 82.96 | 97.35 | 7.1 | 45.95 | 95 | 0 | 0 | 0 | 0 | Normal
2025-01-20 08:00 | 20 | 1 | Summer | 8 | 24 | -5 | 8.44 | 70.2 | 268.8 | 16.13 | 16.87 | 33 | 5 | 45 | 90.2 | -12 | 0 | 0 | 0 | Battery-supported
2025-01-20 09:00 | 20 | 1 | Summer | 9 | 24 | -3.5 | 11.4 | 26.1 | 487.5 | 29.25 | 69.01 | 98.26 | 3.5 | 50.15 | 95 | 13.04 | 0 | 0 | 0 | Normal
2025-01-20 10:00 | 20 | 1 | Summer | 10 | 24 | -3 | 16.45 | 74 | 281.9 | 16.91 | 120 | 136.91 | 3 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-01-20 11:00 | 20 | 1 | Summer | 11 | 24 | 2.2 | 14.23 | 52.8 | 393 | 23.58 | 120 | 143.58 | 0 | 47.48 | 95 | 0 | 0 | 0 | 0 | Normal
2025-01-20 12:00 | 20 | 1 | Summer | 12 | 24 | 0.6 | 6.54 | 23.3 | 541.2 | 32.47 | 3.93 | 36.4 | 0 | 45 | 91.56 | -8.6 | 0 | 0 | 0 | Battery-supported
2025-01-20 13:00 | 20 | 1 | Summer | 13 | 24 | -3.5 | 7.8 | 53.2 | 390.6 | 23.44 | 11.13 | 34.57 | 3.5 | 48.16 | 86.12 | -13.59 | 0 | 0 | 0 | Battery-supported
2025-01-20 14:00 | 20 | 1 | Summer | 14 | 24 | -0.3 | 5.86 | 64.2 | 328.7 | 19.72 | 1.84 | 21.56 | 0.3 | 45 | 76.75 | -23.44 | 0 | 0 | 0 | Battery-supported
2025-01-20 15:00 | 20 | 1 | Summer | 15 | 24 | -1.6 | 5.4 | 45.5 | 399.2 | 23.95 | 0.96 | 24.91 | 1.6 | 48.66 | 67.25 | -23.75 | 0 | 0 | 0 | Battery-supported
2025-01-20 16:00 | 20 | 1 | Summer | 16 | 24 | -0.9 | 10.74 | 13.9 | 508.8 | 30.53 | 53.12 | 83.65 | 0.9 | 45 | 81.47 | 38.65 | 0 | 0 | 0 | Normal
2025-01-20 17:00 | 20 | 1 | Summer | 17 | 24 | 0.4 | 5.82 | 74.6 | 229.2 | 13.75 | 1.75 | 15.5 | 0 | 49.28 | 67.96 | -33.78 | 0 | 0 | 0 | Battery-supported
2025-01-20 18:00 | 20 | 1 | Summer | 18 | 24 | 1.6 | 10.72 | 34.4 | 344.1 | 20.65 | 52.68 | 73.33 | 0 | 45 | 78.38 | 28.33 | 0 | 0 | 0 | Normal
2025-01-20 19:00 | 20 | 1 | Summer | 19 | 24 | -0.3 | 6.3 | 40.8 | 277 | 16.62 | 3.07 | 19.69 | 0.3 | 45 | 68.26 | -25.31 | 0 | 0 | 0 | Battery-supported
2025-01-20 20:00 | 20 | 1 | Summer | 20 | 24 | 2.8 | 6.89 | 35.1 | 241.7 | 14.5 | 5.45 | 19.95 | 0 | 45 | 58.24 | -25.05 | 0 | 0 | 0 | Battery-supported
2025-01-20 21:00 | 20 | 1 | Summer | 21 | 24 | -2.1 | 3.85 | 72.5 | 114.6 | 6.88 | 0.01 | 6.89 | 2.1 | 45 | 43 | -38.11 | 0 | 0 | 0 | Battery-supported
2025-01-20 22:00 | 20 | 1 | Summer | 22 | 24 | 0.3 | 10.56 | 33 | 127.7 | 7.66 | 49.25 | 56.91 | 0 | 45 | 47.38 | 11.91 | 0 | 0 | 0 | Normal
2025-01-20 23:00 | 20 | 1 | Summer | 23 | 24 | 5.7 | 1.76 | 19.8 | 72.9 | 4.37 | 0 | 4.37 | 0 | 45 | 31.13 | -40.63 | 0 | 0 | 0 | Battery-supported
2025-01-21 | 21 | 1 | Summer | 0 | 24 | 0.2 | 13.08 | 81.6 | 0 | 0 | 120 | 120 | 0 | 45 | 58.73 | 75 | 0 | 0 | 0 | Normal
2025-01-21 01:00 | 21 | 1 | Summer | 1 | 24 | 2.5 | 21.5 | 20.6 | 72.4 | 4.34 | 120 | 124.34 | 0 | 45 | 87.92 | 79.34 | 0 | 0 | 0 | Normal
2025-01-21 02:00 | 21 | 1 | Summer | 2 | 24 | -0.9 | 7.04 | 26.4 | 136.1 | 8.17 | 6.21 | 14.38 | 0.9 | 45 | 75.68 | -30.62 | 0 | 0 | 0 | Battery-supported
2025-01-21 03:00 | 21 | 1 | Summer | 3 | 24 | -0.2 | 6.85 | 49.2 | 158.4 | 9.5 | 5.26 | 14.76 | 0.2 | 45 | 63.58 | -30.24 | 0 | 0 | 0 | Battery-supported
2025-01-21 04:00 | 21 | 1 | Summer | 4 | 24 | -1.9 | 2.25 | 40.6 | 228.2 | 13.69 | 0 | 13.69 | 1.9 | 45 | 51.06 | -31.31 | 0 | 0 | 0 | Battery-supported
2025-01-21 05:00 | 21 | 1 | Summer | 5 | 24 | -2.5 | 4.85 | 85.7 | 142.8 | 8.57 | 0.34 | 8.91 | 2.5 | 45 | 36.62 | -36.09 | 0 | 0 | 0 | Battery-supported
2025-01-21 06:00 | 21 | 1 | Summer | 6 | 24 | -4.1 | 11.47 | 54.2 | 275.3 | 16.52 | 70.86 | 87.38 | 4.1 | 45 | 52.22 | 42.38 | 0 | 0 | 0 | Normal
2025-01-21 07:00 | 21 | 1 | Summer | 7 | 24 | -1.6 | 12.42 | 76.4 | 222.1 | 13.33 | 99.34 | 112.67 | 1.6 | 45 | 77.12 | 67.67 | 0 | 0 | 0 | Normal
2025-01-21 08:00 | 21 | 1 | Summer | 8 | 24 | -4.4 | 7.59 | 69.9 | 270.4 | 16.22 | 9.58 | 25.8 | 4.4 | 45 | 69.44 | -19.2 | 0 | 0 | 0 | Battery-supported
2025-01-21 09:00 | 21 | 1 | Summer | 9 | 24 | -1 | 11.08 | 79.7 | 243.9 | 14.63 | 60.96 | 75.59 | 1 | 45 | 80.7 | 30.59 | 0 | 0 | 0 | Normal
2025-01-21 10:00 | 21 | 1 | Summer | 10 | 24 | 0 | 3.9 | 69.4 | 303.8 | 18.23 | 0.01 | 18.24 | 0 | 45 | 69.99 | -26.76 | 0 | 0 | 0 | Battery-supported
2025-01-21 11:00 | 21 | 1 | Summer | 11 | 24 | -1.3 | 8.67 | 22.1 | 542.6 | 32.56 | 19.34 | 51.9 | 1.3 | 45 | 72.53 | 6.9 | 0 | 0 | 0 | Normal
2025-01-21 12:00 | 21 | 1 | Summer | 12 | 24 | -2.4 | 15.01 | 4.8 | 632.1 | 37.93 | 120 | 157.93 | 2.4 | 51.16 | 95 | 61.06 | 0 | 0 | 0 | Normal
2025-01-21 13:00 | 21 | 1 | Summer | 13 | 24 | -0.5 | 9.67 | 67.6 | 320.7 | 19.24 | 32.88 | 52.12 | 0.5 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-01-21 14:00 | 21 | 1 | Summer | 14 | 24 | -1.7 | 16.31 | 20.6 | 535.6 | 32.14 | 120 | 152.14 | 1.7 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-01-21 15:00 | 21 | 1 | Summer | 15 | 24 | 1.4 | 16.6 | 71 | 283.2 | 16.99 | 120 | 136.99 | 0 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-01-21 16:00 | 21 | 1 | Summer | 16 | 24 | -4.3 | 9 | 72.7 | 258.2 | 15.49 | 23.29 | 38.78 | 4.3 | 45 | 92.51 | -6.22 | 0 | 0 | 0 | Battery-supported
2025-01-21 17:00 | 21 | 1 | Summer | 17 | 24 | -0.7 | 0.34 | 38 | 372 | 22.32 | 0 | 22.32 | 0.7 | 51.01 | 81.04 | -28.69 | 0 | 0 | 0 | Battery-supported
2025-01-21 18:00 | 21 | 1 | Summer | 18 | 24 | -4.1 | 12.27 | 72.8 | 210.5 | 12.63 | 94.41 | 107.04 | 4.1 | 45.59 | 95 | 37.95 | 0 | 0 | 0 | Normal
2025-01-21 19:00 | 21 | 1 | Summer | 19 | 24 | -2.9 | 2.83 | 29.8 | 310 | 18.6 | 0 | 18.6 | 2.9 | 53.32 | 81.11 | -34.72 | 0 | 0 | 0 | Battery-supported
2025-01-21 20:00 | 21 | 1 | Summer | 20 | 24 | 3.4 | 0.75 | 5.9 | 313.5 | 18.81 | 0 | 18.81 | 0 | 45 | 70.64 | -26.19 | 0 | 0 | 0 | Battery-supported
2025-01-21 21:00 | 21 | 1 | Summer | 21 | 24 | 2.4 | 1.56 | 36.2 | 182.9 | 10.97 | 0 | 10.97 | 0 | 45 | 57.02 | -34.03 | 0 | 0 | 0 | Battery-supported
2025-01-21 22:00 | 21 | 1 | Summer | 22 | 24 | -1.3 | 12.77 | 36 | 124 | 7.44 | 111.49 | 118.93 | 1.3 | 45 | 84.23 | 73.93 | 0 | 0 | 0 | Normal
2025-01-21 23:00 | 21 | 1 | Summer | 23 | 24 | -3.3 | 9.04 | 72.6 | 39 | 2.34 | 23.8 | 26.14 | 3.3 | 45 | 76.69 | -18.86 | 0 | 0 | 0 | Battery-supported
2025-01-22 | 22 | 1 | Summer | 0 | 24 | -6.9 | 7.72 | 48.5 | 0 | 0 | 10.52 | 10.52 | 6.9 | 45 | 62.89 | -34.48 | 0 | 0 | 0 | Battery-supported
2025-01-22 01:00 | 22 | 1 | Summer | 1 | 24 | -1.9 | 9.56 | 6.9 | 81.2 | 4.87 | 31.15 | 36.02 | 1.9 | 45 | 59.3 | -8.98 | 0 | 0 | 0 | Battery-supported
2025-01-22 02:00 | 22 | 1 | Summer | 2 | 24 | 4.2 | 1.64 | 20.9 | 143.2 | 8.59 | 0 | 8.59 | 0 | 45 | 44.74 | -36.41 | 0 | 0 | 0 | Battery-supported
2025-01-22 03:00 | 22 | 1 | Summer | 3 | 24 | -0.5 | 5.85 | 81.8 | 97 | 5.82 | 1.82 | 7.64 | 0.5 | 45 | 29.79 | -37.36 | 0 | 0 | 0 | Battery-supported
2025-01-22 04:00 | 22 | 1 | Summer | 4 | 24 | -3.1 | 4.36 | 29.7 | 255 | 15.3 | 0.09 | 15.39 | 3.1 | 45 | 17.95 | -29.61 | 0 | 0 | 0 | Battery-supported
2025-01-22 05:00 | 22 | 1 | Summer | 5 | 24 | -1.1 | 7.36 | 50.7 | 247.6 | 14.86 | 8.05 | 22.91 | 1.1 | 45 | 15 | -7.38 | 14.71 | 5.279 | 0 | Diesel-backup
2025-01-22 06:00 | 22 | 1 | Summer | 6 | 24 | -5.8 | 7.52 | 12.2 | 421.4 | 25.28 | 9.09 | 34.37 | 5.8 | 45 | 15 | 0 | 10.63 | 3.869 | 0 | Diesel-backup
2025-01-22 07:00 | 22 | 1 | Summer | 7 | 24 | -3.2 | 9.32 | 5.3 | 499.7 | 29.98 | 27.59 | 57.57 | 3.2 | 45 | 19.63 | 12.57 | 0 | 0 | 0 | Normal
2025-01-22 08:00 | 22 | 1 | Summer | 8 | 24 | -2.4 | 10.16 | 50.9 | 351.3 | 21.08 | 41.35 | 62.43 | 2.4 | 47.95 | 24.95 | 14.48 | 0 | 0 | 0 | Normal
2025-01-22 09:00 | 22 | 1 | Summer | 9 | 24 | -2.7 | 1.71 | 27.4 | 481.3 | 28.88 | 0 | 28.88 | 2.7 | 45 | 18.51 | -16.12 | 0 | 0 | 0 | Battery-supported
2025-01-22 10:00 | 22 | 1 | Summer | 10 | 24 | -0.6 | 5.9 | 49.5 | 398.6 | 23.92 | 1.93 | 25.85 | 0.6 | 45 | 15 | -8.77 | 10.38 | 3.783 | 0 | Diesel-backup
2025-01-22 11:00 | 22 | 1 | Summer | 11 | 24 | -1.4 | 6.76 | 43.3 | 439.1 | 26.35 | 4.85 | 31.2 | 1.4 | 46.19 | 15 | 0 | 14.99 | 5.373 | 0 | Diesel-backup
2025-01-22 12:00 | 22 | 1 | Summer | 12 | 24 | -0.4 | 2.77 | 17.9 | 567.7 | 34.06 | 0 | 34.06 | 0.4 | 46.04 | 15 | 0 | 11.98 | 4.34 | 0 | Diesel-backup
2025-01-22 13:00 | 22 | 1 | Summer | 13 | 24 | -3 | 2.56 | 53.7 | 388.4 | 23.3 | 0 | 23.3 | 3 | 45 | 15 | 0 | 21.7 | 7.591 | 0 | Diesel-backup
2025-01-22 14:00 | 22 | 1 | Summer | 14 | 24 | 0.9 | 1.57 | 87 | 220.2 | 13.21 | 0 | 13.21 | 0 | 49.69 | 15 | 0 | 36.48 | 12.071 | 0 | Diesel-backup
2025-01-22 15:00 | 22 | 1 | Summer | 15 | 24 | 2.9 | 2.29 | 47.8 | 388.8 | 23.33 | 0 | 23.33 | 0 | 45 | 15 | 0 | 21.67 | 7.582 | 0 | Diesel-backup
2025-01-22 16:00 | 22 | 1 | Summer | 16 | 24 | -2.5 | 11.05 | 47.4 | 366.2 | 21.97 | 60.24 | 82.21 | 2.5 | 45.39 | 28.55 | 36.82 | 0 | 0 | 0 | Normal
2025-01-22 17:00 | 22 | 1 | Summer | 17 | 24 | -2 | 1.96 | 14.5 | 463.8 | 27.83 | 0 | 27.83 | 2 | 45 | 21.68 | -17.17 | 0 | 0 | 0 | Battery-supported
2025-01-22 18:00 | 22 | 1 | Summer | 18 | 24 | 3.2 | 2.23 | 66.6 | 232.1 | 13.93 | 0 | 13.93 | 0 | 45 | 15 | -16.7 | 14.37 | 5.16 | 0 | Diesel-backup
2025-01-22 19:00 | 22 | 1 | Summer | 19 | 24 | -0.1 | 7.17 | 1.4 | 395.1 | 23.71 | 6.92 | 30.63 | 0.1 | 45 | 15 | 0 | 14.37 | 5.162 | 0 | Diesel-backup
2025-01-22 20:00 | 22 | 1 | Summer | 20 | 24 | 3.5 | 8.65 | 29.1 | 256.5 | 15.39 | 19.12 | 34.51 | 0 | 45 | 15 | 0 | 10.49 | 3.82 | 0 | Diesel-backup
2025-01-22 21:00 | 22 | 1 | Summer | 21 | 24 | -0.6 | 6.63 | 59.1 | 139.8 | 8.39 | 4.29 | 12.68 | 0.6 | 45 | 15 | 0 | 32.32 | 10.867 | 0 | Diesel-backup
2025-01-22 22:00 | 22 | 1 | Summer | 22 | 24 | 3.4 | 3.18 | 63.2 | 89.3 | 5.36 | 0 | 5.36 | 0 | 45 | 15 | 0 | 39.64 | 12.957 | 0 | Diesel-backup
2025-01-22 23:00 | 22 | 1 | Summer | 23 | 24 | 0.3 | 2.6 | 57.6 | 48.6 | 2.92 | 0 | 2.92 | 0 | 45 | 15 | 0 | 42.08 | 13.623 | 0 | Diesel-backup
2025-01-23 | 23 | 1 | Summer | 0 | 24 | 0.2 | 7.05 | 69.8 | 0 | 0 | 6.26 | 6.26 | 0 | 45 | 15 | 0 | 38.74 | 12.707 | 0 | Diesel-backup
2025-01-23 01:00 | 23 | 1 | Summer | 1 | 24 | 2.7 | 6.18 | 27.3 | 68.1 | 4.09 | 2.69 | 6.78 | 0 | 45 | 15 | 0 | 38.22 | 12.562 | 0 | Diesel-backup
2025-01-23 02:00 | 23 | 1 | Summer | 2 | 24 | -1.9 | 5.22 | 17.1 | 148 | 8.88 | 0.71 | 9.59 | 1.9 | 45 | 15 | 0 | 35.41 | 11.766 | 0 | Diesel-backup
2025-01-23 03:00 | 23 | 1 | Summer | 3 | 24 | -3.6 | 10.77 | 43.3 | 169.4 | 10.16 | 53.78 | 63.94 | 3.6 | 45 | 21.97 | 18.94 | 0 | 0 | 0 | Normal
2025-01-23 04:00 | 23 | 1 | Summer | 4 | 24 | -2.9 | 5.93 | 76.4 | 140 | 8.4 | 2.01 | 10.41 | 2.9 | 45 | 15 | -17.42 | 17.17 | 6.104 | 0 | Diesel-backup
2025-01-23 05:00 | 23 | 1 | Summer | 5 | 24 | -1.2 | 2.43 | 38 | 285.5 | 17.13 | 0 | 17.13 | 1.2 | 45 | 15 | 0 | 27.87 | 9.529 | 0 | Diesel-backup
2025-01-23 06:00 | 23 | 1 | Summer | 6 | 24 | -5.9 | 5.24 | 69.7 | 221.5 | 13.29 | 0.74 | 14.03 | 5.9 | 45 | 15 | 0 | 30.97 | 10.467 | 0 | Diesel-backup
2025-01-23 07:00 | 23 | 1 | Summer | 7 | 24 | -1.2 | 9.24 | 100 | 130.1 | 7.81 | 26.47 | 34.28 | 1.2 | 45 | 15 | 0 | 10.72 | 3.901 | 0 | Diesel-backup
2025-01-23 08:00 | 23 | 1 | Summer | 8 | 24 | -3.8 | 5.7 | 14.2 | 507.4 | 30.44 | 1.49 | 31.93 | 3.8 | 49.38 | 15 | 0 | 17.45 | 6.199 | 0 | Diesel-backup
2025-01-23 09:00 | 23 | 1 | Summer | 9 | 24 | 0 | 9.14 | 22.3 | 504.5 | 30.27 | 25.11 | 55.38 | 0 | 45 | 18.82 | 10.38 | 0 | 0 | 0 | Normal
2025-01-23 10:00 | 23 | 1 | Summer | 10 | 24 | -7.7 | 10.23 | 35.9 | 463.1 | 27.79 | 42.66 | 70.45 | 7.7 | 45 | 28.19 | 25.45 | 0 | 0 | 0 | Normal
2025-01-23 11:00 | 23 | 1 | Summer | 11 | 24 | -3.9 | 5.94 | 45 | 430.9 | 25.85 | 2.03 | 27.88 | 3.9 | 49.1 | 19.7 | -21.22 | 0 | 0 | 0 | Battery-supported
2025-01-23 12:00 | 23 | 1 | Summer | 12 | 24 | -5.6 | 6.62 | 42.5 | 447.1 | 26.83 | 4.25 | 31.08 | 5.6 | 49.88 | 15 | -11.74 | 7.06 | 2.601 | 0 | Diesel-backup
2025-01-23 13:00 | 23 | 1 | Summer | 13 | 24 | -3.3 | 5.47 | 18.5 | 560.3 | 33.62 | 1.07 | 34.69 | 3.3 | 45 | 15 | 0 | 10.31 | 3.757 | 0 | Diesel-backup
2025-01-23 14:00 | 23 | 1 | Summer | 14 | 24 | -0.6 | 9.27 | 2.2 | 622.9 | 37.37 | 26.89 | 64.26 | 0.6 | 45 | 22.09 | 19.26 | 0 | 0 | 0 | Normal
2025-01-23 15:00 | 23 | 1 | Summer | 15 | 24 | -1.1 | 5.36 | 38 | 433.3 | 26 | 0.9 | 26.9 | 1.1 | 45 | 15 | -17.72 | 0.38 | 0.144 | 0 | Diesel-backup
2025-01-23 16:00 | 23 | 1 | Summer | 16 | 24 | -0.9 | 8.73 | 52.1 | 346 | 20.76 | 20.02 | 40.78 | 0.9 | 45 | 15 | 0 | 4.22 | 1.571 | 0 | Diesel-backup
2025-01-23 17:00 | 23 | 1 | Summer | 17 | 24 | -0.4 | 7.6 | 71.1 | 243 | 14.58 | 9.65 | 24.23 | 0.4 | 45 | 15 | 0 | 20.77 | 7.291 | 0 | Diesel-backup
2025-01-23 18:00 | 23 | 1 | Summer | 18 | 24 | 0.6 | 1.55 | 39.3 | 327 | 19.62 | 0 | 19.62 | 0 | 45 | 15 | 0 | 25.38 | 8.759 | 0 | Diesel-backup
2025-01-23 19:00 | 23 | 1 | Summer | 19 | 24 | -1.9 | 9.02 | 86.5 | 140.2 | 8.41 | 23.54 | 31.95 | 1.9 | 45 | 15 | 0 | 13.05 | 4.71 | 0 | Diesel-backup
2025-01-23 20:00 | 23 | 1 | Summer | 20 | 24 | 1.9 | 7.18 | 73.4 | 147.3 | 8.84 | 6.98 | 15.82 | 0 | 45 | 15 | 0 | 29.18 | 9.928 | 0 | Diesel-backup
2025-01-23 21:00 | 23 | 1 | Summer | 21 | 24 | 1.8 | 13.39 | 59.2 | 139.5 | 8.37 | 120 | 128.37 | 0 | 45 | 45.68 | 83.37 | 0 | 0 | 0 | Normal
2025-01-23 22:00 | 23 | 1 | Summer | 22 | 24 | 1 | 2.87 | 87.1 | 58.9 | 3.53 | 0 | 3.53 | 0 | 45 | 29.09 | -41.47 | 0 | 0 | 0 | Battery-supported
2025-01-23 23:00 | 23 | 1 | Summer | 23 | 24 | 1.2 | 7.68 | 86.4 | 30.1 | 1.81 | 10.22 | 12.03 | 0 | 45 | 15.9 | -32.97 | 0 | 0 | 0 | Battery-supported
2025-01-24 | 24 | 1 | Summer | 0 | 24 | 0.3 | 4.88 | 18.8 | 0 | 0 | 0.37 | 0.37 | 0 | 45 | 15 | -2.26 | 42.37 | 13.701 | 0 | Diesel-backup
2025-01-24 01:00 | 24 | 1 | Summer | 1 | 24 | 3.7 | 1.7 | 69.1 | 41.3 | 2.48 | 0 | 2.48 | 0 | 45 | 15 | 0 | 42.52 | 13.741 | 0 | Diesel-backup
2025-01-24 02:00 | 24 | 1 | Summer | 2 | 24 | -1.3 | 1.3 | 72.2 | 77.8 | 4.67 | 0 | 4.67 | 1.3 | 45 | 15 | 0 | 40.33 | 13.147 | 0 | Diesel-backup
2025-01-24 03:00 | 24 | 1 | Summer | 3 | 24 | -2.2 | 14.96 | 71.3 | 116.9 | 7.01 | 120 | 127.01 | 2.2 | 45 | 45.18 | 82.01 | 0 | 0 | 0 | Normal
2025-01-24 04:00 | 24 | 1 | Summer | 4 | 24 | -3.6 | 7.7 | 43.7 | 220.5 | 13.23 | 10.37 | 23.6 | 3.6 | 45 | 36.62 | -21.4 | 0 | 0 | 0 | Battery-supported
2025-01-24 05:00 | 24 | 1 | Summer | 5 | 24 | -4.5 | 5.82 | 72.1 | 183.4 | 11 | 1.75 | 12.75 | 4.5 | 45 | 23.72 | -32.25 | 0 | 0 | 0 | Battery-supported
2025-01-24 06:00 | 24 | 1 | Summer | 6 | 24 | -5.2 | 2.11 | 54.7 | 273.6 | 16.42 | 0 | 16.42 | 5.2 | 45 | 15 | -21.8 | 6.78 | 2.502 | 0 | Diesel-backup
2025-01-24 07:00 | 24 | 1 | Summer | 7 | 24 | -4.5 | 14.45 | 61.1 | 282 | 16.92 | 120 | 136.92 | 4.5 | 45 | 48.83 | 91.92 | 0 | 0 | 0 | Normal
2025-01-24 08:00 | 24 | 1 | Summer | 8 | 24 | -2.8 | 4.07 | 54.9 | 334.3 | 20.06 | 0.03 | 20.09 | 2.8 | 53.89 | 35.31 | -33.8 | 0 | 0 | 0 | Battery-supported
2025-01-24 09:00 | 24 | 1 | Summer | 9 | 24 | -1.9 | 7.92 | 46.5 | 394.8 | 23.69 | 12.09 | 35.78 | 1.9 | 47.13 | 30.77 | -11.35 | 0 | 0 | 0 | Battery-supported
2025-01-24 10:00 | 24 | 1 | Summer | 10 | 24 | -2.3 | 7.01 | 45.1 | 419.3 | 25.16 | 6.05 | 31.21 | 2.3 | 45 | 25.25 | -13.79 | 0 | 0 | 0 | Battery-supported
2025-01-24 11:00 | 24 | 1 | Summer | 11 | 24 | -3.9 | 18.37 | 39.1 | 459.8 | 27.59 | 120 | 147.59 | 3.9 | 51.39 | 60.65 | 96.2 | 0 | 0 | 0 | Normal
2025-01-24 12:00 | 24 | 1 | Summer | 12 | 24 | 0.1 | 6.52 | 58.3 | 368.9 | 22.13 | 3.86 | 25.99 | 0 | 45 | 53.05 | -19.01 | 0 | 0 | 0 | Battery-supported
2025-01-24 13:00 | 24 | 1 | Summer | 13 | 24 | 0.1 | 4.68 | 55.4 | 380.2 | 22.81 | 0.23 | 23.04 | 0 | 45 | 44.26 | -21.96 | 0 | 0 | 0 | Battery-supported
2025-01-24 14:00 | 24 | 1 | Summer | 14 | 24 | -1.5 | 7.77 | 15.8 | 558.7 | 33.52 | 10.9 | 44.42 | 1.5 | 53.38 | 40.68 | -8.96 | 0 | 0 | 0 | Battery-supported
2025-01-24 15:00 | 24 | 1 | Summer | 15 | 24 | -2.2 | 8.28 | 60.7 | 330 | 19.8 | 15.29 | 35.09 | 2.2 | 45 | 36.72 | -9.91 | 0 | 0 | 0 | Battery-supported
2025-01-24 16:00 | 24 | 1 | Summer | 16 | 24 | 0.8 | 25.63 | 79.5 | 229.2 | 13.75 | 120 | 133.75 | 0 | 45 | 69.38 | 88.75 | 0 | 0 | 0 | Normal
2025-01-24 17:00 | 24 | 1 | Summer | 17 | 24 | 0.3 | 6.45 | 60.6 | 283.7 | 17.02 | 3.59 | 20.61 | 0 | 50.92 | 57.25 | -30.31 | 0 | 0 | 0 | Battery-supported
2025-01-24 18:00 | 24 | 1 | Summer | 18 | 24 | -3 | 2.8 | 26.2 | 372.7 | 22.36 | 0 | 22.36 | 3 | 49.83 | 46.26 | -27.47 | 0 | 0 | 0 | Battery-supported
2025-01-24 19:00 | 24 | 1 | Summer | 19 | 24 | 0.2 | 5.22 | 55.2 | 233.9 | 14.03 | 0.71 | 14.74 | 0 | 45.75 | 33.86 | -31.01 | 0 | 0 | 0 | Battery-supported
2025-01-24 20:00 | 24 | 1 | Summer | 20 | 24 | 0.9 | 7.76 | 82.8 | 124.2 | 7.45 | 10.82 | 18.27 | 0 | 45 | 23.17 | -26.73 | 0 | 0 | 0 | Battery-supported
2025-01-24 21:00 | 24 | 1 | Summer | 21 | 24 | -1.7 | 8.62 | 3.9 | 243.7 | 14.62 | 18.79 | 33.41 | 1.7 | 45 | 18.53 | -11.59 | 0 | 0 | 0 | Battery-supported
2025-01-24 22:00 | 24 | 1 | Summer | 22 | 24 | 0.6 | 1.96 | 28.8 | 133.1 | 7.99 | 0 | 7.99 | 0 | 45 | 15 | -8.83 | 28.18 | 9.624 | 0 | Diesel-backup
2025-01-24 23:00 | 24 | 1 | Summer | 23 | 24 | -3.3 | 4.82 | 42.9 | 58.1 | 3.49 | 0.32 | 3.81 | 3.3 | 45 | 15 | 0 | 41.19 | 13.382 | 0 | Diesel-backup
2025-01-25 | 25 | 1 | Summer | 0 | 24 | 2.5 | 17.77 | 15.8 | 0 | 0 | 120 | 120 | 0 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-01-25 01:00 | 25 | 1 | Summer | 1 | 24 | 2 | 3.53 | 66.3 | 43 | 2.58 | 0 | 2.58 | 0 | 45 | 25.63 | -42.42 | 0 | 0 | 0 | Battery-supported
2025-01-25 02:00 | 25 | 1 | Summer | 2 | 24 | -1.7 | 10.93 | 89.9 | 55.3 | 3.32 | 57.41 | 60.73 | 1.7 | 45 | 31.42 | 15.73 | 0 | 0 | 0 | Normal
2025-01-25 03:00 | 25 | 1 | Summer | 3 | 24 | -0.8 | 5.34 | 43.1 | 169.8 | 10.19 | 0.87 | 11.06 | 0.8 | 45 | 17.84 | -33.94 | 0 | 0 | 0 | Battery-supported
2025-01-25 04:00 | 25 | 1 | Summer | 4 | 24 | -7.2 | 6.69 | 18.2 | 283.1 | 16.99 | 4.54 | 21.53 | 7.2 | 45.14 | 15 | -7.11 | 16.5 | 5.881 | 0 | Diesel-backup
2025-01-25 05:00 | 25 | 1 | Summer | 5 | 24 | -4.8 | 2.16 | 40.8 | 277.2 | 16.63 | 0 | 16.63 | 4.8 | 45 | 15 | 0 | 28.37 | 9.682 | 0 | Diesel-backup
2025-01-25 06:00 | 25 | 1 | Summer | 6 | 24 | -3.1 | 5.68 | 69.6 | 221.9 | 13.31 | 1.45 | 14.76 | 3.1 | 45 | 15 | 0 | 30.24 | 10.248 | 0 | Diesel-backup
2025-01-25 07:00 | 25 | 1 | Summer | 7 | 24 | -5 | 7.7 | 48.6 | 330.8 | 19.85 | 10.37 | 30.22 | 5 | 45 | 15 | 0 | 14.78 | 5.301 | 0 | Diesel-backup
2025-01-25 08:00 | 25 | 1 | Summer | 8 | 24 | -1.1 | 6.51 | 63.9 | 295.8 | 17.75 | 3.82 | 21.57 | 1.1 | 45 | 15 | 0 | 23.43 | 8.144 | 0 | Diesel-backup
2025-01-25 09:00 | 25 | 1 | Summer | 9 | 24 | 1.8 | 5.91 | 49.3 | 381.8 | 22.91 | 1.96 | 24.87 | 0 | 45 | 15 | 0 | 20.13 | 7.082 | 0 | Diesel-backup
2025-01-25 10:00 | 25 | 1 | Summer | 10 | 24 | -5.1 | 9.31 | 57.7 | 359.6 | 21.58 | 27.45 | 49.03 | 5.1 | 45 | 16.48 | 4.03 | 0 | 0 | 0 | Normal
2025-01-25 11:00 | 25 | 1 | Summer | 11 | 24 | -4.1 | 2.6 | 73 | 294.1 | 17.65 | 0 | 17.65 | 4.1 | 47.62 | 15 | -3.71 | 26.26 | 9.034 | 0 | Diesel-backup
2025-01-25 12:00 | 25 | 1 | Summer | 12 | 24 | -1.4 | 7.92 | 75.4 | 285 | 17.1 | 12.09 | 29.19 | 1.4 | 47.4 | 15 | 0 | 18.21 | 6.452 | 0 | Diesel-backup
2025-01-25 13:00 | 25 | 1 | Summer | 13 | 24 | 2 | 1.21 | 69.7 | 310.1 | 18.61 | 0 | 18.61 | 0 | 45 | 15 | 0 | 26.39 | 9.073 | 0 | Diesel-backup
2025-01-25 14:00 | 25 | 1 | Summer | 14 | 24 | -3.9 | 12.72 | 95.7 | 178.9 | 10.73 | 109.7 | 120.43 | 3.9 | 45 | 42.76 | 75.43 | 0 | 0 | 0 | Normal
2025-01-25 15:00 | 25 | 1 | Summer | 15 | 24 | -0.2 | 6.04 | 38.8 | 429.7 | 25.78 | 2.29 | 28.07 | 0.2 | 45 | 35.99 | -16.93 | 0 | 0 | 0 | Battery-supported
2025-01-25 16:00 | 25 | 1 | Summer | 16 | 24 | 3.6 | 10.51 | 48.6 | 361.2 | 21.67 | 48.21 | 69.88 | 0 | 45 | 45.14 | 24.88 | 0 | 0 | 0 | Normal
2025-01-25 17:00 | 25 | 1 | Summer | 17 | 24 | -3.8 | 0.55 | 42.1 | 356.2 | 21.37 | 0 | 21.37 | 3.8 | 49.5 | 33.89 | -28.13 | 0 | 0 | 0 | Battery-supported
2025-01-25 18:00 | 25 | 1 | Summer | 18 | 24 | -2.7 | 9.65 | 53 | 279.6 | 16.78 | 32.56 | 49.34 | 2.7 | 45 | 35.49 | 4.34 | 0 | 0 | 0 | Normal
2025-01-25 19:00 | 25 | 1 | Summer | 19 | 24 | -0.7 | 3.97 | 72.8 | 181.3 | 10.88 | 0.01 | 10.89 | 0.7 | 45 | 21.84 | -34.11 | 0 | 0 | 0 | Battery-supported
2025-01-25 20:00 | 25 | 1 | Summer | 20 | 24 | -0.8 | 6.72 | 53.5 | 196.4 | 11.78 | 4.67 | 16.45 | 0.8 | 45 | 15 | -17.11 | 11.44 | 4.153 | 0 | Diesel-backup
2025-01-25 21:00 | 25 | 1 | Summer | 21 | 24 | 2.1 | 9.75 | 71.1 | 117.1 | 7.03 | 34.17 | 41.2 | 0 | 45 | 15 | 0 | 3.8 | 1.416 | 0 | Diesel-backup
2025-01-25 22:00 | 25 | 1 | Summer | 22 | 24 | 0.7 | 6.34 | 34.1 | 126.4 | 7.58 | 3.21 | 10.79 | 0 | 45 | 15 | 0 | 34.21 | 11.42 | 0 | Diesel-backup
2025-01-25 23:00 | 25 | 1 | Summer | 23 | 24 | -4 | 9.07 | 76.6 | 36.4 | 2.18 | 24.19 | 26.37 | 4 | 45 | 15 | 0 | 18.63 | 6.59 | 0 | Diesel-backup
2025-01-26 | 26 | 1 | Summer | 0 | 22.95 | 0.7 | 5.4 | 63.5 | 0 | 0 | 0.96 | 0.96 | 0 | 45 | 15 | 0 | 44.04 | 14.147 | 0 | Diesel-backup
2025-01-26 01:00 | 26 | 1 | Summer | 1 | 22.95 | -2.1 | 13.31 | 18 | 36.8 | 2.21 | 120 | 122.21 | 2.1 | 45 | 43.41 | 77.21 | 0 | 0 | 0 | Normal
2025-01-26 02:00 | 26 | 1 | Summer | 2 | 22.95 | 1.6 | 6.03 | 83.7 | 48.9 | 2.93 | 2.27 | 5.2 | 0 | 45 | 27.49 | -39.8 | 0 | 0 | 0 | Battery-supported
2025-01-26 03:00 | 26 | 1 | Summer | 3 | 22.95 | -3 | 6.11 | 30 | 168.9 | 10.13 | 2.49 | 12.62 | 3 | 45 | 15 | -31.23 | 1.15 | 0.431 | 0 | Diesel-backup
2025-01-26 04:00 | 26 | 1 | Summer | 4 | 22.95 | -3.4 | 6.18 | 28.1 | 237 | 14.22 | 2.69 | 16.91 | 3.4 | 45 | 15 | 0 | 28.09 | 9.597 | 0 | Diesel-backup
2025-01-26 05:00 | 26 | 1 | Summer | 5 | 22.95 | -1.1 | 6.61 | 69.4 | 180.9 | 10.85 | 4.21 | 15.06 | 1.1 | 45 | 15 | 0 | 29.94 | 10.158 | 0 | Diesel-backup
2025-01-26 06:00 | 26 | 1 | Summer | 6 | 22.95 | -0.8 | 2.7 | 43.2 | 302.2 | 18.13 | 0 | 18.13 | 0.8 | 45 | 15 | 0 | 26.87 | 9.222 | 0 | Diesel-backup
2025-01-26 07:00 | 26 | 1 | Summer | 7 | 22.95 | -1.7 | 3.46 | 53.7 | 303.4 | 18.2 | 0 | 18.2 | 1.7 | 45 | 15 | 0 | 26.8 | 9.2 | 0 | Diesel-backup
2025-01-26 08:00 | 26 | 1 | Summer | 8 | 22.95 | -6.4 | 11.43 | 26.5 | 448.9 | 26.93 | 69.8 | 96.73 | 6.4 | 49.99 | 32.2 | 46.74 | 0 | 0 | 0 | Normal
2025-01-26 09:00 | 26 | 1 | Summer | 9 | 22.95 | -1.5 | 10.52 | 18.8 | 516.7 | 31 | 48.42 | 79.42 | 1.5 | 45 | 44.87 | 34.42 | 0 | 0 | 0 | Normal
2025-01-26 10:00 | 26 | 1 | Summer | 10 | 22.95 | -4.8 | 10.13 | 42.4 | 430.6 | 25.84 | 40.79 | 66.63 | 4.8 | 47.21 | 52.01 | 19.42 | 0 | 0 | 0 | Normal
2025-01-26 11:00 | 26 | 1 | Summer | 11 | 22.95 | -1.8 | 8.6 | 33.4 | 486.8 | 29.21 | 18.57 | 47.78 | 1.8 | 45 | 53.04 | 2.78 | 0 | 0 | 0 | Normal
2025-01-26 12:00 | 26 | 1 | Summer | 12 | 22.95 | -5.1 | 4.76 | 35.3 | 482.4 | 28.94 | 0.28 | 29.22 | 5.1 | 49.64 | 44.87 | -20.42 | 0 | 0 | 0 | Battery-supported
2025-01-26 13:00 | 26 | 1 | Summer | 13 | 22.95 | -0.6 | 4.44 | 61.7 | 349 | 20.94 | 0.12 | 21.06 | 0.6 | 45 | 35.29 | -23.94 | 0 | 0 | 0 | Battery-supported
2025-01-26 14:00 | 26 | 1 | Summer | 14 | 22.95 | -3 | 6.44 | 83.8 | 234.6 | 14.08 | 3.56 | 17.64 | 3 | 50.33 | 22.22 | -32.69 | 0 | 0 | 0 | Battery-supported
2025-01-26 15:00 | 26 | 1 | Summer | 15 | 22.95 | -3.6 | 12.45 | 45.3 | 397 | 23.82 | 100.34 | 124.16 | 3.6 | 51.59 | 48.92 | 72.57 | 0 | 0 | 0 | Normal
2025-01-26 16:00 | 26 | 1 | Summer | 16 | 22.95 | 1.1 | 7.45 | 65.1 | 286.7 | 17.2 | 8.63 | 25.83 | 0 | 52.69 | 38.18 | -26.86 | 0 | 0 | 0 | Battery-supported
2025-01-26 17:00 | 26 | 1 | Summer | 17 | 22.95 | 0.4 | 3.34 | 85 | 184.1 | 11.05 | 0 | 11.05 | 0 | 45 | 24.6 | -33.95 | 0 | 0 | 0 | Battery-supported
2025-01-26 18:00 | 26 | 1 | Summer | 18 | 22.95 | -1.3 | 2.29 | 41.7 | 307.2 | 18.43 | 0 | 18.43 | 1.3 | 45 | 15 | -24 | 2.57 | 0.964 | 0 | Diesel-backup
2025-01-26 19:00 | 26 | 1 | Summer | 19 | 22.95 | 3.4 | 10.71 | 40.2 | 263.3 | 15.8 | 52.46 | 68.26 | 0 | 45 | 23.56 | 23.26 | 0 | 0 | 0 | Normal
2025-01-26 20:00 | 26 | 1 | Summer | 20 | 22.95 | -0.7 | 14.7 | 20 | 255.2 | 15.31 | 120 | 135.31 | 0.7 | 46.1 | 56.39 | 89.21 | 0 | 0 | 0 | Normal
2025-01-26 21:00 | 26 | 1 | Summer | 21 | 22.95 | 0.3 | 1.88 | 34.6 | 161.5 | 9.69 | 0 | 9.69 | 0 | 45 | 42.26 | -35.31 | 0 | 0 | 0 | Battery-supported
2025-01-26 22:00 | 26 | 1 | Summer | 22 | 22.95 | 0.7 | 10.91 | 71.3 | 61.2 | 3.67 | 56.95 | 60.62 | 0 | 45 | 48.01 | 15.62 | 0 | 0 | 0 | Normal
2025-01-26 23:00 | 26 | 1 | Summer | 23 | 22.95 | -1.5 | 8.48 | 31.9 | 32.4 | 1.94 | 17.29 | 19.23 | 1.5 | 45 | 37.71 | -25.77 | 0 | 0 | 0 | Battery-supported
2025-01-27 | 27 | 1 | Summer | 0 | 22.37 | 0.5 | 3.89 | 28.7 | 0 | 0 | 0.01 | 0.01 | 0 | 45 | 19.71 | -44.99 | 0 | 0 | 0 | Battery-supported
2025-01-27 01:00 | 27 | 1 | Summer | 1 | 22.37 | -2 | 7.51 | 55.7 | 9.9 | 0.59 | 9.02 | 9.61 | 2 | 45 | 15 | -11.77 | 23.62 | 8.204 | 0 | Diesel-backup
2025-01-27 02:00 | 27 | 1 | Summer | 2 | 22.37 | -2.2 | 2.97 | 67 | 54 | 3.24 | 0 | 3.24 | 2.2 | 45 | 15 | 0 | 41.76 | 13.536 | 0 | Diesel-backup
2025-01-27 03:00 | 27 | 1 | Summer | 3 | 22.37 | 1.4 | 5.75 | 73.9 | 88.3 | 5.3 | 1.59 | 6.89 | 0 | 45 | 15 | 0 | 38.11 | 12.531 | 0 | Diesel-backup
2025-01-27 04:00 | 27 | 1 | Summer | 4 | 22.37 | -4.3 | 6.67 | 42.9 | 192.4 | 11.54 | 4.46 | 16 | 4.3 | 45.14 | 15 | 0 | 29.14 | 9.916 | 0 | Diesel-backup
2025-01-27 05:00 | 27 | 1 | Summer | 5 | 22.37 | -7.6 | 13.25 | 72.7 | 165.4 | 9.92 | 120 | 129.92 | 7.6 | 45 | 46.25 | 84.92 | 0 | 0 | 0 | Normal
2025-01-27 06:00 | 27 | 1 | Summer | 6 | 22.37 | 1 | 5.58 | 53.9 | 260 | 15.6 | 1.26 | 16.86 | 0 | 45 | 34.99 | -28.14 | 0 | 0 | 0 | Battery-supported
2025-01-27 07:00 | 27 | 1 | Summer | 7 | 22.37 | 2.9 | 4.18 | 42.7 | 340.5 | 20.43 | 0.04 | 20.47 | 0 | 45 | 25.18 | -24.53 | 0 | 0 | 0 | Battery-supported
2025-01-27 08:00 | 27 | 1 | Summer | 8 | 22.37 | -3.6 | 8.11 | 64.5 | 286.4 | 17.18 | 13.71 | 30.89 | 3.6 | 45 | 19.54 | -14.11 | 0 | 0 | 0 | Battery-supported
2025-01-27 09:00 | 27 | 1 | Summer | 9 | 22.37 | -7 | 9.23 | 52.1 | 364.9 | 21.89 | 26.33 | 48.22 | 7 | 53.93 | 17.25 | -5.71 | 0 | 0 | 0 | Battery-supported
2025-01-27 10:00 | 27 | 1 | Summer | 10 | 22.37 | -3.2 | 4.08 | 43.5 | 424.7 | 25.48 | 0.03 | 25.51 | 3.2 | 47.77 | 15 | -5.64 | 16.62 | 5.923 | 0 | Diesel-backup
2025-01-27 11:00 | 27 | 1 | Summer | 11 | 22.37 | -2.9 | 3.25 | 61.3 | 350.8 | 21.05 | 0 | 21.05 | 2.9 | 45 | 15 | 0 | 23.95 | 8.309 | 0 | Diesel-backup
2025-01-27 12:00 | 27 | 1 | Summer | 12 | 22.37 | -2.4 | 3.45 | 34.7 | 485.3 | 29.12 | 0 | 29.12 | 2.4 | 45 | 15 | 0 | 15.88 | 5.674 | 0 | Diesel-backup
2025-01-27 13:00 | 27 | 1 | Summer | 13 | 22.37 | -4.1 | 13.27 | 81.5 | 252.4 | 15.14 | 120 | 135.14 | 4.1 | 45.16 | 48.11 | 89.98 | 0 | 0 | 0 | Normal
2025-01-27 14:00 | 27 | 1 | Summer | 14 | 22.37 | 0 | 9 | 37.3 | 453.8 | 27.23 | 23.29 | 50.52 | 0 | 45 | 50.14 | 5.52 | 0 | 0 | 0 | Normal
2025-01-27 15:00 | 27 | 1 | Summer | 15 | 22.37 | 0.3 | 5.35 | 49.5 | 376.3 | 22.58 | 0.89 | 23.47 | 0 | 45 | 41.53 | -21.53 | 0 | 0 | 0 | Battery-supported
2025-01-27 16:00 | 27 | 1 | Summer | 16 | 22.37 | -3.8 | 12.02 | 9.7 | 514.6 | 30.88 | 86.56 | 117.44 | 3.8 | 45 | 68.19 | 72.44 | 0 | 0 | 0 | Normal
2025-01-27 17:00 | 27 | 1 | Summer | 17 | 22.37 | 1.3 | 4.06 | 72 | 230.2 | 13.81 | 0.02 | 13.83 | 0 | 45 | 55.72 | -31.17 | 0 | 0 | 0 | Battery-supported
2025-01-27 18:00 | 27 | 1 | Summer | 18 | 22.37 | 4.6 | 6.29 | 3.7 | 424.3 | 25.46 | 3.04 | 28.5 | 0 | 45 | 49.12 | -16.5 | 0 | 0 | 0 | Battery-supported
2025-01-27 19:00 | 27 | 1 | Summer | 19 | 22.37 | 0.6 | 2.93 | 46.5 | 237 | 14.22 | 0 | 14.22 | 0 | 45.32 | 36.68 | -31.1 | 0 | 0 | 0 | Battery-supported
2025-01-27 20:00 | 27 | 1 | Summer | 20 | 22.37 | -0.5 | 11.73 | 36.1 | 206.9 | 12.41 | 78.02 | 90.43 | 0.5 | 45 | 53.4 | 45.43 | 0 | 0 | 0 | Normal
2025-01-27 21:00 | 27 | 1 | Summer | 21 | 22.37 | -0.1 | 3.84 | 82.6 | 75.4 | 4.52 | 0.01 | 4.53 | 0.1 | 45 | 37.21 | -40.47 | 0 | 0 | 0 | Battery-supported
2025-01-27 22:00 | 27 | 1 | Summer | 22 | 22.37 | 1.4 | 3.9 | 42.6 | 73.9 | 4.43 | 0.01 | 4.44 | 0 | 45 | 20.99 | -40.56 | 0 | 0 | 0 | Battery-supported
2025-01-27 23:00 | 27 | 1 | Summer | 23 | 22.37 | -4 | 8.22 | 48.9 | 10.8 | 0.65 | 14.72 | 15.37 | 4 | 45 | 15 | -14.97 | 14.66 | 5.26 | 0 | Diesel-backup
2025-01-28 | 28 | 1 | Summer | 0 | 21.94 | -0.2 | 1.11 | 58.8 | 0 | 0 | 0 | 0 | 0.2 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-01-28 01:00 | 28 | 1 | Summer | 1 | 21.94 | -1.8 | 2.48 | 61.3 | 0 | 0 | 0 | 0 | 1.8 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-01-28 02:00 | 28 | 1 | Summer | 2 | 21.94 | 2.8 | 9.96 | 26 | 73 | 4.38 | 37.73 | 42.11 | 0 | 45 | 15 | 0 | 2.89 | 1.081 | 0 | Diesel-backup
2025-01-28 03:00 | 28 | 1 | Summer | 3 | 21.94 | -2.1 | 3.41 | 53 | 109.9 | 6.59 | 0 | 6.59 | 2.1 | 45 | 15 | 0 | 38.41 | 12.615 | 0 | Diesel-backup
2025-01-28 04:00 | 28 | 1 | Summer | 4 | 21.94 | 1.6 | 21.81 | 29.4 | 211 | 12.66 | 120 | 132.66 | 0 | 45 | 47.26 | 87.66 | 0 | 0 | 0 | Normal
2025-01-28 05:00 | 28 | 1 | Summer | 5 | 21.94 | -4.8 | 7.29 | 15.5 | 312.1 | 18.73 | 7.62 | 26.35 | 4.8 | 45 | 39.8 | -18.65 | 0 | 0 | 0 | Battery-supported
2025-01-28 06:00 | 28 | 1 | Summer | 6 | 21.94 | -1.3 | 1.78 | 58.8 | 239.5 | 14.37 | 0 | 14.37 | 1.3 | 45 | 27.55 | -30.63 | 0 | 0 | 0 | Battery-supported
2025-01-28 07:00 | 28 | 1 | Summer | 7 | 21.94 | -2 | 0.78 | 67.7 | 243.7 | 14.62 | 0 | 14.62 | 2 | 45 | 15.39 | -30.38 | 0 | 0 | 0 | Battery-supported
2025-01-28 08:00 | 28 | 1 | Summer | 8 | 21.94 | -4.7 | 15.15 | 29.7 | 428.3 | 25.7 | 120 | 145.7 | 4.7 | 46.97 | 51.73 | 98.73 | 0 | 0 | 0 | Normal
2025-01-28 09:00 | 28 | 1 | Summer | 9 | 21.94 | -2.4 | 7.28 | 22.9 | 493.9 | 29.63 | 7.56 | 37.19 | 2.4 | 45 | 48.6 | -7.81 | 0 | 0 | 0 | Battery-supported
2025-01-28 10:00 | 28 | 1 | Summer | 10 | 21.94 | 0.1 | 5.85 | 43.5 | 424.1 | 25.45 | 1.82 | 27.27 | 0 | 47.91 | 40.35 | -20.64 | 0 | 0 | 0 | Battery-supported
2025-01-28 11:00 | 28 | 1 | Summer | 11 | 21.94 | -3.1 | 7.27 | 50.4 | 403.7 | 24.22 | 7.5 | 31.72 | 3.1 | 45 | 35.04 | -13.28 | 0 | 0 | 0 | Battery-supported
2025-01-28 12:00 | 28 | 1 | Summer | 12 | 21.94 | -5.8 | 1.77 | 73.2 | 296 | 17.76 | 0 | 17.76 | 5.8 | 52.46 | 21.16 | -34.7 | 0 | 0 | 0 | Battery-supported
2025-01-28 13:00 | 28 | 1 | Summer | 13 | 21.94 | -1.7 | 6.43 | 47.5 | 418 | 25.08 | 3.52 | 28.6 | 1.7 | 45 | 15 | -15.39 | 1.01 | 0.381 | 0 | Diesel-backup
2025-01-28 14:00 | 28 | 1 | Summer | 14 | 21.94 | -3.3 | 3.58 | 32.8 | 474.6 | 28.48 | 0 | 28.48 | 3.3 | 45 | 15 | 0 | 16.52 | 5.889 | 0 | Diesel-backup
2025-01-28 15:00 | 28 | 1 | Summer | 15 | 21.94 | -1.7 | 6.18 | 5.4 | 572.2 | 34.33 | 2.69 | 37.02 | 1.7 | 45.87 | 15 | 0 | 8.85 | 3.242 | 0 | Diesel-backup
2025-01-28 16:00 | 28 | 1 | Summer | 16 | 21.94 | -0.7 | 4.85 | 51.8 | 337.1 | 20.23 | 0.34 | 20.57 | 0.7 | 49.41 | 15 | 0 | 28.84 | 9.825 | 0 | Diesel-backup
2025-01-28 17:00 | 28 | 1 | Summer | 17 | 21.94 | -4 | 7.04 | 63.2 | 260.5 | 15.63 | 6.21 | 21.84 | 4 | 47.59 | 15 | 0 | 25.75 | 8.874 | 0 | Diesel-backup
2025-01-28 18:00 | 28 | 1 | Summer | 18 | 21.94 | -3.6 | 5.35 | 25.7 | 345.8 | 20.75 | 0.89 | 21.64 | 3.6 | 45 | 15 | 0 | 23.36 | 8.122 | 0 | Diesel-backup
2025-01-28 19:00 | 28 | 1 | Summer | 19 | 21.94 | 1.2 | 4.65 | 32.1 | 268 | 16.08 | 0.21 | 16.29 | 0 | 45.84 | 15 | 0 | 29.55 | 10.04 | 0 | Diesel-backup
2025-01-28 20:00 | 28 | 1 | Summer | 20 | 21.94 | -0.9 | 3.32 | 77.7 | 113 | 6.78 | 0 | 6.78 | 0.9 | 45 | 15 | 0 | 38.22 | 12.562 | 0 | Diesel-backup
2025-01-28 21:00 | 28 | 1 | Summer | 21 | 21.94 | -5.5 | 1.83 | 15.2 | 161.6 | 9.7 | 0 | 9.7 | 5.5 | 45 | 15 | 0 | 35.3 | 11.734 | 0 | Diesel-backup
2025-01-28 22:00 | 28 | 1 | Summer | 22 | 21.94 | 1.7 | 1.53 | 88.4 | 30.6 | 1.84 | 0 | 1.84 | 0 | 45 | 15 | 0 | 43.16 | 13.913 | 0 | Diesel-backup
2025-01-28 23:00 | 28 | 1 | Summer | 23 | 21.94 | 0.4 | 2.55 | 72.8 | 0 | 0 | 0 | 0 | 0 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-01-29 | 29 | 1 | Summer | 0 | 21.57 | -2.2 | 9.52 | 71.4 | 0 | 0 | 30.54 | 30.54 | 2.2 | 45 | 15 | 0 | 14.46 | 5.192 | 0 | Diesel-backup
2025-01-29 01:00 | 29 | 1 | Summer | 1 | 21.57 | -3.9 | 3.19 | 51.7 | 0 | 0 | 0 | 0 | 3.9 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-01-29 02:00 | 29 | 1 | Summer | 2 | 21.57 | 0.5 | 4.16 | 15.5 | 66.3 | 3.98 | 0.04 | 4.02 | 0 | 45 | 15 | 0 | 40.98 | 13.324 | 0 | Diesel-backup
2025-01-29 03:00 | 29 | 1 | Summer | 3 | 21.57 | -1 | 4.19 | 84.4 | 61.9 | 3.71 | 0.05 | 3.76 | 1 | 45 | 15 | 0 | 41.24 | 13.395 | 0 | Diesel-backup
2025-01-29 04:00 | 29 | 1 | Summer | 4 | 21.57 | 3.1 | 4.9 | 41.8 | 177.7 | 10.66 | 0.38 | 11.04 | 0 | 45 | 15 | 0 | 33.96 | 11.347 | 0 | Diesel-backup
2025-01-29 05:00 | 29 | 1 | Summer | 5 | 21.57 | -1.5 | 8.58 | 14.8 | 305.6 | 18.34 | 18.35 | 36.69 | 1.5 | 45 | 15 | 0 | 8.31 | 3.049 | 0 | Diesel-backup
2025-01-29 06:00 | 29 | 1 | Summer | 6 | 21.57 | -1.8 | 5.32 | 56 | 244.1 | 14.65 | 0.84 | 15.49 | 1.8 | 45 | 15 | 0 | 29.51 | 10.028 | 0 | Diesel-backup
2025-01-29 07:00 | 29 | 1 | Summer | 7 | 21.57 | -3.2 | 10.58 | 72.8 | 222.5 | 13.35 | 49.67 | 63.02 | 3.2 | 45 | 21.63 | 18.02 | 0 | 0 | 0 | Normal
2025-01-29 08:00 | 29 | 1 | Summer | 8 | 21.57 | -1 | 2.57 | 8 | 514.7 | 30.88 | 0 | 30.88 | 1 | 53.32 | 15 | -16.58 | 5.86 | 2.169 | 0 | Diesel-backup
2025-01-29 09:00 | 29 | 1 | Summer | 9 | 21.57 | -1.4 | 9.94 | 85.1 | 215 | 12.9 | 37.38 | 50.28 | 1.4 | 45 | 16.94 | 5.28 | 0 | 0 | 0 | Normal
2025-01-29 10:00 | 29 | 1 | Summer | 10 | 21.57 | 0.1 | 14.15 | 51.2 | 387 | 23.22 | 120 | 143.22 | 0 | 45 | 53.09 | 98.22 | 0 | 0 | 0 | Normal
2025-01-29 11:00 | 29 | 1 | Summer | 11 | 21.57 | -3.6 | 6.38 | 48.4 | 413.6 | 24.82 | 3.34 | 28.16 | 3.6 | 49.69 | 44.48 | -21.53 | 0 | 0 | 0 | Battery-supported
2025-01-29 12:00 | 29 | 1 | Summer | 12 | 21.57 | -3.1 | 3.02 | 27.6 | 520.1 | 31.21 | 0 | 31.21 | 3.1 | 45.96 | 38.58 | -14.75 | 0 | 0 | 0 | Battery-supported
2025-01-29 13:00 | 29 | 1 | Summer | 13 | 21.57 | -2.8 | 8.68 | 45.6 | 427.3 | 25.64 | 19.45 | 45.09 | 2.8 | 45 | 38.61 | 0.09 | 0 | 0 | 0 | Normal
2025-01-29 14:00 | 29 | 1 | Summer | 14 | 21.57 | 0.4 | 6.45 | 31.6 | 479.3 | 28.76 | 3.59 | 32.35 | 0 | 45 | 33.55 | -12.65 | 0 | 0 | 0 | Battery-supported
2025-01-29 15:00 | 29 | 1 | Summer | 15 | 21.57 | 2.3 | 7.79 | 40.2 | 415.2 | 24.91 | 11.05 | 35.96 | 0 | 45 | 29.93 | -9.04 | 0 | 0 | 0 | Battery-supported
2025-01-29 16:00 | 29 | 1 | Summer | 16 | 21.57 | -1.6 | 10.76 | 49.3 | 345.2 | 20.71 | 53.56 | 74.27 | 1.6 | 45 | 40.7 | 29.27 | 0 | 0 | 0 | Normal
2025-01-29 17:00 | 29 | 1 | Summer | 17 | 21.57 | -1.2 | 5.06 | 10.5 | 451.1 | 27.07 | 0.53 | 27.6 | 1.2 | 47.44 | 32.77 | -19.84 | 0 | 0 | 0 | Battery-supported
2025-01-29 18:00 | 29 | 1 | Summer | 18 | 21.57 | 0.6 | 4.55 | 28.9 | 329.7 | 19.78 | 0.16 | 19.94 | 0 | 45 | 22.74 | -25.06 | 0 | 0 | 0 | Battery-supported
2025-01-29 19:00 | 29 | 1 | Summer | 19 | 21.57 | -0.4 | 24.27 | 46.3 | 224.4 | 13.46 | 120 | 133.46 | 0.4 | 45.25 | 55.21 | 88.21 | 0 | 0 | 0 | Normal
2025-01-29 20:00 | 29 | 1 | Summer | 20 | 21.57 | 2.2 | 8.75 | 32 | 196.8 | 11.81 | 20.25 | 32.06 | 0 | 45 | 50.03 | -12.94 | 0 | 0 | 0 | Battery-supported
2025-01-29 21:00 | 29 | 1 | Summer | 21 | 21.57 | -4.9 | 11.85 | 83.8 | 62.7 | 3.76 | 81.48 | 85.24 | 4.9 | 45 | 64.84 | 40.24 | 0 | 0 | 0 | Normal
2025-01-29 22:00 | 29 | 1 | Summer | 22 | 21.57 | -1.9 | 10.4 | 48.1 | 48 | 2.88 | 45.98 | 48.86 | 1.9 | 45 | 66.26 | 3.86 | 0 | 0 | 0 | Normal
2025-01-29 23:00 | 29 | 1 | Summer | 23 | 21.57 | -2 | 11.93 | 21.9 | 0 | 0 | 83.85 | 83.85 | 2 | 45 | 80.56 | 38.85 | 0 | 0 | 0 | Normal
2025-01-30 | 30 | 1 | Summer | 0 | 21.25 | -5.8 | 7.96 | 90.1 | 0 | 0 | 12.42 | 12.42 | 5.8 | 45 | 67.52 | -32.58 | 0 | 0 | 0 | Battery-supported
2025-01-30 01:00 | 30 | 1 | Summer | 1 | 21.25 | -3.1 | 11.12 | 81.3 | 0 | 0 | 61.93 | 61.93 | 3.1 | 45 | 73.75 | 16.93 | 0 | 0 | 0 | Normal
2025-01-30 02:00 | 30 | 1 | Summer | 2 | 21.25 | -3.4 | 4.18 | 57.1 | 34.6 | 2.08 | 0.04 | 2.12 | 3.4 | 45 | 56.6 | -42.88 | 0 | 0 | 0 | Battery-supported
2025-01-30 03:00 | 30 | 1 | Summer | 3 | 21.25 | -2.2 | 1.8 | 36.6 | 113.2 | 6.79 | 0 | 6.79 | 2.2 | 45 | 41.32 | -38.21 | 0 | 0 | 0 | Battery-supported
2025-01-30 04:00 | 30 | 1 | Summer | 4 | 21.25 | 0.3 | 3.49 | 61.4 | 133.9 | 8.03 | 0 | 8.03 | 0 | 45 | 26.53 | -36.97 | 0 | 0 | 0 | Battery-supported
2025-01-30 05:00 | 30 | 1 | Summer | 5 | 21.25 | -3 | 5.88 | 42.3 | 228.6 | 13.72 | 1.89 | 15.61 | 3 | 45 | 15 | -28.82 | 0.57 | 0.213 | 0 | Diesel-backup
2025-01-30 06:00 | 30 | 1 | Summer | 6 | 21.25 | -5 | 5.41 | 49.3 | 261.2 | 15.67 | 0.98 | 16.65 | 5 | 45 | 15 | 0 | 28.35 | 9.676 | 0 | Diesel-backup
2025-01-30 07:00 | 30 | 1 | Summer | 7 | 21.25 | -3 | 6.48 | 30 | 375.5 | 22.53 | 3.7 | 26.23 | 3 | 45 | 15 | 0 | 18.77 | 6.637 | 0 | Diesel-backup
2025-01-30 08:00 | 30 | 1 | Summer | 8 | 21.25 | -0.6 | 4.02 | 84 | 201.5 | 12.09 | 0.02 | 12.11 | 0.6 | 46.6 | 15 | 0 | 34.49 | 11.501 | 0 | Diesel-backup
2025-01-30 09:00 | 30 | 1 | Summer | 9 | 21.25 | -5 | 1.25 | 8 | 556.8 | 33.41 | 0 | 33.41 | 5 | 45 | 15 | 0 | 11.59 | 4.204 | 0 | Diesel-backup
2025-01-30 10:00 | 30 | 1 | Summer | 10 | 21.25 | -4.7 | 4.97 | 4.2 | 607.5 | 36.45 | 0.44 | 36.89 | 4.7 | 51.24 | 15 | 0 | 14.35 | 5.155 | 0 | Diesel-backup
2025-01-30 11:00 | 30 | 1 | Summer | 11 | 21.25 | -1.2 | 2.34 | 36.8 | 469.8 | 28.19 | 0 | 28.19 | 1.2 | 45 | 15 | 0 | 16.81 | 5.986 | 0 | Diesel-backup
2025-01-30 12:00 | 30 | 1 | Summer | 12 | 21.25 | -2.6 | 6.31 | 42 | 449.1 | 26.95 | 3.11 | 30.06 | 2.6 | 45 | 15 | 0 | 14.94 | 5.356 | 0 | Diesel-backup
2025-01-30 13:00 | 30 | 1 | Summer | 13 | 21.25 | -0.4 | 8.19 | 56.9 | 372.1 | 22.33 | 14.44 | 36.77 | 0.4 | 45.99 | 15 | 0 | 9.22 | 3.373 | 0 | Diesel-backup
2025-01-30 14:00 | 30 | 1 | Summer | 14 | 21.25 | -1.4 | 4.91 | 37.9 | 449 | 26.94 | 0.39 | 27.33 | 1.4 | 47.61 | 15 | 0 | 20.28 | 7.131 | 0 | Diesel-backup
2025-01-30 15:00 | 30 | 1 | Summer | 15 | 21.25 | 0.5 | 2.89 | 34.6 | 438.9 | 26.33 | 0 | 26.33 | 0 | 45.33 | 15 | 0 | 19 | 6.712 | 0 | Diesel-backup
2025-01-30 16:00 | 30 | 1 | Summer | 16 | 21.25 | -2.9 | 6.69 | 39.9 | 381.8 | 22.91 | 4.54 | 27.45 | 2.9 | 45 | 15 | 0 | 17.55 | 6.233 | 0 | Diesel-backup
2025-01-30 17:00 | 30 | 1 | Summer | 17 | 21.25 | -0.4 | 25.06 | 35.1 | 357.1 | 21.43 | 120 | 141.43 | 0.4 | 45 | 50.49 | 96.43 | 0 | 0 | 0 | Normal
2025-01-30 18:00 | 30 | 1 | Summer | 18 | 21.25 | -0.6 | 8.75 | 20.1 | 351.8 | 21.11 | 20.25 | 41.36 | 0.6 | 45 | 49.03 | -3.64 | 0 | 0 | 0 | Battery-supported
2025-01-30 19:00 | 30 | 1 | Summer | 19 | 21.25 | -2.6 | 9.14 | 62.3 | 178.5 | 10.71 | 25.11 | 35.82 | 2.6 | 45 | 45.36 | -9.18 | 0 | 0 | 0 | Battery-supported
2025-01-30 20:00 | 30 | 1 | Summer | 20 | 21.25 | -3.3 | 4.58 | 81.9 | 95.8 | 5.75 | 0.18 | 5.93 | 3.3 | 47.42 | 28.76 | -41.49 | 0 | 0 | 0 | Battery-supported
2025-01-30 21:00 | 30 | 1 | Summer | 21 | 21.25 | 1.6 | 3.67 | 46.2 | 102 | 6.12 | 0 | 6.12 | 0 | 45 | 15 | -34.41 | 4.47 | 1.664 | 0 | Diesel-backup
2025-01-30 22:00 | 30 | 1 | Summer | 22 | 21.25 | -0.9 | 11.96 | 48.5 | 38.5 | 2.31 | 84.75 | 87.06 | 0.9 | 45 | 30.48 | 42.06 | 0 | 0 | 0 | Normal
2025-01-30 23:00 | 30 | 1 | Summer | 23 | 21.25 | -2.6 | 0.88 | 0.2 | 0 | 0 | 0 | 0 | 2.6 | 45 | 15 | -38.7 | 6.3 | 2.33 | 0 | Diesel-backup
2025-01-31 | 31 | 1 | Summer | 0 | 20.96 | -0.9 | 3.94 | 17 | 0 | 0 | 0.01 | 0.01 | 0.9 | 45 | 15 | 0 | 44.99 | 14.397 | 0 | Diesel-backup
2025-01-31 01:00 | 31 | 1 | Summer | 1 | 20.96 | 1.4 | 16.02 | 42.8 | 0 | 0 | 120 | 120 | 0 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-01-31 02:00 | 31 | 1 | Summer | 2 | 20.96 | -6.5 | 6.08 | 35.8 | 34.3 | 2.06 | 2.4 | 4.46 | 6.5 | 45 | 26.38 | -40.54 | 0 | 0 | 0 | Battery-supported
2025-01-31 03:00 | 31 | 1 | Summer | 3 | 20.96 | -5.1 | 1.99 | 84.3 | 53 | 3.18 | 0 | 3.18 | 5.1 | 45 | 15 | -28.46 | 13.36 | 4.816 | 0 | Diesel-backup
2025-01-31 04:00 | 31 | 1 | Summer | 4 | 20.96 | -4.2 | 8.34 | 80.8 | 93.8 | 5.63 | 15.87 | 21.5 | 4.2 | 45 | 15 | 0 | 23.5 | 8.167 | 0 | Diesel-backup
2025-01-31 05:00 | 31 | 1 | Summer | 5 | 20.96 | 0.7 | 4.94 | 9.9 | 302.5 | 18.15 | 0.42 | 18.57 | 0 | 45 | 15 | 0 | 26.43 | 9.086 | 0 | Diesel-backup
2025-01-31 06:00 | 31 | 1 | Summer | 6 | 20.96 | -2.1 | 1.64 | 43.9 | 273.6 | 16.42 | 0 | 16.42 | 2.1 | 45 | 15 | 0 | 28.58 | 9.746 | 0 | Diesel-backup
2025-01-31 07:00 | 31 | 1 | Summer | 7 | 20.96 | -1.2 | 7.42 | 27.4 | 381.4 | 22.88 | 8.43 | 31.31 | 1.2 | 45 | 15 | 0 | 13.69 | 4.929 | 0 | Diesel-backup
2025-01-31 08:00 | 31 | 1 | Summer | 8 | 20.96 | -5.5 | 6.76 | 7.2 | 512.3 | 30.74 | 4.85 | 35.59 | 5.5 | 49.04 | 15 | 0 | 13.45 | 4.847 | 0 | Diesel-backup
2025-01-31 09:00 | 31 | 1 | Summer | 9 | 20.96 | -5.4 | 6.53 | 52.4 | 358.5 | 21.51 | 3.89 | 25.4 | 5.4 | 59.24 | 15 | 0 | 33.84 | 11.312 | 0 | Diesel-backup
2025-01-31 10:00 | 31 | 1 | Summer | 10 | 20.96 | -1.8 | 8.69 | 42.5 | 427.1 | 25.63 | 19.57 | 45.2 | 1.8 | 45 | 15.07 | 0.2 | 0 | 0 | 0 | Normal
2025-01-31 11:00 | 31 | 1 | Summer | 11 | 20.96 | -2.4 | 2.76 | 67.8 | 318.7 | 19.12 | 0 | 19.12 | 2.4 | 51.36 | 15 | -0.18 | 32.06 | 10.789 | 0 | Diesel-backup
2025-01-31 12:00 | 31 | 1 | Summer | 12 | 20.96 | -1 | 7.88 | 97.4 | 177 | 10.62 | 11.76 | 22.38 | 1 | 46.21 | 15 | 0 | 23.83 | 8.271 | 0 | Diesel-backup
2025-01-31 13:00 | 31 | 1 | Summer | 13 | 20.96 | -2.3 | 7.07 | 62.2 | 345.8 | 20.75 | 6.37 | 27.12 | 2.3 | 54.48 | 15 | 0 | 27.36 | 9.373 | 0 | Diesel-backup
2025-01-31 14:00 | 31 | 1 | Summer | 14 | 20.96 | -0.8 | 11.83 | 48.8 | 397.5 | 23.85 | 80.9 | 104.75 | 0.8 | 45 | 36.99 | 59.75 | 0 | 0 | 0 | Normal
2025-01-31 15:00 | 31 | 1 | Summer | 15 | 20.96 | -0.7 | 3.9 | 28.7 | 463.7 | 27.82 | 0.01 | 27.83 | 0.7 | 49.85 | 28.18 | -22.02 | 0 | 0 | 0 | Battery-supported
2025-01-31 16:00 | 31 | 1 | Summer | 16 | 20.96 | 1 | 13.04 | 83.6 | 201.9 | 12.11 | 120 | 132.11 | 0 | 49.55 | 58.56 | 82.56 | 0 | 0 | 0 | Normal
2025-01-31 17:00 | 31 | 1 | Summer | 17 | 20.96 | 1.4 | 10.31 | 19.8 | 408.9 | 24.53 | 44.2 | 68.73 | 0 | 45 | 67.29 | 23.73 | 0 | 0 | 0 | Normal
2025-01-31 18:00 | 31 | 1 | Summer | 18 | 20.96 | -3.7 | 5.93 | 24.1 | 334.1 | 20.05 | 2.01 | 22.06 | 3.7 | 45 | 58.12 | -22.94 | 0 | 0 | 0 | Battery-supported
2025-01-31 19:00 | 31 | 1 | Summer | 19 | 20.96 | -4.9 | 6.52 | 87.2 | 113.1 | 6.79 | 3.86 | 10.65 | 4.9 | 56.39 | 39.82 | -45.74 | 0 | 0 | 0 | Battery-supported
2025-01-31 20:00 | 31 | 1 | Summer | 20 | 20.96 | 2.3 | 0.95 | 80 | 95.2 | 5.71 | 0 | 5.71 | 0 | 45 | 24.11 | -39.29 | 0 | 0 | 0 | Battery-supported
2025-01-31 21:00 | 31 | 1 | Summer | 21 | 20.96 | 2.6 | 6.41 | 67.8 | 70.8 | 4.25 | 3.45 | 7.7 | 0 | 45 | 15 | -22.77 | 14.53 | 5.217 | 0 | Diesel-backup
2025-01-31 22:00 | 31 | 1 | Summer | 22 | 20.96 | -2.4 | 9.9 | 54.7 | 27.7 | 1.66 | 36.69 | 38.35 | 2.4 | 45 | 15 | 0 | 6.65 | 2.454 | 0 | Diesel-backup
2025-01-31 23:00 | 31 | 1 | Summer | 23 | 20.96 | -4.5 | 5.37 | 58.9 | 0 | 0 | 0.92 | 0.92 | 4.5 | 45 | 15 | 0 | 44.08 | 14.158 | 0 | Diesel-backup
2025-02-01 | 32 | 2 | Summer | 0 | 20.68 | -0.5 | 11.83 | 27.4 | 0 | 0 | 80.9 | 80.9 | 0.5 | 45 | 28.21 | 35.9 | 0 | 0 | 0 | Normal
2025-02-01 01:00 | 32 | 2 | Summer | 1 | 20.68 | 0.9 | 8.44 | 42.2 | 0 | 0 | 16.87 | 16.87 | 0 | 45 | 16.96 | -28.13 | 0 | 0 | 0 | Battery-supported
2025-02-01 02:00 | 32 | 2 | Summer | 2 | 20.68 | 2.4 | 18.82 | 10.9 | 31.1 | 1.87 | 120 | 121.87 | 0 | 45 | 45.25 | 76.87 | 0 | 0 | 0 | Normal
2025-02-01 03:00 | 32 | 2 | Summer | 3 | 20.68 | -0.8 | 4.1 | 93.1 | 40 | 2.4 | 0.03 | 2.43 | 0.8 | 45 | 28.22 | -42.57 | 0 | 0 | 0 | Battery-supported
2025-02-01 04:00 | 32 | 2 | Summer | 4 | 20.68 | -3.1 | 9.36 | 66.8 | 113.9 | 6.83 | 28.16 | 34.99 | 3.1 | 45 | 24.22 | -10.01 | 0 | 0 | 0 | Battery-supported
2025-02-01 05:00 | 32 | 2 | Summer | 5 | 20.68 | -4.5 | 2.4 | 23.2 | 263.3 | 15.8 | 0 | 15.8 | 4.5 | 45 | 15 | -23.04 | 6.16 | 2.278 | 0 | Diesel-backup
2025-02-01 06:00 | 32 | 2 | Summer | 6 | 20.68 | -2.8 | 5.69 | 62.1 | 214.7 | 12.88 | 1.47 | 14.35 | 2.8 | 45 | 15 | 0 | 30.65 | 10.371 | 0 | Diesel-backup
2025-02-01 07:00 | 32 | 2 | Summer | 7 | 20.68 | -3.6 | 8.74 | 80.6 | 187.9 | 11.27 | 20.14 | 31.41 | 3.6 | 45 | 15 | 0 | 13.59 | 4.895 | 0 | Diesel-backup
2025-02-01 08:00 | 32 | 2 | Summer | 8 | 20.68 | -5.2 | 9.71 | 42.5 | 366.7 | 22 | 33.52 | 55.52 | 5.2 | 47.61 | 17.91 | 7.91 | 0 | 0 | 0 | Normal
2025-02-01 09:00 | 32 | 2 | Summer | 9 | 20.68 | 1.5 | 5.11 | 69.4 | 282.6 | 16.96 | 0.58 | 17.54 | 0 | 48.34 | 15 | -7.28 | 23.52 | 8.174 | 0 | Diesel-backup
2025-02-01 10:00 | 32 | 2 | Summer | 10 | 20.68 | 1.1 | 12.57 | 52.9 | 377.4 | 22.64 | 104.43 | 127.07 | 0 | 48.5 | 43.91 | 78.57 | 0 | 0 | 0 | Normal
2025-02-01 11:00 | 32 | 2 | Summer | 11 | 20.68 | -0.1 | 14.14 | 20.9 | 546.6 | 32.8 | 120 | 152.8 | 0.1 | 45 | 83.58 | 107.8 | 0 | 0 | 0 | Normal
2025-02-01 12:00 | 32 | 2 | Summer | 12 | 20.68 | -4.3 | 4.13 | 76 | 281.8 | 16.91 | 0.03 | 16.94 | 4.3 | 45.44 | 72.18 | -28.5 | 0 | 0 | 0 | Battery-supported
2025-02-01 13:00 | 32 | 2 | Summer | 13 | 20.68 | 0 | 5.8 | 41 | 449.1 | 26.95 | 1.7 | 28.65 | 0 | 45.32 | 65.52 | -16.67 | 0 | 0 | 0 | Battery-supported
2025-02-01 14:00 | 32 | 2 | Summer | 14 | 20.68 | -0.1 | 5.43 | 98.5 | 163.6 | 9.82 | 1.01 | 10.83 | 0.1 | 48.73 | 50.36 | -37.9 | 0 | 0 | 0 | Battery-supported
2025-02-01 15:00 | 32 | 2 | Summer | 15 | 20.68 | -0.1 | 4.59 | 47.3 | 380.2 | 22.81 | 0.18 | 22.99 | 0.1 | 45 | 41.55 | -22.01 | 0 | 0 | 0 | Battery-supported
2025-02-01 16:00 | 32 | 2 | Summer | 16 | 20.68 | 2 | 13.64 | 86.2 | 190.5 | 11.43 | 120 | 131.43 | 0 | 45 | 73.36 | 86.43 | 0 | 0 | 0 | Normal
2025-02-01 17:00 | 32 | 2 | Summer | 17 | 20.68 | 0.9 | 13.55 | 86.8 | 165.9 | 9.95 | 120 | 129.95 | 0 | 45 | 95 | 58.81 | 0 | 0 | 0 | Normal
2025-02-01 18:00 | 32 | 2 | Summer | 18 | 20.68 | 1.4 | 5.54 | 98 | 106.5 | 6.39 | 1.19 | 7.58 | 0 | 45 | 80.03 | -37.42 | 0 | 0 | 0 | Battery-supported
2025-02-01 19:00 | 32 | 2 | Summer | 19 | 20.68 | 1.3 | 9.34 | 71.7 | 147.4 | 8.84 | 27.88 | 36.72 | 0 | 45 | 76.72 | -8.28 | 0 | 0 | 0 | Battery-supported
2025-02-01 20:00 | 32 | 2 | Summer | 20 | 20.68 | 0.7 | 11.75 | 56 | 132.5 | 7.95 | 78.59 | 86.54 | 0 | 45 | 92.01 | 41.54 | 0 | 0 | 0 | Normal
2025-02-01 21:00 | 32 | 2 | Summer | 21 | 20.68 | -4 | 7.49 | 95.5 | 37.6 | 2.26 | 8.89 | 11.15 | 4 | 45 | 78.47 | -33.85 | 0 | 0 | 0 | Battery-supported
2025-02-01 22:00 | 32 | 2 | Summer | 22 | 20.68 | 0 | 5.28 | 0 | 33.9 | 2.03 | 0.79 | 2.82 | 0 | 45 | 61.59 | -42.18 | 0 | 0 | 0 | Battery-supported
2025-02-01 23:00 | 32 | 2 | Summer | 23 | 20.68 | -1.7 | 3.93 | 33.5 | 0 | 0 | 0.01 | 0.01 | 1.7 | 45 | 43.6 | -44.99 | 0 | 0 | 0 | Battery-supported
2025-02-02 | 33 | 2 | Summer | 0 | 20.42 | -3.6 | 9.88 | 43.6 | 0 | 0 | 36.35 | 36.35 | 3.6 | 45 | 40.14 | -8.65 | 0 | 0 | 0 | Battery-supported
2025-02-02 01:00 | 33 | 2 | Summer | 1 | 20.42 | 2.5 | 2.55 | 56.6 | 0 | 0 | 0 | 0 | 0 | 45 | 22.14 | -45 | 0 | 0 | 0 | Battery-supported
2025-02-02 02:00 | 33 | 2 | Summer | 2 | 20.42 | 2.2 | 5.38 | 35 | 15.7 | 0.94 | 0.93 | 1.87 | 0 | 45 | 15 | -17.85 | 25.28 | 8.729 | 0 | Diesel-backup
2025-02-02 03:00 | 33 | 2 | Summer | 3 | 20.42 | 1 | 4.79 | 62 | 64.9 | 3.89 | 0.3 | 4.19 | 0 | 45 | 15 | 0 | 40.81 | 13.278 | 0 | Diesel-backup
2025-02-02 04:00 | 33 | 2 | Summer | 4 | 20.42 | -1.8 | 2.43 | 5.8 | 209.3 | 12.56 | 0 | 12.56 | 1.8 | 45 | 15 | 0 | 32.44 | 10.902 | 0 | Diesel-backup
2025-02-02 05:00 | 33 | 2 | Summer | 5 | 20.42 | 0.3 | 6.11 | 0.4 | 310 | 18.6 | 2.49 | 21.09 | 0 | 45 | 15 | 0 | 23.91 | 8.297 | 0 | Diesel-backup
2025-02-02 06:00 | 33 | 2 | Summer | 6 | 20.42 | -2.8 | 5.73 | 77.8 | 164.7 | 9.88 | 1.55 | 11.43 | 2.8 | 45 | 15 | 0 | 33.57 | 11.234 | 0 | Diesel-backup
2025-02-02 07:00 | 33 | 2 | Summer | 7 | 20.42 | -2.6 | 3.39 | 60.8 | 256.5 | 15.39 | 0 | 15.39 | 2.6 | 45 | 15 | 0 | 29.61 | 10.058 | 0 | Diesel-backup
2025-02-02 08:00 | 33 | 2 | Summer | 8 | 20.42 | -5.5 | 13.36 | 26.7 | 428.2 | 25.69 | 120 | 145.69 | 5.5 | 45 | 52.05 | 100.69 | 0 | 0 | 0 | Normal
2025-02-02 09:00 | 33 | 2 | Summer | 9 | 20.42 | -2.1 | 9.92 | 79 | 239.4 | 14.36 | 37.04 | 51.4 | 2.1 | 49.4 | 52.79 | 2 | 0 | 0 | 0 | Normal
2025-02-02 10:00 | 33 | 2 | Summer | 10 | 20.42 | -2.7 | 6.61 | 87.9 | 213.1 | 12.79 | 4.21 | 17 | 2.7 | 46.48 | 41 | -29.48 | 0 | 0 | 0 | Battery-supported
2025-02-02 11:00 | 33 | 2 | Summer | 11 | 20.42 | -5.5 | 10.81 | 44.5 | 431.7 | 25.9 | 54.67 | 80.57 | 5.5 | 49.19 | 52.55 | 31.38 | 0 | 0 | 0 | Normal
2025-02-02 12:00 | 33 | 2 | Summer | 12 | 20.42 | -2.4 | 12.3 | 45.5 | 432.1 | 25.93 | 95.38 | 121.31 | 2.4 | 45 | 80.63 | 76.31 | 0 | 0 | 0 | Normal
2025-02-02 13:00 | 33 | 2 | Summer | 13 | 20.42 | -2.1 | 13.71 | 6.6 | 616.3 | 36.98 | 120 | 156.98 | 2.1 | 48.13 | 95 | 39.05 | 0 | 0 | 0 | Normal
2025-02-02 14:00 | 33 | 2 | Summer | 14 | 20.42 | 2.4 | 4.09 | 71 | 292.1 | 17.53 | 0.03 | 17.56 | 0 | 45 | 84.02 | -27.44 | 0 | 0 | 0 | Battery-supported
2025-02-02 15:00 | 33 | 2 | Summer | 15 | 20.42 | 0.8 | 10.8 | 53.9 | 349.7 | 20.98 | 54.45 | 75.43 | 0 | 46.11 | 94.81 | 29.32 | 0 | 0 | 0 | Normal
2025-02-02 16:00 | 33 | 2 | Summer | 16 | 20.42 | -0.8 | 5.75 | 75.9 | 230.8 | 13.85 | 1.59 | 15.44 | 0.8 | 45 | 82.99 | -29.56 | 0 | 0 | 0 | Battery-supported
2025-02-02 17:00 | 33 | 2 | Summer | 17 | 20.42 | 0 | 7.35 | 33.8 | 351.8 | 21.11 | 7.99 | 29.1 | 0 | 45 | 76.63 | -15.9 | 0 | 0 | 0 | Battery-supported
2025-02-02 18:00 | 33 | 2 | Summer | 18 | 20.42 | -0.2 | 4.23 | 37.9 | 283.2 | 16.99 | 0.05 | 17.04 | 0.2 | 45 | 65.45 | -27.96 | 0 | 0 | 0 | Battery-supported
2025-02-02 19:00 | 33 | 2 | Summer | 19 | 20.42 | -0.6 | 6.42 | 24.9 | 252.9 | 15.17 | 3.48 | 18.65 | 0.6 | 45.29 | 54.79 | -26.64 | 0 | 0 | 0 | Battery-supported
2025-02-02 20:00 | 33 | 2 | Summer | 20 | 20.42 | -2.5 | 10.89 | 64.4 | 113.2 | 6.79 | 56.49 | 63.28 | 2.5 | 45 | 61.52 | 18.28 | 0 | 0 | 0 | Normal
2025-02-02 21:00 | 33 | 2 | Summer | 21 | 20.42 | -0.5 | 15.7 | 39 | 85.9 | 5.15 | 120 | 125.15 | 0.5 | 45 | 91.01 | 80.15 | 0 | 0 | 0 | Normal
2025-02-02 22:00 | 33 | 2 | Summer | 22 | 20.42 | -1.9 | 6.03 | 33.7 | 15.9 | 0.95 | 2.27 | 3.22 | 1.9 | 45 | 74.3 | -41.78 | 0 | 0 | 0 | Battery-supported
2025-02-02 23:00 | 33 | 2 | Summer | 23 | 20.42 | -3.3 | 3.47 | 31.6 | 0 | 0 | 0 | 0 | 3.3 | 45 | 56.3 | -45 | 0 | 0 | 0 | Battery-supported
2025-02-03 | 34 | 2 | Summer | 0 | 20.17 | 0.2 | 17.06 | 86.6 | 0 | 0 | 120 | 120 | 0 | 45 | 83.9 | 75 | 0 | 0 | 0 | Normal
2025-02-03 01:00 | 34 | 2 | Summer | 1 | 20.17 | -0.4 | 3.98 | 48.1 | 0 | 0 | 0.02 | 0.02 | 0.4 | 45 | 65.91 | -44.98 | 0 | 0 | 0 | Battery-supported
2025-02-03 02:00 | 34 | 2 | Summer | 2 | 20.17 | -5.6 | 1.84 | 54.7 | 5.3 | 0.32 | 0 | 0.32 | 5.6 | 45 | 48.04 | -44.68 | 0 | 0 | 0 | Battery-supported
2025-02-03 03:00 | 34 | 2 | Summer | 3 | 20.17 | -2.3 | 4.46 | 35.8 | 80.9 | 4.85 | 0.12 | 4.97 | 2.3 | 45 | 32.02 | -40.03 | 0 | 0 | 0 | Battery-supported
2025-02-03 04:00 | 34 | 2 | Summer | 4 | 20.17 | -0.2 | 1.04 | 26.8 | 167.3 | 10.04 | 0 | 10.04 | 0.2 | 45 | 18.04 | -34.96 | 0 | 0 | 0 | Battery-supported
2025-02-03 05:00 | 34 | 2 | Summer | 5 | 20.17 | -0.4 | 11.97 | 26.4 | 243.3 | 14.6 | 85.05 | 99.65 | 0.4 | 45 | 38.15 | 54.65 | 0 | 0 | 0 | Normal
2025-02-03 06:00 | 34 | 2 | Summer | 6 | 20.17 | -0.7 | 1.56 | 65.7 | 197.8 | 11.87 | 0 | 11.87 | 0.7 | 45 | 24.9 | -33.13 | 0 | 0 | 0 | Battery-supported
2025-02-03 07:00 | 34 | 2 | Summer | 7 | 20.17 | -3 | 3.81 | 78.1 | 193.3 | 11.6 | 0 | 11.6 | 3 | 45 | 15 | -24.75 | 8.65 | 3.171 | 0 | Diesel-backup
2025-02-03 08:00 | 34 | 2 | Summer | 8 | 20.17 | -5 | 2.86 | 34.6 | 394.3 | 23.66 | 0 | 23.66 | 5 | 50.24 | 15 | 0 | 26.58 | 9.132 | 0 | Diesel-backup
2025-02-03 09:00 | 34 | 2 | Summer | 9 | 20.17 | -5.5 | 6.94 | 55 | 344.2 | 20.65 | 5.7 | 26.35 | 5.5 | 50.75 | 15 | 0 | 24.4 | 8.451 | 0 | Diesel-backup
2025-02-03 10:00 | 34 | 2 | Summer | 10 | 20.17 | -2.2 | 15.73 | 30.3 | 482.6 | 28.96 | 120 | 148.96 | 2.2 | 45.72 | 52.99 | 103.24 | 0 | 0 | 0 | Normal
2025-02-03 11:00 | 34 | 2 | Summer | 11 | 20.17 | -1.9 | 8.56 | 68.1 | 317 | 19.02 | 18.13 | 37.15 | 1.9 | 45.23 | 49.76 | -8.08 | 0 | 0 | 0 | Battery-supported
2025-02-03 12:00 | 34 | 2 | Summer | 12 | 20.17 | 0.4 | 2.53 | 2.3 | 644.5 | 38.67 | 0 | 38.67 | 0 | 45 | 47.23 | -6.33 | 0 | 0 | 0 | Battery-supported
2025-02-03 13:00 | 34 | 2 | Summer | 13 | 20.17 | 0.4 | 20.46 | 78.2 | 267.9 | 16.07 | 120 | 136.07 | 0 | 45 | 80.74 | 91.07 | 0 | 0 | 0 | Normal
2025-02-03 14:00 | 34 | 2 | Summer | 14 | 20.17 | -1.9 | 7.96 | 47 | 404.5 | 24.27 | 12.42 | 36.69 | 1.9 | 45.42 | 77.25 | -8.73 | 0 | 0 | 0 | Battery-supported
2025-02-03 15:00 | 34 | 2 | Summer | 15 | 20.17 | -4 | 11.28 | 78.5 | 241 | 14.46 | 65.91 | 80.37 | 4 | 45 | 90.27 | 35.37 | 0 | 0 | 0 | Normal
2025-02-03 16:00 | 34 | 2 | Summer | 16 | 20.17 | -1.6 | 2.13 | 75.9 | 229.4 | 13.76 | 0 | 13.76 | 1.6 | 45 | 77.77 | -31.24 | 0 | 0 | 0 | Battery-supported
2025-02-03 17:00 | 34 | 2 | Summer | 17 | 20.17 | -0.1 | 18.51 | 63.9 | 243.2 | 14.59 | 120 | 134.59 | 0.1 | 51.45 | 95 | 46.82 | 0 | 0 | 0 | Normal
2025-02-03 18:00 | 34 | 2 | Summer | 18 | 20.17 | -0.8 | 5.06 | 64.1 | 202.5 | 12.15 | 0.53 | 12.68 | 0.8 | 45 | 82.07 | -32.32 | 0 | 0 | 0 | Battery-supported
2025-02-03 19:00 | 34 | 2 | Summer | 19 | 20.17 | -1.5 | 1.99 | 39.9 | 212.7 | 12.76 | 0 | 12.76 | 1.5 | 45 | 69.18 | -32.24 | 0 | 0 | 0 | Battery-supported
2025-02-03 20:00 | 34 | 2 | Summer | 20 | 20.17 | 0.4 | 7.45 | 78.6 | 86 | 5.16 | 8.63 | 13.79 | 0 | 47.45 | 55.71 | -33.66 | 0 | 0 | 0 | Battery-supported
2025-02-03 21:00 | 34 | 2 | Summer | 21 | 20.17 | -1.3 | 11.28 | 39.3 | 77.9 | 4.67 | 65.91 | 70.58 | 1.3 | 45 | 65.13 | 25.58 | 0 | 0 | 0 | Normal
2025-02-03 22:00 | 34 | 2 | Summer | 22 | 20.17 | -1.7 | 9.33 | 34.8 | 6.6 | 0.4 | 27.73 | 28.13 | 1.7 | 45 | 58.38 | -16.87 | 0 | 0 | 0 | Battery-supported
2025-02-03 23:00 | 34 | 2 | Summer | 23 | 20.17 | 0.1 | 9.24 | 43.7 | 0 | 0 | 26.47 | 26.47 | 0 | 45 | 50.97 | -18.53 | 0 | 0 | 0 | Battery-supported
2025-02-04 | 35 | 2 | Summer | 0 | 19.94 | -1.8 | 8.86 | 67.4 | 0 | 0 | 21.55 | 21.55 | 1.8 | 45 | 41.59 | -23.45 | 0 | 0 | 0 | Battery-supported
2025-02-04 01:00 | 35 | 2 | Summer | 1 | 19.94 | -0.8 | 7.06 | 33.6 | 0 | 0 | 6.31 | 6.31 | 0.8 | 45 | 26.11 | -38.69 | 0 | 0 | 0 | Battery-supported
2025-02-04 02:00 | 35 | 2 | Summer | 2 | 19.94 | -1.1 | 2.12 | 48.8 | 0 | 0 | 0 | 0 | 1.1 | 45 | 15 | -27.77 | 17.23 | 6.125 | 0 | Diesel-backup
2025-02-04 03:00 | 35 | 2 | Summer | 3 | 19.94 | -4.6 | 5.71 | 60.3 | 54.6 | 3.28 | 1.51 | 4.79 | 4.6 | 45 | 15 | 0 | 40.21 | 13.114 | 0 | Diesel-backup
2025-02-04 04:00 | 35 | 2 | Summer | 4 | 19.94 | -3.5 | 5.22 | 89 | 66.6 | 4 | 0.71 | 4.71 | 3.5 | 45 | 15 | 0 | 40.29 | 13.136 | 0 | Diesel-backup
2025-02-04 05:00 | 35 | 2 | Summer | 5 | 19.94 | 0.4 | 13.78 | 93.6 | 88.2 | 5.29 | 120 | 125.29 | 0 | 45 | 44.55 | 80.29 | 0 | 0 | 0 | Normal
2025-02-04 06:00 | 35 | 2 | Summer | 6 | 19.94 | -5.6 | 12 | 39.8 | 269.4 | 16.16 | 85.95 | 102.11 | 5.6 | 45 | 65.56 | 57.11 | 0 | 0 | 0 | Normal
2025-02-04 07:00 | 35 | 2 | Summer | 7 | 19.94 | -7.8 | 4.78 | 41 | 320.3 | 19.22 | 0.29 | 19.51 | 7.8 | 45 | 55.37 | -25.49 | 0 | 0 | 0 | Battery-supported
2025-02-04 08:00 | 35 | 2 | Summer | 8 | 19.94 | -7.3 | 10.27 | 100 | 132.5 | 7.95 | 43.43 | 51.38 | 7.3 | 53.1 | 54.68 | -1.72 | 0 | 0 | 0 | Battery-supported
2025-02-04 09:00 | 35 | 2 | Summer | 9 | 19.94 | -3.1 | 6.24 | 56.7 | 335.7 | 20.14 | 2.88 | 23.02 | 3.1 | 48.48 | 44.5 | -25.46 | 0 | 0 | 0 | Battery-supported
2025-02-04 10:00 | 35 | 2 | Summer | 10 | 19.94 | -2.9 | 1.85 | 44.5 | 415.3 | 24.92 | 0 | 24.92 | 2.9 | 49.39 | 34.71 | -24.47 | 0 | 0 | 0 | Battery-supported
2025-02-04 11:00 | 35 | 2 | Summer | 11 | 19.94 | -3 | 0.97 | 40.1 | 452.9 | 27.17 | 0 | 27.17 | 3 | 49.08 | 25.94 | -21.91 | 0 | 0 | 0 | Battery-supported
2025-02-04 12:00 | 35 | 2 | Summer | 12 | 19.94 | 0.2 | 9.56 | 39.9 | 459.9 | 27.59 | 31.15 | 58.74 | 0 | 45.98 | 30.64 | 12.76 | 0 | 0 | 0 | Normal
2025-02-04 13:00 | 35 | 2 | Summer | 13 | 19.94 | -8 | 3.13 | 8.4 | 607.1 | 36.43 | 0 | 36.43 | 8 | 49.18 | 25.54 | -12.75 | 0 | 0 | 0 | Battery-supported
2025-02-04 14:00 | 35 | 2 | Summer | 14 | 19.94 | -0.8 | 3.12 | 55.2 | 365.5 | 21.93 | 0 | 21.93 | 0.8 | 45 | 16.31 | -23.07 | 0 | 0 | 0 | Battery-supported
2025-02-04 15:00 | 35 | 2 | Summer | 15 | 19.94 | 2.1 | 4.07 | 55.4 | 341.3 | 20.48 | 0.03 | 20.51 | 0 | 45 | 15 | -3.28 | 21.21 | 7.434 | 0 | Diesel-backup
2025-02-04 16:00 | 35 | 2 | Summer | 16 | 19.94 | -3.4 | 9.69 | 59.4 | 293.8 | 17.63 | 33.2 | 50.83 | 3.4 | 47.2 | 16.34 | 3.63 | 0 | 0 | 0 | Normal
2025-02-04 17:00 | 35 | 2 | Summer | 17 | 19.94 | -1.5 | 12.09 | 75 | 202.6 | 12.16 | 88.71 | 100.87 | 1.5 | 45 | 36.9 | 55.87 | 0 | 0 | 0 | Normal
2025-02-04 18:00 | 35 | 2 | Summer | 18 | 19.94 | -2.1 | 11.95 | 55.7 | 223.5 | 13.41 | 84.45 | 97.86 | 2.1 | 46.98 | 55.62 | 50.88 | 0 | 0 | 0 | Normal
2025-02-04 19:00 | 35 | 2 | Summer | 19 | 19.94 | -2.2 | 1.68 | 30.8 | 227.4 | 13.64 | 0 | 13.64 | 2.2 | 50 | 41.08 | -36.36 | 0 | 0 | 0 | Battery-supported
2025-02-04 20:00 | 35 | 2 | Summer | 20 | 19.94 | -0.9 | 3.95 | 25.5 | 161.9 | 9.71 | 0.01 | 9.72 | 0.9 | 45 | 26.96 | -35.28 | 0 | 0 | 0 | Battery-supported
2025-02-04 21:00 | 35 | 2 | Summer | 21 | 19.94 | 2.9 | 3.52 | 75 | 43.7 | 2.62 | 0 | 2.62 | 0 | 45 | 15 | -29.91 | 12.47 | 4.51 | 0 | Diesel-backup
2025-02-04 22:00 | 35 | 2 | Summer | 22 | 19.94 | 3.6 | 9.68 | 14.7 | 0 | 0 | 33.04 | 33.04 | 0 | 45 | 15 | 0 | 11.96 | 4.333 | 0 | Diesel-backup
2025-02-04 23:00 | 35 | 2 | Summer | 23 | 19.94 | -1.4 | 3.99 | 26.4 | 0 | 0 | 0.02 | 0.02 | 1.4 | 45 | 15 | 0 | 44.98 | 14.395 | 0 | Diesel-backup
2025-02-05 | 36 | 2 | Summer | 0 | 19.71 | 3.2 | 5.97 | 85.7 | 0 | 0 | 2.11 | 2.11 | 0 | 45 | 15 | 0 | 42.89 | 13.841 | 0 | Diesel-backup
2025-02-05 01:00 | 36 | 2 | Summer | 1 | 19.71 | -1.3 | 10.21 | 46 | 0 | 0 | 42.28 | 42.28 | 1.3 | 45 | 15 | 0 | 2.72 | 1.018 | 0 | Diesel-backup
2025-02-05 02:00 | 36 | 2 | Summer | 2 | 19.71 | 2.1 | 6.7 | 47 | 0 | 0 | 4.59 | 4.59 | 0 | 45 | 15 | 0 | 40.41 | 13.169 | 0 | Diesel-backup
2025-02-05 03:00 | 36 | 2 | Summer | 3 | 19.71 | -2.4 | 7.97 | 37.9 | 63.8 | 3.83 | 12.5 | 16.33 | 2.4 | 45 | 15 | 0 | 28.67 | 9.774 | 0 | Diesel-backup
2025-02-05 04:00 | 36 | 2 | Summer | 4 | 19.71 | -2.2 | 5.83 | 75.6 | 82.8 | 4.97 | 1.77 | 6.74 | 2.2 | 45 | 15 | 0 | 38.26 | 12.573 | 0 | Diesel-backup
2025-02-05 05:00 | 36 | 2 | Summer | 5 | 19.71 | -2 | 11.39 | 87.9 | 98.2 | 5.89 | 68.75 | 74.64 | 2 | 45 | 25.91 | 29.64 | 0 | 0 | 0 | Normal
2025-02-05 06:00 | 36 | 2 | Summer | 6 | 19.71 | 3.9 | 12.06 | 73.9 | 168.7 | 10.12 | 87.79 | 97.91 | 0 | 45 | 45.38 | 52.91 | 0 | 0 | 0 | Normal
2025-02-05 07:00 | 36 | 2 | Summer | 7 | 19.71 | -1.4 | 8.87 | 60.8 | 249.5 | 14.97 | 21.67 | 36.64 | 1.4 | 45 | 42.03 | -8.36 | 0 | 0 | 0 | Battery-supported
2025-02-05 08:00 | 36 | 2 | Summer | 8 | 19.71 | -4.8 | 12.08 | 71 | 246.2 | 14.77 | 88.4 | 103.17 | 4.8 | 50.04 | 61.59 | 53.13 | 0 | 0 | 0 | Normal
2025-02-05 09:00 | 36 | 2 | Summer | 9 | 19.71 | -1.1 | 24.36 | 28.2 | 459.3 | 27.56 | 120 | 147.56 | 1.1 | 45 | 95 | 90.8 | 0 | 0 | 0 | Normal
2025-02-05 10:00 | 36 | 2 | Summer | 10 | 19.71 | -3.9 | 10.11 | 29 | 487.3 | 29.24 | 40.42 | 69.66 | 3.9 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-02-05 11:00 | 36 | 2 | Summer | 11 | 19.71 | -3.9 | 6.38 | 59.3 | 359.4 | 21.56 | 3.34 | 24.9 | 3.9 | 45.53 | 86.75 | -20.63 | 0 | 0 | 0 | Battery-supported
2025-02-05 12:00 | 36 | 2 | Summer | 12 | 19.71 | -0.5 | 8.08 | 64.5 | 338.8 | 20.33 | 13.45 | 33.78 | 0.5 | 45 | 82.26 | -11.22 | 0 | 0 | 0 | Battery-supported
2025-02-05 13:00 | 36 | 2 | Summer | 13 | 19.71 | -2.1 | 12.79 | 31.9 | 492.5 | 29.55 | 112.22 | 141.77 | 2.1 | 45.47 | 95 | 34.62 | 0 | 0 | 0 | Normal
2025-02-05 14:00 | 36 | 2 | Summer | 14 | 19.71 | -1.2 | 5.04 | 31.4 | 476 | 28.56 | 0.51 | 29.07 | 1.2 | 45 | 88.63 | -15.93 | 0 | 0 | 0 | Battery-supported
2025-02-05 15:00 | 36 | 2 | Summer | 15 | 19.71 | -1.4 | 4.77 | 55.3 | 340.7 | 20.44 | 0.29 | 20.73 | 1.4 | 45.4 | 78.76 | -24.67 | 0 | 0 | 0 | Battery-supported
2025-02-05 16:00 | 36 | 2 | Summer | 16 | 19.71 | -0.3 | 8 | 15.2 | 467 | 28.02 | 12.75 | 40.77 | 0.3 | 45 | 77.07 | -4.23 | 0 | 0 | 0 | Battery-supported
2025-02-05 17:00 | 36 | 2 | Summer | 17 | 19.71 | 0.2 | 6.31 | 95.6 | 129.8 | 7.79 | 3.11 | 10.9 | 0 | 45 | 63.43 | -34.1 | 0 | 0 | 0 | Battery-supported
2025-02-05 18:00 | 36 | 2 | Summer | 18 | 19.71 | -4.7 | 3.5 | 59.5 | 209.5 | 12.57 | 0 | 12.57 | 4.7 | 51.29 | 47.94 | -38.72 | 0 | 0 | 0 | Battery-supported
2025-02-05 19:00 | 36 | 2 | Summer | 19 | 19.71 | 1.1 | 7.27 | 43.1 | 195.2 | 11.71 | 7.5 | 19.21 | 0 | 45 | 37.62 | -25.79 | 0 | 0 | 0 | Battery-supported
2025-02-05 20:00 | 36 | 2 | Summer | 20 | 19.71 | -2.4 | 14.31 | 53.3 | 114.7 | 6.88 | 120 | 126.88 | 2.4 | 45 | 67.76 | 81.88 | 0 | 0 | 0 | Normal
2025-02-05 21:00 | 36 | 2 | Summer | 21 | 19.71 | -3.5 | 8.7 | 62.2 | 47.6 | 2.86 | 19.68 | 22.54 | 3.5 | 45 | 58.77 | -22.46 | 0 | 0 | 0 | Battery-supported
2025-02-05 22:00 | 36 | 2 | Summer | 22 | 19.71 | -0.6 | 3.02 | 28.3 | 0 | 0 | 0 | 0 | 0.6 | 45 | 40.77 | -45 | 0 | 0 | 0 | Battery-supported
2025-02-05 23:00 | 36 | 2 | Summer | 23 | 19.71 | -0.5 | 9.53 | 42 | 0 | 0 | 30.69 | 30.69 | 0.5 | 45 | 35.05 | -14.31 | 0 | 0 | 0 | Battery-supported
2025-02-06 | 37 | 2 | Summer | 0 | 19.49 | -2.6 | 5.53 | 82.2 | 0 | 0 | 1.17 | 1.17 | 2.6 | 45 | 17.52 | -43.83 | 0 | 0 | 0 | Battery-supported
2025-02-06 01:00 | 37 | 2 | Summer | 1 | 19.49 | 0.4 | 19.91 | 17.3 | 0 | 0 | 120 | 120 | 0 | 45 | 45.12 | 75 | 0 | 0 | 0 | Normal
2025-02-06 02:00 | 37 | 2 | Summer | 2 | 19.49 | -4.8 | 9.1 | 72.4 | 0 | 0 | 24.58 | 24.58 | 4.8 | 45 | 36.95 | -20.42 | 0 | 0 | 0 | Battery-supported
2025-02-06 03:00 | 37 | 2 | Summer | 3 | 19.49 | -3.1 | 4.46 | 11.4 | 71.8 | 4.31 | 0.12 | 4.43 | 3.1 | 45 | 20.72 | -40.57 | 0 | 0 | 0 | Battery-supported
2025-02-06 04:00 | 37 | 2 | Summer | 4 | 19.49 | -3.9 | 9.96 | 83.8 | 67.6 | 4.06 | 37.73 | 41.79 | 3.9 | 45 | 19.44 | -3.21 | 0 | 0 | 0 | Battery-supported
2025-02-06 05:00 | 37 | 2 | Summer | 5 | 19.49 | -3 | 7.6 | 37.5 | 201.8 | 12.11 | 9.65 | 21.76 | 3 | 45 | 15 | -11.09 | 12.15 | 4.399 | 0 | Diesel-backup
2025-02-06 06:00 | 37 | 2 | Summer | 6 | 19.49 | -2.5 | 13.56 | 28.4 | 293.1 | 17.59 | 120 | 137.59 | 2.5 | 45 | 49.07 | 92.59 | 0 | 0 | 0 | Normal
2025-02-06 07:00 | 37 | 2 | Summer | 7 | 19.49 | -5.5 | 4.76 | 29.2 | 354.7 | 21.28 | 0.28 | 21.56 | 5.5 | 45 | 39.7 | -23.44 | 0 | 0 | 0 | Battery-supported
2025-02-06 08:00 | 37 | 2 | Summer | 8 | 19.49 | -1.8 | 9.09 | 59.6 | 290 | 17.4 | 24.45 | 41.85 | 1.8 | 53.84 | 34.9 | -11.99 | 0 | 0 | 0 | Battery-supported
2025-02-06 09:00 | 37 | 2 | Summer | 9 | 19.49 | -3.2 | 2.13 | 34.5 | 430.5 | 25.83 | 0 | 25.83 | 3.2 | 45 | 27.23 | -19.17 | 0 | 0 | 0 | Battery-supported
2025-02-06 10:00 | 37 | 2 | Summer | 10 | 19.49 | -7.3 | 7.09 | 7.1 | 589 | 35.34 | 6.48 | 41.82 | 7.3 | 58.58 | 20.53 | -16.76 | 0 | 0 | 0 | Battery-supported
2025-02-06 11:00 | 37 | 2 | Summer | 11 | 19.49 | -7.2 | 2.97 | 86.4 | 227.7 | 13.66 | 0 | 13.66 | 7.2 | 53.65 | 15 | -13.82 | 26.17 | 9.004 | 0 | Diesel-backup
2025-02-06 12:00 | 37 | 2 | Summer | 12 | 19.49 | -2.6 | 7.45 | 71 | 306.6 | 18.4 | 8.63 | 27.03 | 2.6 | 45 | 15 | 0 | 17.97 | 6.372 | 0 | Diesel-backup
2025-02-06 13:00 | 37 | 2 | Summer | 13 | 19.49 | -2.7 | 8.45 | 4.1 | 627.5 | 37.65 | 16.98 | 54.63 | 2.7 | 45 | 18.54 | 9.63 | 0 | 0 | 0 | Normal
2025-02-06 14:00 | 37 | 2 | Summer | 14 | 19.49 | -2.1 | 8.88 | 78 | 258.1 | 15.49 | 21.8 | 37.29 | 2.1 | 45.87 | 15.11 | -8.58 | 0 | 0 | 0 | Battery-supported
2025-02-06 15:00 | 37 | 2 | Summer | 15 | 19.49 | -1.5 | 4.76 | 38.5 | 413.1 | 24.79 | 0.28 | 25.07 | 1.5 | 45 | 15 | -0.28 | 19.65 | 6.926 | 0 | Diesel-backup
2025-02-06 16:00 | 37 | 2 | Summer | 16 | 19.49 | -0.6 | 7.22 | 48.2 | 334.9 | 20.09 | 7.21 | 27.3 | 0.6 | 45 | 15 | 0 | 17.7 | 6.283 | 0 | Diesel-backup
2025-02-06 17:00 | 37 | 2 | Summer | 17 | 19.49 | 1.3 | 12.6 | 33.9 | 338.6 | 20.32 | 105.47 | 125.79 | 0 | 45 | 44.73 | 80.79 | 0 | 0 | 0 | Normal
2025-02-06 18:00 | 37 | 2 | Summer | 18 | 19.49 | -3 | 16.79 | 42.2 | 254.5 | 15.27 | 120 | 135.27 | 3 | 52.2 | 75.3 | 83.07 | 0 | 0 | 0 | Normal
2025-02-06 19:00 | 37 | 2 | Summer | 19 | 19.49 | -3 | 7.37 | 97 | 76.6 | 4.6 | 8.11 | 12.71 | 3 | 46.62 | 61.74 | -33.91 | 0 | 0 | 0 | Battery-supported
2025-02-06 20:00 | 37 | 2 | Summer | 20 | 19.49 | -2.8 | 12.8 | 42.1 | 124.6 | 7.48 | 112.58 | 120.06 | 2.8 | 47.68 | 88.37 | 72.38 | 0 | 0 | 0 | Normal
2025-02-06 21:00 | 37 | 2 | Summer | 21 | 19.49 | 0.2 | 3.72 | 51.4 | 48.3 | 2.9 | 0 | 2.9 | 0 | 45 | 71.53 | -42.1 | 0 | 0 | 0 | Battery-supported
2025-02-06 22:00 | 37 | 2 | Summer | 22 | 19.49 | 2.2 | 5.25 | 35.2 | 0 | 0 | 0.75 | 0.75 | 0 | 45 | 53.83 | -44.25 | 0 | 0 | 0 | Battery-supported
2025-02-06 23:00 | 37 | 2 | Summer | 23 | 19.49 | -1.7 | 7.86 | 63.9 | 0 | 0 | 11.6 | 11.6 | 1.7 | 45.32 | 40.34 | -33.72 | 0 | 0 | 0 | Battery-supported
2025-02-07 | 38 | 2 | Summer | 0 | 19.28 | -6.7 | 6.35 | 57.5 | 0 | 0 | 3.24 | 3.24 | 6.7 | 45 | 23.64 | -41.76 | 0 | 0 | 0 | Battery-supported
2025-02-07 01:00 | 38 | 2 | Summer | 1 | 19.28 | -5.3 | 5.95 | 97.4 | 0 | 0 | 2.06 | 2.06 | 5.3 | 50.82 | 15 | -21.6 | 27.16 | 9.311 | 0 | Diesel-backup
2025-02-07 02:00 | 38 | 2 | Summer | 2 | 19.28 | -3.8 | 12.06 | 42.4 | 0 | 0 | 87.79 | 87.79 | 3.8 | 45 | 30.75 | 42.79 | 0 | 0 | 0 | Normal
2025-02-07 03:00 | 38 | 2 | Summer | 3 | 19.28 | -3.5 | 3.32 | 70.4 | 32.2 | 1.93 | 0 | 1.93 | 3.5 | 45 | 15 | -39.37 | 3.7 | 1.381 | 0 | Diesel-backup
2025-02-07 04:00 | 38 | 2 | Summer | 4 | 19.28 | -3.6 | 3.56 | 62.7 | 91.6 | 5.5 | 0 | 5.5 | 3.6 | 45 | 15 | 0 | 39.5 | 12.918 | 0 | Diesel-backup
2025-02-07 05:00 | 38 | 2 | Summer | 5 | 19.28 | -2.9 | 2.64 | 67.6 | 134.8 | 8.09 | 0 | 8.09 | 2.9 | 45 | 15 | 0 | 36.91 | 12.193 | 0 | Diesel-backup
2025-02-07 06:00 | 38 | 2 | Summer | 6 | 19.28 | -3.9 | 8.02 | 75.5 | 158.9 | 9.53 | 12.92 | 22.45 | 3.9 | 45 | 15 | 0 | 22.55 | 7.864 | 0 | Diesel-backup
2025-02-07 07:00 | 38 | 2 | Summer | 7 | 19.28 | -1.1 | 5.53 | 39.1 | 318.1 | 19.09 | 1.17 | 20.26 | 1.1 | 45 | 15 | 0 | 24.74 | 8.558 | 0 | Diesel-backup
2025-02-07 08:00 | 38 | 2 | Summer | 8 | 19.28 | -4.9 | 11.4 | 14.2 | 466 | 27.96 | 69.01 | 96.97 | 4.9 | 45 | 34.12 | 51.97 | 0 | 0 | 0 | Normal
2025-02-07 09:00 | 38 | 2 | Summer | 9 | 19.28 | -5.3 | 7.61 | 25.5 | 468.2 | 28.09 | 9.72 | 37.81 | 5.3 | 48.71 | 29.76 | -10.9 | 0 | 0 | 0 | Battery-supported
2025-02-07 10:00 | 38 | 2 | Summer | 10 | 19.28 | -2.2 | 4.7 | 9.8 | 575.8 | 34.55 | 0.24 | 34.79 | 2.2 | 51.07 | 23.25 | -16.28 | 0 | 0 | 0 | Battery-supported
2025-02-07 11:00 | 38 | 2 | Summer | 11 | 19.28 | -6.4 | 4.23 | 69.4 | 310.4 | 18.62 | 0.05 | 18.67 | 6.4 | 46.88 | 15 | -20.63 | 7.58 | 2.788 | 0 | Diesel-backup
2025-02-07 12:00 | 38 | 2 | Summer | 12 | 19.28 | -1.8 | 0.98 | 76.7 | 278.4 | 16.7 | 0 | 16.7 | 1.8 | 47.12 | 15 | 0 | 30.42 | 10.302 | 0 | Diesel-backup
2025-02-07 13:00 | 38 | 2 | Summer | 13 | 19.28 | -2.1 | 6.11 | 54.7 | 381.7 | 22.9 | 2.49 | 25.39 | 2.1 | 45 | 15 | 0 | 19.61 | 6.913 | 0 | Diesel-backup
2025-02-07 14:00 | 38 | 2 | Summer | 14 | 19.28 | -2.3 | 3 | 29.6 | 483.4 | 29 | 0 | 29 | 2.3 | 49.08 | 15 | 0 | 20.08 | 7.066 | 0 | Diesel-backup
2025-02-07 15:00 | 38 | 2 | Summer | 15 | 19.28 | 2 | 12.23 | 63.2 | 304.4 | 18.26 | 93.12 | 111.38 | 0 | 45 | 39.43 | 66.38 | 0 | 0 | 0 | Normal
2025-02-07 16:00 | 38 | 2 | Summer | 16 | 19.28 | -2.5 | 5.36 | 51.8 | 318.9 | 19.13 | 0.9 | 20.03 | 2.5 | 46.57 | 28.81 | -26.54 | 0 | 0 | 0 | Battery-supported
2025-02-07 17:00 | 38 | 2 | Summer | 17 | 19.28 | 3.7 | 2.31 | 85.8 | 160.5 | 9.63 | 0 | 9.63 | 0 | 45 | 15 | -34.53 | 0.84 | 0.316 | 0 | Diesel-backup
2025-02-07 18:00 | 38 | 2 | Summer | 18 | 19.28 | -1.1 | 13.63 | 50.4 | 227.9 | 13.67 | 120 | 133.67 | 1.1 | 45 | 47.63 | 88.67 | 0 | 0 | 0 | Normal
2025-02-07 19:00 | 38 | 2 | Summer | 19 | 19.28 | -3.3 | 6.17 | 73.4 | 122.8 | 7.37 | 2.66 | 10.03 | 3.3 | 45 | 33.64 | -34.97 | 0 | 0 | 0 | Battery-supported
2025-02-07 20:00 | 38 | 2 | Summer | 20 | 19.28 | -0.3 | 9.52 | 82.2 | 66.4 | 3.98 | 30.54 | 34.52 | 0.3 | 45 | 29.45 | -10.48 | 0 | 0 | 0 | Battery-supported
2025-02-07 21:00 | 38 | 2 | Summer | 21 | 19.28 | -2.8 | 4.74 | 18.2 | 58.8 | 3.53 | 0.27 | 3.8 | 2.8 | 45 | 15 | -36.13 | 5.07 | 1.883 | 0 | Diesel-backup
2025-02-07 22:00 | 38 | 2 | Summer | 22 | 19.28 | -2.3 | 13.89 | 75.9 | 0 | 0 | 120 | 120 | 2.3 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-02-07 23:00 | 38 | 2 | Summer | 23 | 19.28 | 0 | 3.86 | 94.4 | 0 | 0 | 0.01 | 0.01 | 0 | 45 | 24.6 | -44.99 | 0 | 0 | 0 | Battery-supported
2025-02-08 | 39 | 2 | Summer | 0 | 19.07 | 0 | 5.54 | 19.2 | 0 | 0 | 1.19 | 1.19 | 0 | 45 | 15 | -24.01 | 19.8 | 6.975 | 0 | Diesel-backup
2025-02-08 01:00 | 39 | 2 | Summer | 1 | 19.07 | -3 | 1.78 | 79.4 | 0 | 0 | 0 | 0 | 3 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-02-08 02:00 | 39 | 2 | Summer | 2 | 19.07 | 0.2 | 13.73 | 75.9 | 0 | 0 | 120 | 120 | 0 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-02-08 03:00 | 39 | 2 | Summer | 3 | 19.07 | 0.1 | 4.37 | 23.3 | 47.5 | 2.85 | 0.09 | 2.94 | 0 | 45 | 25.78 | -42.06 | 0 | 0 | 0 | Battery-supported
2025-02-08 04:00 | 39 | 2 | Summer | 4 | 19.07 | 0.4 | 8.15 | 51.7 | 100.4 | 6.02 | 14.07 | 20.09 | 0 | 45 | 15.81 | -24.91 | 0 | 0 | 0 | Battery-supported
2025-02-08 05:00 | 39 | 2 | Summer | 5 | 19.07 | -1.9 | 8.84 | 34.9 | 196.3 | 11.78 | 21.31 | 33.09 | 1.9 | 45 | 15 | -2.03 | 9.88 | 3.606 | 0 | Diesel-backup
2025-02-08 06:00 | 39 | 2 | Summer | 6 | 19.07 | -0.3 | 12.47 | 80.8 | 142 | 8.52 | 101.02 | 109.54 | 0.3 | 45 | 38.75 | 64.54 | 0 | 0 | 0 | Normal
2025-02-08 07:00 | 39 | 2 | Summer | 7 | 19.07 | -7.6 | 7.78 | 15.2 | 394.8 | 23.69 | 10.97 | 34.66 | 7.6 | 45 | 34.61 | -10.34 | 0 | 0 | 0 | Battery-supported
2025-02-08 08:00 | 39 | 2 | Summer | 8 | 19.07 | -4.2 | 6.41 | 100 | 129.6 | 7.78 | 3.45 | 11.23 | 4.2 | 52.63 | 18.05 | -41.4 | 0 | 0 | 0 | Battery-supported
2025-02-08 09:00 | 39 | 2 | Summer | 9 | 19.07 | -5.4 | 11.74 | 77.1 | 243.4 | 14.6 | 78.31 | 92.91 | 5.4 | 45.29 | 35.58 | 47.62 | 0 | 0 | 0 | Normal
2025-02-08 10:00 | 39 | 2 | Summer | 10 | 19.07 | -3 | 8.75 | 57.2 | 354.6 | 21.28 | 20.25 | 41.53 | 3 | 45 | 34.19 | -3.47 | 0 | 0 | 0 | Battery-supported
2025-02-08 11:00 | 39 | 2 | Summer | 11 | 19.07 | -4.3 | 5.81 | 18.2 | 558.6 | 33.52 | 1.73 | 35.25 | 4.3 | 45 | 30.29 | -9.75 | 0 | 0 | 0 | Battery-supported
2025-02-08 12:00 | 39 | 2 | Summer | 12 | 19.07 | -3.1 | 14.08 | 55.4 | 383.6 | 23.02 | 120 | 143.02 | 3.1 | 45.58 | 66.15 | 97.44 | 0 | 0 | 0 | Normal
2025-02-08 13:00 | 39 | 2 | Summer | 13 | 19.07 | 1.7 | 9.15 | 75.5 | 280.5 | 16.83 | 25.24 | 42.07 | 0 | 45 | 64.98 | -2.93 | 0 | 0 | 0 | Battery-supported
2025-02-08 14:00 | 39 | 2 | Summer | 14 | 19.07 | -2.4 | 2.83 | 34.5 | 459.9 | 27.59 | 0 | 27.59 | 2.4 | 45 | 58.01 | -17.41 | 0 | 0 | 0 | Battery-supported
2025-02-08 15:00 | 39 | 2 | Summer | 15 | 19.07 | -0.7 | 15.53 | 98.4 | 151.3 | 9.08 | 120 | 129.08 | 0.7 | 45 | 88.95 | 84.08 | 0 | 0 | 0 | Normal
2025-02-08 16:00 | 39 | 2 | Summer | 16 | 19.07 | -1.8 | 4.67 | 66 | 262.1 | 15.73 | 0.22 | 15.95 | 1.8 | 45 | 77.33 | -29.05 | 0 | 0 | 0 | Battery-supported
2025-02-08 17:00 | 39 | 2 | Summer | 17 | 19.07 | -0.8 | 12.43 | 49.7 | 279.5 | 16.77 | 99.67 | 116.44 | 0.8 | 45 | 95 | 48 | 0 | 0 | 0 | Normal
2025-02-08 18:00 | 39 | 2 | Summer | 18 | 19.07 | -0.7 | 2.35 | 48.3 | 230.1 | 13.81 | 0 | 13.81 | 0.7 | 45.13 | 82.47 | -31.32 | 0 | 0 | 0 | Battery-supported
2025-02-08 19:00 | 39 | 2 | Summer | 19 | 19.07 | 0.4 | 11.7 | 30.9 | 204.4 | 12.26 | 77.17 | 89.43 | 0 | 45 | 95 | 34.04 | 0 | 0 | 0 | Normal
2025-02-08 20:00 | 39 | 2 | Summer | 20 | 19.07 | 2.1 | 2.95 | 35.6 | 120.2 | 7.21 | 0 | 7.21 | 0 | 49.44 | 78.11 | -42.23 | 0 | 0 | 0 | Battery-supported
2025-02-08 21:00 | 39 | 2 | Summer | 21 | 19.07 | 3.1 | 7.66 | 51.1 | 35.5 | 2.13 | 10.08 | 12.21 | 0 | 45 | 64.99 | -32.79 | 0 | 0 | 0 | Battery-supported
2025-02-08 22:00 | 39 | 2 | Summer | 22 | 19.07 | 0 | 9 | 59.2 | 0 | 0 | 23.29 | 23.29 | 0 | 45 | 56.31 | -21.71 | 0 | 0 | 0 | Battery-supported
2025-02-08 23:00 | 39 | 2 | Summer | 23 | 19.07 | 0.3 | 5.89 | 55.7 | 0 | 0 | 1.91 | 1.91 | 0 | 45 | 39.07 | -43.09 | 0 | 0 | 0 | Battery-supported
2025-02-09 | 40 | 2 | Summer | 0 | 18.86 | -3.9 | 6.9 | 75.6 | 0 | 0 | 5.5 | 5.5 | 3.9 | 45 | 23.27 | -39.5 | 0 | 0 | 0 | Battery-supported
2025-02-09 01:00 | 40 | 2 | Summer | 1 | 18.86 | -1.9 | 3.42 | 71.1 | 0 | 0 | 0 | 0 | 1.9 | 45 | 15 | -20.68 | 24.32 | 8.426 | 0 | Diesel-backup
2025-02-09 02:00 | 40 | 2 | Summer | 2 | 18.86 | 0 | 11.02 | 14.3 | 0 | 0 | 59.52 | 59.52 | 0 | 45 | 20.34 | 14.52 | 0 | 0 | 0 | Normal
2025-02-09 03:00 | 40 | 2 | Summer | 3 | 18.86 | -0.6 | 7.92 | 48.4 | 30 | 1.8 | 12.09 | 13.89 | 0.6 | 45 | 15 | -13.36 | 17.75 | 6.3 | 0 | Diesel-backup
2025-02-09 04:00 | 40 | 2 | Summer | 4 | 18.86 | -2.4 | 3.86 | 48.6 | 98.4 | 5.9 | 0.01 | 5.91 | 2.4 | 45 | 15 | 0 | 39.09 | 12.805 | 0 | Diesel-backup
2025-02-09 05:00 | 40 | 2 | Summer | 5 | 18.86 | -1.2 | 8.1 | 14.9 | 229.6 | 13.78 | 13.62 | 27.4 | 1.2 | 45 | 15 | 0 | 17.6 | 6.249 | 0 | Diesel-backup
2025-02-09 06:00 | 40 | 2 | Summer | 6 | 18.86 | -2.3 | 8.25 | 33.5 | 265.6 | 15.94 | 15 | 30.94 | 2.3 | 46.48 | 15 | 0 | 15.54 | 5.559 | 0 | Diesel-backup
2025-02-09 07:00 | 40 | 2 | Summer | 7 | 18.86 | -0.9 | 7.1 | 62 | 236.1 | 14.17 | 6.53 | 20.7 | 0.9 | 45 | 15 | 0 | 24.3 | 8.42 | 0 | Diesel-backup
2025-02-09 08:00 | 40 | 2 | Summer | 8 | 18.86 | -3 | 1 | 11 | 473.2 | 28.39 | 0 | 28.39 | 3 | 45 | 15 | 0 | 16.61 | 5.919 | 0 | Diesel-backup
2025-02-09 09:00 | 40 | 2 | Summer | 9 | 18.86 | -4.3 | 5.38 | 71 | 269.2 | 16.15 | 0.93 | 17.08 | 4.3 | 54.19 | 15 | 0 | 37.11 | 12.25 | 0 | Diesel-backup
2025-02-09 10:00 | 40 | 2 | Summer | 10 | 18.86 | -2.7 | 10.93 | 6.7 | 588.6 | 35.32 | 57.41 | 92.73 | 2.7 | 48.61 | 31.24 | 44.12 | 0 | 0 | 0 | Normal
2025-02-09 11:00 | 40 | 2 | Summer | 11 | 18.86 | -9.6 | 9.32 | 26.8 | 517 | 31.02 | 27.59 | 58.61 | 9.6 | 53.34 | 33.18 | 5.27 | 0 | 0 | 0 | Normal
2025-02-09 12:00 | 40 | 2 | Summer | 12 | 18.86 | -2 | 9.15 | 61.5 | 353.3 | 21.2 | 25.24 | 46.44 | 2 | 48.24 | 32.46 | -1.8 | 0 | 0 | 0 | Battery-supported
2025-02-09 13:00 | 40 | 2 | Summer | 13 | 18.86 | -10.5 | 7.88 | 52.9 | 390.3 | 23.42 | 11.76 | 35.18 | 10.5 | 50.78 | 26.22 | -15.6 | 0 | 0 | 0 | Battery-supported
2025-02-09 14:00 | 40 | 2 | Summer | 14 | 18.86 | -5.9 | 11.66 | 34.6 | 458.9 | 27.53 | 76.05 | 103.58 | 5.9 | 45 | 47.77 | 58.58 | 0 | 0 | 0 | Normal
2025-02-09 15:00 | 40 | 2 | Summer | 15 | 18.86 | -0.7 | 4.66 | 40.2 | 402.1 | 24.13 | 0.22 | 24.35 | 0.7 | 45 | 39.51 | -20.65 | 0 | 0 | 0 | Battery-supported
2025-02-09 16:00 | 40 | 2 | Summer | 16 | 18.86 | -0.3 | 4.03 | 83.7 | 191.8 | 11.51 | 0.02 | 11.53 | 0.3 | 45 | 26.12 | -33.47 | 0 | 0 | 0 | Battery-supported
2025-02-09 17:00 | 40 | 2 | Summer | 17 | 18.86 | -3.6 | 17.77 | 28.3 | 347.8 | 20.87 | 120 | 140.87 | 3.6 | 45 | 61.41 | 95.87 | 0 | 0 | 0 | Normal
2025-02-09 18:00 | 40 | 2 | Summer | 18 | 18.86 | -2.4 | 4.34 | 72.2 | 162.7 | 9.76 | 0.08 | 9.84 | 2.4 | 45 | 47.34 | -35.16 | 0 | 0 | 0 | Battery-supported
2025-02-09 19:00 | 40 | 2 | Summer | 19 | 18.86 | 2.4 | 2.76 | 7.2 | 244.5 | 14.67 | 0 | 14.67 | 0 | 45 | 35.21 | -30.33 | 0 | 0 | 0 | Battery-supported
2025-02-09 20:00 | 40 | 2 | Summer | 20 | 18.86 | -1.7 | 5.84 | 22.8 | 128.5 | 7.71 | 1.79 | 9.5 | 1.7 | 45 | 21.01 | -35.5 | 0 | 0 | 0 | Battery-supported
2025-02-09 21:00 | 40 | 2 | Summer | 21 | 18.86 | 4.3 | 7.26 | 68.3 | 23 | 1.38 | 7.44 | 8.82 | 0 | 45 | 15 | -15.02 | 21.16 | 7.416 | 0 | Diesel-backup
2025-02-09 22:00 | 40 | 2 | Summer | 22 | 18.86 | -0.8 | 11.7 | 55.5 | 0 | 0 | 77.17 | 77.17 | 0.8 | 45 | 26.84 | 32.17 | 0 | 0 | 0 | Normal
2025-02-09 23:00 | 40 | 2 | Summer | 23 | 18.86 | -0.1 | 5.39 | 24.6 | 0 | 0 | 0.94 | 0.94 | 0.1 | 45 | 15 | -29.6 | 14.46 | 5.194 | 0 | Diesel-backup
2025-02-10 | 41 | 2 | Summer | 0 | 18.66 | 2.1 | 5.37 | 57.2 | 0 | 0 | 0.92 | 0.92 | 0 | 45 | 15 | 0 | 44.08 | 14.158 | 0 | Diesel-backup
2025-02-10 01:00 | 41 | 2 | Summer | 1 | 18.66 | -1.5 | 6.87 | 36.5 | 0 | 0 | 5.36 | 5.36 | 1.5 | 45 | 15 | 0 | 39.64 | 12.957 | 0 | Diesel-backup
2025-02-10 02:00 | 41 | 2 | Summer | 2 | 18.66 | -4.4 | 4.82 | 50.4 | 0 | 0 | 0.32 | 0.32 | 4.4 | 45 | 15 | 0 | 44.68 | 14.316 | 0 | Diesel-backup
2025-02-10 03:00 | 41 | 2 | Summer | 3 | 18.66 | -2.8 | 2.38 | 41.6 | 25.2 | 1.51 | 0 | 1.51 | 2.8 | 45 | 15 | 0 | 43.49 | 14.001 | 0 | Diesel-backup
2025-02-10 04:00 | 41 | 2 | Summer | 4 | 18.66 | -3 | 2.93 | 43.1 | 98.7 | 5.92 | 0 | 5.92 | 3 | 45 | 15 | 0 | 39.08 | 12.802 | 0 | Diesel-backup
2025-02-10 05:00 | 41 | 2 | Summer | 5 | 18.66 | -6.2 | 13.53 | 82.2 | 96.2 | 5.77 | 120 | 125.77 | 6.2 | 45 | 44.72 | 80.77 | 0 | 0 | 0 | Normal
2025-02-10 06:00 | 41 | 2 | Summer | 6 | 18.66 | -4 | 10.31 | 76.5 | 148.6 | 8.92 | 44.2 | 53.12 | 4 | 45 | 47.71 | 8.12 | 0 | 0 | 0 | Normal
2025-02-10 07:00 | 41 | 2 | Summer | 7 | 18.66 | -5.3 | 6.73 | 8.4 | 409.4 | 24.56 | 4.72 | 29.28 | 5.3 | 45 | 41.42 | -15.72 | 0 | 0 | 0 | Battery-supported
2025-02-10 08:00 | 41 | 2 | Summer | 8 | 18.66 | -1.6 | 9.32 | 6.4 | 488.3 | 29.3 | 27.59 | 56.89 | 1.6 | 54.66 | 42.24 | 2.23 | 0 | 0 | 0 | Normal
2025-02-10 09:00 | 41 | 2 | Summer | 9 | 18.66 | -3.6 | 10.49 | 50.3 | 357.4 | 21.44 | 47.8 | 69.24 | 3.6 | 45 | 51.16 | 24.24 | 0 | 0 | 0 | Normal
2025-02-10 10:00 | 41 | 2 | Summer | 10 | 18.66 | -4.1 | 4.5 | 49.7 | 388.3 | 23.3 | 0.14 | 23.44 | 4.1 | 46.23 | 42.05 | -22.79 | 0 | 0 | 0 | Battery-supported
2025-02-10 11:00 | 41 | 2 | Summer | 11 | 18.66 | -3.5 | 3.4 | 15.7 | 570.4 | 34.22 | 0 | 34.22 | 3.5 | 45 | 37.74 | -10.78 | 0 | 0 | 0 | Battery-supported
2025-02-10 12:00 | 41 | 2 | Summer | 12 | 18.66 | -2.4 | 12.75 | 60.3 | 359.5 | 21.57 | 110.77 | 132.34 | 2.4 | 45 | 69.88 | 87.34 | 0 | 0 | 0 | Normal
2025-02-10 13:00 | 41 | 2 | Summer | 13 | 18.66 | -1.2 | 1.23 | 48.2 | 412.7 | 24.76 | 0 | 24.76 | 1.2 | 45 | 61.78 | -20.24 | 0 | 0 | 0 | Battery-supported
2025-02-10 14:00 | 41 | 2 | Summer | 14 | 18.66 | -4.4 | 9.4 | 56.1 | 358.6 | 21.52 | 28.75 | 50.27 | 4.4 | 45 | 63.72 | 5.27 | 0 | 0 | 0 | Normal
2025-02-10 15:00 | 41 | 2 | Summer | 15 | 18.66 | -4.1 | 7.63 | 37.1 | 414.3 | 24.86 | 9.86 | 34.72 | 4.1 | 47.84 | 58.47 | -13.12 | 0 | 0 | 0 | Battery-supported
2025-02-10 16:00 | 41 | 2 | Summer | 16 | 18.66 | 1 | 12.03 | 67.8 | 252.2 | 15.13 | 86.87 | 102 | 0 | 45 | 79.45 | 57 | 0 | 0 | 0 | Normal
2025-02-10 17:00 | 41 | 2 | Summer | 17 | 18.66 | -2 | 9.6 | 76 | 187.9 | 11.27 | 31.77 | 43.04 | 2 | 45 | 78.66 | -1.96 | 0 | 0 | 0 | Battery-supported
2025-02-10 18:00 | 41 | 2 | Summer | 18 | 18.66 | -4 | 9.28 | 51.4 | 214.5 | 12.87 | 27.03 | 39.9 | 4 | 52.07 | 73.8 | -12.17 | 0 | 0 | 0 | Battery-supported
2025-02-10 19:00 | 41 | 2 | Summer | 19 | 18.66 | 0.2 | 3.64 | 32.3 | 190.1 | 11.41 | 0 | 11.41 | 0 | 45.23 | 60.27 | -33.82 | 0 | 0 | 0 | Battery-supported
2025-02-10 20:00 | 41 | 2 | Summer | 20 | 18.66 | 0.3 | 10.72 | 17.6 | 126.6 | 7.6 | 52.68 | 60.28 | 0 | 46.34 | 65.4 | 13.94 | 0 | 0 | 0 | Normal
2025-02-10 21:00 | 41 | 2 | Summer | 21 | 18.66 | -4.1 | 8.74 | 66.6 | 18.3 | 1.1 | 20.14 | 21.24 | 4.1 | 45 | 55.89 | -23.76 | 0 | 0 | 0 | Battery-supported
2025-02-10 22:00 | 41 | 2 | Summer | 22 | 18.66 | -0.4 | 3.97 | 17.4 | 0 | 0 | 0.01 | 0.01 | 0.4 | 45 | 37.9 | -44.99 | 0 | 0 | 0 | Battery-supported
2025-02-10 23:00 | 41 | 2 | Summer | 23 | 18.66 | 0.5 | 7.67 | 89.8 | 0 | 0 | 10.15 | 10.15 | 0 | 45 | 23.96 | -34.85 | 0 | 0 | 0 | Battery-supported
2025-02-11 | 42 | 2 | Summer | 0 | 18.47 | -0.7 | 3.14 | 66.1 | 0 | 0 | 0 | 0 | 0.7 | 45 | 15 | -22.4 | 22.6 | 7.881 | 0 | Diesel-backup
2025-02-11 01:00 | 42 | 2 | Summer | 1 | 18.47 | -0.5 | 6.17 | 85.7 | 0 | 0 | 2.66 | 2.66 | 0.5 | 45 | 15 | 0 | 42.34 | 13.693 | 0 | Diesel-backup
2025-02-11 02:00 | 42 | 2 | Summer | 2 | 18.47 | -5.4 | 21.94 | 76.5 | 0 | 0 | 120 | 120 | 5.4 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-02-11 03:00 | 42 | 2 | Summer | 3 | 18.47 | -1.9 | 3.51 | 76.2 | 11.2 | 0.67 | 0 | 0.67 | 1.9 | 45 | 24.87 | -44.33 | 0 | 0 | 0 | Battery-supported
2025-02-11 04:00 | 42 | 2 | Summer | 4 | 18.47 | -3.7 | 2.36 | 48.5 | 86.9 | 5.21 | 0 | 5.21 | 3.7 | 45 | 15 | -24.67 | 15.12 | 5.417 | 0 | Diesel-backup
2025-02-11 05:00 | 42 | 2 | Summer | 5 | 18.47 | -4.4 | 2.96 | 55.7 | 141.7 | 8.5 | 0 | 8.5 | 4.4 | 45 | 15 | 0 | 36.5 | 12.077 | 0 | Diesel-backup
2025-02-11 06:00 | 42 | 2 | Summer | 6 | 18.47 | -1.7 | 6.12 | 72.6 | 156.2 | 9.37 | 2.52 | 11.89 | 1.7 | 45 | 15 | 0 | 33.11 | 11.099 | 0 | Diesel-backup
2025-02-11 07:00 | 42 | 2 | Summer | 7 | 18.47 | -0.5 | 10.03 | 62.8 | 228.9 | 13.73 | 38.97 | 52.7 | 0.5 | 45 | 17.83 | 7.7 | 0 | 0 | 0 | Normal
2025-02-11 08:00 | 42 | 2 | Summer | 8 | 18.47 | 0.2 | 7.01 | 58.3 | 287 | 17.22 | 6.05 | 23.27 | 0 | 45 | 15 | -7.08 | 14.65 | 5.256 | 0 | Diesel-backup
2025-02-11 09:00 | 42 | 2 | Summer | 9 | 18.47 | -0.8 | 2.62 | 12.3 | 519.7 | 31.18 | 0 | 31.18 | 0.8 | 47.2 | 15 | 0 | 16.02 | 5.721 | 0 | Diesel-backup
2025-02-11 10:00 | 42 | 2 | Summer | 10 | 18.47 | -3.8 | 9.96 | 43.5 | 416.6 | 25 | 37.73 | 62.73 | 3.8 | 45.19 | 21.45 | 17.54 | 0 | 0 | 0 | Normal
2025-02-11 11:00 | 42 | 2 | Summer | 11 | 18.47 | -2.6 | 1.62 | 12.7 | 584.8 | 35.09 | 0 | 35.09 | 2.6 | 45.88 | 17.14 | -10.79 | 0 | 0 | 0 | Battery-supported
2025-02-11 12:00 | 42 | 2 | Summer | 12 | 18.47 | -1.3 | 2.84 | 4.8 | 632.4 | 37.94 | 0 | 37.94 | 1.3 | 48.71 | 15 | -5.35 | 5.42 | 2.01 | 0 | Diesel-backup
2025-02-11 13:00 | 42 | 2 | Summer | 13 | 18.47 | -2.4 | 4.7 | 73.7 | 288.9 | 17.33 | 0.24 | 17.57 | 2.4 | 50.76 | 15 | 0 | 33.19 | 11.123 | 0 | Diesel-backup
2025-02-11 14:00 | 42 | 2 | Summer | 14 | 18.47 | -2 | 12.52 | 49.3 | 389.6 | 23.38 | 102.71 | 126.09 | 2 | 45 | 44.84 | 81.09 | 0 | 0 | 0 | Normal
2025-02-11 15:00 | 42 | 2 | Summer | 15 | 18.47 | -0.1 | 7.18 | 58 | 323.3 | 19.4 | 6.98 | 26.38 | 0.1 | 45 | 37.39 | -18.62 | 0 | 0 | 0 | Battery-supported
2025-02-11 16:00 | 42 | 2 | Summer | 16 | 18.47 | -1.7 | 7.35 | 57.3 | 290.9 | 17.45 | 7.99 | 25.44 | 1.7 | 50.69 | 27.29 | -25.25 | 0 | 0 | 0 | Battery-supported
2025-02-11 17:00 | 42 | 2 | Summer | 17 | 18.47 | -2.8 | 2.65 | 80.7 | 170.7 | 10.24 | 0 | 10.24 | 2.8 | 45.4 | 15 | -30.73 | 4.43 | 1.647 | 0 | Diesel-backup
2025-02-11 18:00 | 42 | 2 | Summer | 18 | 18.47 | -1.9 | 5.01 | 48.7 | 217.6 | 13.06 | 0.48 | 13.54 | 1.9 | 45 | 15 | 0 | 31.46 | 10.612 | 0 | Diesel-backup
2025-02-11 19:00 | 42 | 2 | Summer | 19 | 18.47 | 0.6 | 11.49 | 27.5 | 193.1 | 11.59 | 71.39 | 82.98 | 0 | 45 | 28.98 | 37.98 | 0 | 0 | 0 | Normal
2025-02-11 20:00 | 42 | 2 | Summer | 20 | 18.47 | -0.8 | 8.43 | 62.2 | 73 | 4.38 | 16.77 | 21.15 | 0.8 | 45 | 19.44 | -23.85 | 0 | 0 | 0 | Battery-supported
2025-02-11 21:00 | 42 | 2 | Summer | 21 | 18.47 | -0.1 | 10.17 | 25.7 | 21.1 | 1.27 | 41.53 | 42.8 | 0.1 | 45 | 18.56 | -2.2 | 0 | 0 | 0 | Battery-supported
2025-02-11 22:00 | 42 | 2 | Summer | 22 | 18.47 | 0.5 | 6.71 | 71.7 | 0 | 0 | 4.63 | 4.63 | 0 | 45 | 15 | -8.89 | 31.48 | 10.618 | 0 | Diesel-backup
2025-02-11 23:00 | 42 | 2 | Summer | 23 | 18.47 | -2 | 11.56 | 41.7 | 0 | 0 | 73.29 | 73.29 | 2 | 45 | 25.41 | 28.29 | 0 | 0 | 0 | Normal
2025-02-12 | 43 | 2 | Summer | 0 | 18.28 | 0 | 2.64 | 24.7 | 0 | 0 | 0 | 0 | 0 | 45 | 15 | -26.03 | 18.97 | 6.704 | 0 | Diesel-backup
2025-02-12 01:00 | 43 | 2 | Summer | 1 | 18.28 | -1.1 | 6.04 | 68.9 | 0 | 0 | 2.29 | 2.29 | 1.1 | 45 | 15 | 0 | 42.71 | 13.792 | 0 | Diesel-backup
2025-02-12 02:00 | 43 | 2 | Summer | 2 | 18.28 | -5.1 | 9.2 | 54.3 | 0 | 0 | 25.92 | 25.92 | 5.1 | 45 | 15 | 0 | 19.08 | 6.739 | 0 | Diesel-backup
2025-02-12 03:00 | 43 | 2 | Summer | 3 | 18.28 | 0.4 | 2.04 | 31.3 | 11.9 | 0.71 | 0 | 0.71 | 0 | 45 | 15 | 0 | 44.29 | 14.213 | 0 | Diesel-backup
2025-02-12 04:00 | 43 | 2 | Summer | 4 | 18.28 | -4.2 | 0.77 | 46.1 | 83.4 | 5 | 0 | 5 | 4.2 | 45 | 15 | 0 | 40 | 13.056 | 0 | Diesel-backup
2025-02-12 05:00 | 43 | 2 | Summer | 5 | 18.28 | -7.1 | 17.88 | 55.5 | 137.6 | 8.26 | 120 | 128.26 | 7.1 | 45 | 45.64 | 83.26 | 0 | 0 | 0 | Normal
2025-02-12 06:00 | 43 | 2 | Summer | 6 | 18.28 | -6 | 7.25 | 79.3 | 136.4 | 8.18 | 7.38 | 15.56 | 6 | 45 | 33.86 | -29.44 | 0 | 0 | 0 | Battery-supported
2025-02-12 07:00 | 43 | 2 | Summer | 7 | 18.28 | -6.1 | 1.88 | 44.4 | 285.6 | 17.14 | 0 | 17.14 | 6.1 | 45 | 22.72 | -27.86 | 0 | 0 | 0 | Battery-supported
2025-02-12 08:00 | 43 | 2 | Summer | 8 | 18.28 | -3.8 | 7.14 | 43.6 | 341.2 | 20.47 | 6.75 | 27.22 | 3.8 | 46.09 | 15.17 | -18.87 | 0 | 0 | 0 | Battery-supported
2025-02-12 09:00 | 43 | 2 | Summer | 9 | 18.28 | -4.4 | 2.87 | 49.2 | 360.1 | 21.61 | 0 | 21.61 | 4.4 | 49.88 | 15 | -0.43 | 27.84 | 9.521 | 0 | Diesel-backup
2025-02-12 10:00 | 43 | 2 | Summer | 10 | 18.28 | -4.4 | 3.66 | 32.6 | 466.4 | 27.98 | 0 | 27.98 | 4.4 | 63.51 | 15 | 0 | 35.53 | 11.8 | 0 | Diesel-backup
2025-02-12 11:00 | 43 | 2 | Summer | 11 | 18.28 | -2.1 | 12.79 | 72.4 | 295.5 | 17.73 | 112.22 | 129.95 | 2.1 | 45 | 46.26 | 84.95 | 0 | 0 | 0 | Normal
2025-02-12 12:00 | 43 | 2 | Summer | 12 | 18.28 | -2.4 | 4.79 | 38.8 | 464.9 | 27.89 | 0.3 | 28.19 | 2.4 | 45 | 39.54 | -16.81 | 0 | 0 | 0 | Battery-supported
2025-02-12 13:00 | 43 | 2 | Summer | 13 | 18.28 | -2.1 | 4.76 | 37.1 | 466.3 | 27.98 | 0.28 | 28.26 | 2.1 | 49.59 | 31.01 | -21.33 | 0 | 0 | 0 | Battery-supported
2025-02-12 14:00 | 43 | 2 | Summer | 14 | 18.28 | -1.5 | 2.81 | 75.1 | 269.7 | 16.18 | 0 | 16.18 | 1.5 | 45 | 19.48 | -28.82 | 0 | 0 | 0 | Battery-supported
2025-02-12 15:00 | 43 | 2 | Summer | 15 | 18.28 | -0.6 | 5.47 | 51.8 | 349.1 | 20.95 | 1.07 | 22.02 | 0.6 | 45.08 | 15 | -11.19 | 11.87 | 4.3 | 0 | Diesel-backup
2025-02-12 16:00 | 43 | 2 | Summer | 16 | 18.28 | -6.3 | 7.54 | 85.6 | 181.5 | 10.89 | 9.23 | 20.12 | 6.3 | 51.73 | 15 | 0 | 31.61 | 10.657 | 0 | Diesel-backup
2025-02-12 17:00 | 43 | 2 | Summer | 17 | 18.28 | -2.1 | 4.78 | 62.5 | 227.3 | 13.64 | 0.29 | 13.93 | 2.1 | 45 | 15 | 0 | 31.07 | 10.496 | 0 | Diesel-backup
2025-02-12 18:00 | 43 | 2 | Summer | 18 | 18.28 | -5.9 | 20.54 | 61.7 | 181 | 10.86 | 120 | 130.86 | 5.9 | 50.01 | 44.75 | 80.85 | 0 | 0 | 0 | Normal
2025-02-12 19:00 | 43 | 2 | Summer | 19 | 18.28 | -0.8 | 3.32 | 100 | 58.9 | 3.53 | 0 | 3.53 | 0.8 | 50.64 | 25.91 | -47.11 | 0 | 0 | 0 | Battery-supported
2025-02-12 20:00 | 43 | 2 | Summer | 20 | 18.28 | -0.9 | 3.31 | 76.5 | 54.3 | 3.26 | 0 | 3.26 | 0.9 | 45 | 15 | -27.27 | 14.47 | 5.195 | 0 | Diesel-backup
2025-02-12 21:00 | 43 | 2 | Summer | 21 | 18.28 | 1.4 | 5.33 | 0.9 | 15.5 | 0.93 | 0.86 | 1.79 | 0 | 45 | 15 | 0 | 43.21 | 13.926 | 0 | Diesel-backup
2025-02-12 22:00 | 43 | 2 | Summer | 22 | 18.28 | 1.5 | 19.16 | 52.6 | 0 | 0 | 120 | 120 | 0 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-02-12 23:00 | 43 | 2 | Summer | 23 | 18.28 | -0.9 | 10.29 | 75.2 | 0 | 0 | 43.81 | 43.81 | 0.9 | 45 | 42.12 | -1.19 | 0 | 0 | 0 | Battery-supported
2025-02-13 | 44 | 2 | Summer | 0 | 18.09 | -2.8 | 4.69 | 0 | 0 | 0 | 0.24 | 0.24 | 2.8 | 45 | 24.22 | -44.76 | 0 | 0 | 0 | Battery-supported
2025-02-13 01:00 | 44 | 2 | Summer | 1 | 18.09 | -1 | 4.69 | 12.8 | 0 | 0 | 0.24 | 0.24 | 1 | 45 | 15 | -23.05 | 21.71 | 7.594 | 0 | Diesel-backup
2025-02-13 02:00 | 44 | 2 | Summer | 2 | 18.09 | -3.6 | 3.24 | 31.6 | 0 | 0 | 0 | 0 | 3.6 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-02-13 03:00 | 44 | 2 | Summer | 3 | 18.09 | -2.9 | 5.24 | 16.2 | 4.3 | 0.26 | 0.74 | 1 | 2.9 | 45 | 15 | 0 | 44 | 14.136 | 0 | Diesel-backup
2025-02-13 04:00 | 44 | 2 | Summer | 4 | 18.09 | -1 | 5.95 | 55.4 | 69.1 | 4.15 | 2.06 | 6.21 | 1 | 45 | 15 | 0 | 38.79 | 12.721 | 0 | Diesel-backup
2025-02-13 05:00 | 44 | 2 | Summer | 5 | 18.09 | -4.8 | 10.03 | 74.9 | 100 | 6 | 38.97 | 44.97 | 4.8 | 45 | 15 | 0 | 0.03 | 0.011 | 0 | Diesel-backup
2025-02-13 06:00 | 44 | 2 | Summer | 6 | 18.09 | -2 | 8.83 | 69.5 | 158.3 | 9.5 | 21.19 | 30.69 | 2 | 45 | 15 | 0 | 14.31 | 5.141 | 0 | Diesel-backup
2025-02-13 07:00 | 44 | 2 | Summer | 7 | 18.09 | -2.4 | 5.13 | 55.1 | 248.6 | 14.92 | 0.61 | 15.53 | 2.4 | 45 | 15 | 0 | 29.47 | 10.016 | 0 | Diesel-backup
2025-02-13 08:00 | 44 | 2 | Summer | 8 | 18.09 | -6.1 | 15.24 | 32.6 | 380.7 | 22.84 | 120 | 142.84 | 6.1 | 46.65 | 50.4 | 96.19 | 0 | 0 | 0 | Normal
2025-02-13 09:00 | 44 | 2 | Summer | 9 | 18.09 | -1.8 | 4.27 | 68.5 | 276.8 | 16.61 | 0.06 | 16.67 | 1.8 | 45 | 39.07 | -28.33 | 0 | 0 | 0 | Battery-supported
2025-02-13 10:00 | 44 | 2 | Summer | 10 | 18.09 | -2.2 | 2.34 | 48.7 | 391.6 | 23.5 | 0 | 23.5 | 2.2 | 52.67 | 27.4 | -29.17 | 0 | 0 | 0 | Battery-supported
2025-02-13 11:00 | 44 | 2 | Summer | 11 | 18.09 | -3.3 | 7.77 | 60 | 355.1 | 21.31 | 10.9 | 32.21 | 3.3 | 45.07 | 22.25 | -12.86 | 0 | 0 | 0 | Battery-supported
2025-02-13 12:00 | 44 | 2 | Summer | 12 | 18.09 | -4.9 | 12.27 | 80.1 | 262 | 15.72 | 94.41 | 110.13 | 4.9 | 47.86 | 45.17 | 62.27 | 0 | 0 | 0 | Normal
2025-02-13 13:00 | 44 | 2 | Summer | 13 | 18.09 | -4.7 | 6.58 | 28 | 510.3 | 30.62 | 4.09 | 34.71 | 4.7 | 45 | 41.05 | -10.29 | 0 | 0 | 0 | Battery-supported
2025-02-13 14:00 | 44 | 2 | Summer | 14 | 18.09 | -3.6 | 2.73 | 42 | 422.6 | 25.36 | 0 | 25.36 | 3.6 | 54.78 | 29.29 | -29.42 | 0 | 0 | 0 | Battery-supported
2025-02-13 15:00 | 44 | 2 | Summer | 15 | 18.09 | -0.9 | 7.4 | 35.8 | 416.2 | 24.97 | 8.3 | 33.27 | 0.9 | 45 | 24.59 | -11.73 | 0 | 0 | 0 | Battery-supported
2025-02-13 16:00 | 44 | 2 | Summer | 16 | 18.09 | -3.8 | 7.97 | 52.6 | 305.1 | 18.31 | 12.5 | 30.81 | 3.8 | 45 | 18.92 | -14.19 | 0 | 0 | 0 | Battery-supported
2025-02-13 17:00 | 44 | 2 | Summer | 17 | 18.09 | -0.4 | 8.47 | 72.7 | 192.7 | 11.56 | 17.18 | 28.74 | 0.4 | 45 | 15 | -9.79 | 6.47 | 2.388 | 0 | Diesel-backup
2025-02-13 18:00 | 44 | 2 | Summer | 18 | 18.09 | -3.9 | 7.49 | 31 | 253.8 | 15.23 | 8.89 | 24.12 | 3.9 | 46.06 | 15 | 0 | 21.94 | 7.668 | 0 | Diesel-backup
2025-02-13 19:00 | 44 | 2 | Summer | 19 | 18.09 | -1.5 | 13.21 | 26.1 | 183.3 | 11 | 120 | 131 | 1.5 | 45 | 46.65 | 86 | 0 | 0 | 0 | Normal
2025-02-13 20:00 | 44 | 2 | Summer | 20 | 18.09 | -0.7 | 3.18 | 56.7 | 68 | 4.08 | 0 | 4.08 | 0.7 | 45 | 30.28 | -40.92 | 0 | 0 | 0 | Battery-supported
2025-02-13 21:00 | 44 | 2 | Summer | 21 | 18.09 | 4.4 | 0.48 | 38.8 | 3.5 | 0.21 | 0 | 0.21 | 0 | 45 | 15 | -38.2 | 6.59 | 2.433 | 0 | Diesel-backup
2025-02-13 22:00 | 44 | 2 | Summer | 22 | 18.09 | -4.2 | 1.63 | 50.2 | 0 | 0 | 0 | 0 | 4.2 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-02-13 23:00 | 44 | 2 | Summer | 23 | 18.09 | 1.8 | 2.7 | 39.8 | 0 | 0 | 0 | 0 | 0 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-02-14 | 45 | 2 | Summer | 0 | 17.9 | -1.5 | 11.08 | 55.7 | 0 | 0 | 60.96 | 60.96 | 1.5 | 45 | 20.87 | 15.96 | 0 | 0 | 0 | Normal
2025-02-14 01:00 | 45 | 2 | Summer | 1 | 17.9 | -1.3 | 5.49 | 39.7 | 0 | 0 | 1.1 | 1.1 | 1.3 | 45 | 15 | -14.68 | 29.22 | 9.94 | 0 | Diesel-backup
2025-02-14 02:00 | 45 | 2 | Summer | 2 | 17.9 | -2.3 | 15.97 | 59.4 | 0 | 0 | 120 | 120 | 2.3 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-02-14 03:00 | 45 | 2 | Summer | 3 | 17.9 | -2 | 3.02 | 58.8 | 0 | 0 | 0 | 0 | 2 | 45 | 24.6 | -45 | 0 | 0 | 0 | Battery-supported
2025-02-14 04:00 | 45 | 2 | Summer | 4 | 17.9 | -3.7 | 15.78 | 18 | 94.2 | 5.65 | 120 | 125.65 | 3.7 | 45 | 54.28 | 80.65 | 0 | 0 | 0 | Normal
2025-02-14 05:00 | 45 | 2 | Summer | 5 | 17.9 | -0.4 | 3.7 | 80.2 | 87.8 | 5.27 | 0 | 5.27 | 0.4 | 45 | 38.39 | -39.73 | 0 | 0 | 0 | Battery-supported
2025-02-14 06:00 | 45 | 2 | Summer | 6 | 17.9 | -4.9 | 5.95 | 38.2 | 231.6 | 13.9 | 2.06 | 15.96 | 4.9 | 47.19 | 25.9 | -31.23 | 0 | 0 | 0 | Battery-supported
2025-02-14 07:00 | 45 | 2 | Summer | 7 | 17.9 | -1.5 | 1.9 | 59.1 | 233.5 | 14.01 | 0 | 14.01 | 1.5 | 45 | 15 | -27.24 | 3.75 | 1.399 | 0 | Diesel-backup
2025-02-14 08:00 | 45 | 2 | Summer | 8 | 17.9 | -5.5 | 14.59 | 68.6 | 243.2 | 14.59 | 120 | 134.59 | 5.5 | 48.48 | 46.69 | 86.11 | 0 | 0 | 0 | Normal
2025-02-14 09:00 | 45 | 2 | Summer | 9 | 17.9 | -4.1 | 6.47 | 44.3 | 378.8 | 22.73 | 3.67 | 26.4 | 4.1 | 45 | 39.25 | -18.6 | 0 | 0 | 0 | Battery-supported
2025-02-14 10:00 | 45 | 2 | Summer | 10 | 17.9 | -6.2 | 21.15 | 78.3 | 254.3 | 15.26 | 120 | 135.26 | 6.2 | 45 | 72.46 | 90.26 | 0 | 0 | 0 | Normal
2025-02-14 11:00 | 45 | 2 | Summer | 11 | 17.9 | -2.6 | 12.63 | 34.9 | 476.9 | 28.61 | 106.52 | 135.13 | 2.6 | 48.08 | 95 | 61.24 | 0 | 0 | 0 | Normal
2025-02-14 12:00 | 45 | 2 | Summer | 12 | 17.9 | -0.1 | 5.86 | 52.9 | 395.9 | 23.75 | 1.84 | 25.59 | 0.1 | 45 | 87.24 | -19.41 | 0 | 0 | 0 | Battery-supported
2025-02-14 13:00 | 45 | 2 | Summer | 13 | 17.9 | -3.1 | 4.12 | 25.5 | 522.5 | 31.35 | 0.03 | 31.38 | 3.1 | 46.14 | 81.33 | -14.76 | 0 | 0 | 0 | Battery-supported
2025-02-14 14:00 | 45 | 2 | Summer | 14 | 17.9 | -3 | 11.37 | 0.6 | 613.1 | 36.79 | 68.22 | 105.01 | 3 | 45 | 95 | 37.14 | 0 | 0 | 0 | Normal
2025-02-14 15:00 | 45 | 2 | Summer | 15 | 17.9 | -4.6 | 6.9 | 5.2 | 544.8 | 32.69 | 5.5 | 38.19 | 4.6 | 45 | 92.28 | -6.81 | 0 | 0 | 0 | Battery-supported
2025-02-14 16:00 | 45 | 2 | Summer | 16 | 17.9 | -2.3 | 3.97 | 48.4 | 318.9 | 19.13 | 0.01 | 19.14 | 2.3 | 48.01 | 80.73 | -28.87 | 0 | 0 | 0 | Battery-supported
2025-02-14 17:00 | 45 | 2 | Summer | 17 | 17.9 | -5 | 7.21 | 45.9 | 274.8 | 16.49 | 7.15 | 23.64 | 5 | 54.82 | 68.26 | -31.18 | 0 | 0 | 0 | Battery-supported
2025-02-14 18:00 | 45 | 2 | Summer | 18 | 17.9 | -3.3 | 1.42 | 13.7 | 291.4 | 17.48 | 0 | 17.48 | 3.3 | 45 | 57.25 | -27.52 | 0 | 0 | 0 | Battery-supported
2025-02-14 19:00 | 45 | 2 | Summer | 19 | 17.9 | -0.6 | 8.59 | 68.6 | 106.9 | 6.41 | 18.46 | 24.87 | 0.6 | 45 | 49.2 | -20.13 | 0 | 0 | 0 | Battery-supported
2025-02-14 20:00 | 45 | 2 | Summer | 20 | 17.9 | 1.8 | 9.59 | 75.9 | 46.9 | 2.81 | 31.61 | 34.42 | 0 | 45 | 44.96 | -10.58 | 0 | 0 | 0 | Battery-supported
2025-02-14 21:00 | 45 | 2 | Summer | 21 | 17.9 | 5.1 | 2.95 | 82.3 | 0 | 0 | 0 | 0 | 0 | 45 | 26.96 | -45 | 0 | 0 | 0 | Battery-supported
2025-02-14 22:00 | 45 | 2 | Summer | 22 | 17.9 | -2.6 | 13.45 | 14.7 | 0 | 0 | 120 | 120 | 2.6 | 45 | 54.56 | 75 | 0 | 0 | 0 | Normal
2025-02-14 23:00 | 45 | 2 | Summer | 23 | 17.9 | 1.7 | 11.83 | 19.4 | 0 | 0 | 80.9 | 80.9 | 0 | 45 | 67.78 | 35.9 | 0 | 0 | 0 | Normal
2025-02-15 | 46 | 2 | Summer | 0 | 17.72 | -1.4 | 8.14 | 39.9 | 0 | 0 | 13.98 | 13.98 | 1.4 | 45 | 55.37 | -31.02 | 0 | 0 | 0 | Battery-supported
2025-02-15 01:00 | 46 | 2 | Summer | 1 | 17.72 | -2.6 | 3.52 | 59.3 | 0 | 0 | 0 | 0 | 2.6 | 45 | 37.37 | -45 | 0 | 0 | 0 | Battery-supported
2025-02-15 02:00 | 46 | 2 | Summer | 2 | 17.72 | -1.7 | 9.95 | 65.1 | 0 | 0 | 37.56 | 37.56 | 1.7 | 45 | 34.39 | -7.44 | 0 | 0 | 0 | Battery-supported
2025-02-15 03:00 | 46 | 2 | Summer | 3 | 17.72 | -2.9 | 5.31 | 40.8 | 0 | 0 | 0.83 | 0.83 | 2.9 | 45 | 16.72 | -44.17 | 0 | 0 | 0 | Battery-supported
2025-02-15 04:00 | 46 | 2 | Summer | 4 | 17.72 | -3.2 | 7.63 | 49.2 | 62.8 | 3.77 | 9.86 | 13.63 | 3.2 | 45 | 15 | -4.31 | 27.06 | 9.281 | 0 | Diesel-backup
2025-02-15 05:00 | 46 | 2 | Summer | 5 | 17.72 | -4.6 | 10.51 | 37 | 153.4 | 9.2 | 48.21 | 57.41 | 4.6 | 45 | 19.57 | 12.41 | 0 | 0 | 0 | Normal
2025-02-15 06:00 | 46 | 2 | Summer | 6 | 17.72 | -7 | 2.38 | 67.1 | 158.3 | 9.5 | 0 | 9.5 | 7 | 45 | 15 | -11.42 | 24.08 | 8.351 | 0 | Diesel-backup
2025-02-15 07:00 | 46 | 2 | Summer | 7 | 17.72 | -7.5 | 1.84 | 58.1 | 234 | 14.04 | 0 | 14.04 | 7.5 | 47.98 | 15 | 0 | 33.94 | 11.341 | 0 | Diesel-backup
2025-02-15 08:00 | 46 | 2 | Summer | 8 | 17.72 | -2.7 | 4.97 | 60.1 | 273.5 | 16.41 | 0.44 | 16.85 | 2.7 | 45 | 15 | 0 | 28.15 | 9.615 | 0 | Diesel-backup
2025-02-15 09:00 | 46 | 2 | Summer | 9 | 17.72 | -4.7 | 19.16 | 56.6 | 325.2 | 19.51 | 120 | 139.51 | 4.7 | 46.73 | 49.14 | 92.78 | 0 | 0 | 0 | Normal
2025-02-15 10:00 | 46 | 2 | Summer | 10 | 17.72 | -5.3 | 21.7 | 24.7 | 501.3 | 30.08 | 120 | 150.08 | 5.3 | 50.93 | 85.63 | 99.15 | 0 | 0 | 0 | Normal
2025-02-15 11:00 | 46 | 2 | Summer | 11 | 17.72 | -3.7 | 8.49 | 76.7 | 274.3 | 16.46 | 17.39 | 33.85 | 3.7 | 52.7 | 78.09 | -18.85 | 0 | 0 | 0 | Battery-supported
2025-02-15 12:00 | 46 | 2 | Summer | 12 | 17.72 | -1.7 | 12.05 | 56.3 | 378.8 | 22.73 | 87.48 | 110.21 | 1.7 | 45 | 95 | 45.95 | 0 | 0 | 0 | Normal
2025-02-15 13:00 | 46 | 2 | Summer | 13 | 17.72 | -2.7 | 6.66 | 82.7 | 245.4 | 14.72 | 4.42 | 19.14 | 2.7 | 46.68 | 83.98 | -27.54 | 0 | 0 | 0 | Battery-supported
2025-02-15 14:00 | 46 | 2 | Summer | 14 | 17.72 | -4.1 | 7.23 | 73.3 | 277 | 16.62 | 7.26 | 23.88 | 4.1 | 46.97 | 74.75 | -23.09 | 0 | 0 | 0 | Battery-supported
2025-02-15 15:00 | 46 | 2 | Summer | 15 | 17.72 | 0.4 | 5.96 | 0.2 | 564.4 | 33.86 | 2.08 | 35.94 | 0 | 45 | 71.12 | -9.06 | 0 | 0 | 0 | Battery-supported
2025-02-15 16:00 | 46 | 2 | Summer | 16 | 17.72 | 1.6 | 12.91 | 80.9 | 195.8 | 11.75 | 116.62 | 128.37 | 0 | 45 | 95 | 64.88 | 0 | 0 | 0 | Normal
2025-02-15 17:00 | 46 | 2 | Summer | 17 | 17.72 | -0.5 | 16.1 | 85.7 | 148.1 | 8.89 | 120 | 128.89 | 0.5 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-02-15 18:00 | 46 | 2 | Summer | 18 | 17.72 | 0.8 | 7.13 | 69.2 | 153.3 | 9.2 | 6.69 | 15.89 | 0 | 45 | 83.36 | -29.11 | 0 | 0 | 0 | Battery-supported
2025-02-15 19:00 | 46 | 2 | Summer | 19 | 17.72 | 1.5 | 7.21 | 52.8 | 128.2 | 7.69 | 7.15 | 14.84 | 0 | 45 | 71.29 | -30.16 | 0 | 0 | 0 | Battery-supported
2025-02-15 20:00 | 46 | 2 | Summer | 20 | 17.72 | 1.3 | 6.16 | 73.7 | 44.5 | 2.67 | 2.63 | 5.3 | 0 | 45 | 55.41 | -39.7 | 0 | 0 | 0 | Battery-supported
2025-02-15 21:00 | 46 | 2 | Summer | 21 | 17.72 | 0.1 | 16.34 | 63.3 | 0 | 0 | 120 | 120 | 0 | 45 | 83.01 | 75 | 0 | 0 | 0 | Normal
2025-02-15 22:00 | 46 | 2 | Summer | 22 | 17.72 | -0.1 | 11.18 | 27 | 0 | 0 | 63.4 | 63.4 | 0.1 | 45 | 89.78 | 18.4 | 0 | 0 | 0 | Normal
2025-02-15 23:00 | 46 | 2 | Summer | 23 | 17.72 | -0.5 | 3.46 | 96.1 | 0 | 0 | 0 | 0 | 0.5 | 45 | 71.78 | -45 | 0 | 0 | 0 | Battery-supported
2025-02-16 | 47 | 2 | Summer | 0 | 17.54 | -4.4 | 18.87 | 82.9 | 0 | 0 | 120 | 120 | 4.4 | 45 | 95 | 63.09 | 0 | 0 | 0 | Normal
2025-02-16 01:00 | 47 | 2 | Summer | 1 | 17.54 | -0.8 | 0.97 | 36.9 | 0 | 0 | 0 | 0 | 0.8 | 45 | 77 | -45 | 0 | 0 | 0 | Battery-supported
2025-02-16 02:00 | 47 | 2 | Summer | 2 | 17.54 | -5.8 | 15.45 | 66.3 | 0 | 0 | 120 | 120 | 5.8 | 45 | 95 | 48.91 | 0 | 0 | 0 | Normal
2025-02-16 03:00 | 47 | 2 | Summer | 3 | 17.54 | -4.9 | 12.34 | 8.1 | 0 | 0 | 96.69 | 96.69 | 4.9 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-02-16 04:00 | 47 | 2 | Summer | 4 | 17.54 | -0.7 | 7.16 | 40.2 | 62.8 | 3.77 | 6.86 | 10.63 | 0.7 | 45 | 81.25 | -34.37 | 0 | 0 | 0 | Battery-supported
2025-02-16 05:00 | 47 | 2 | Summer | 5 | 17.54 | -2 | 7.05 | 36.1 | 149 | 8.94 | 6.26 | 15.2 | 2 | 45 | 69.33 | -29.8 | 0 | 0 | 0 | Battery-supported
2025-02-16 06:00 | 47 | 2 | Summer | 6 | 17.54 | -0.8 | 6.37 | 61.6 | 168 | 10.08 | 3.31 | 13.39 | 0.8 | 45 | 56.69 | -31.61 | 0 | 0 | 0 | Battery-supported
2025-02-16 07:00 | 47 | 2 | Summer | 7 | 17.54 | -4.8 | 3.59 | 45.2 | 270.8 | 16.25 | 0 | 16.25 | 4.8 | 45 | 45.19 | -28.75 | 0 | 0 | 0 | Battery-supported
2025-02-16 08:00 | 47 | 2 | Summer | 8 | 17.54 | -6.8 | 18.02 | 57.6 | 280.9 | 16.85 | 120 | 136.85 | 6.8 | 52.8 | 76.12 | 84.05 | 0 | 0 | 0 | Normal
2025-02-16 09:00 | 47 | 2 | Summer | 9 | 17.54 | -4.8 | 6.92 | 64 | 293 | 17.58 | 5.6 | 23.18 | 4.8 | 45 | 67.39 | -21.82 | 0 | 0 | 0 | Battery-supported
2025-02-16 10:00 | 47 | 2 | Summer | 10 | 17.54 | -3.8 | 3.55 | 93.1 | 185.5 | 11.13 | 0 | 11.13 | 3.8 | 49.88 | 51.89 | -38.75 | 0 | 0 | 0 | Battery-supported
2025-02-16 11:00 | 47 | 2 | Summer | 11 | 17.54 | -3.7 | 17.4 | 42.6 | 439.2 | 26.35 | 120 | 146.35 | 3.7 | 50.14 | 87.3 | 96.21 | 0 | 0 | 0 | Normal
2025-02-16 12:00 | 47 | 2 | Summer | 12 | 17.54 | -1 | 9.09 | 38.4 | 467.2 | 28.03 | 24.45 | 52.48 | 1 | 45 | 90.05 | 7.48 | 0 | 0 | 0 | Normal
2025-02-16 13:00 | 47 | 2 | Summer | 13 | 17.54 | -4 | 9.42 | 61.3 | 348.8 | 20.93 | 29.04 | 49.97 | 4 | 47.17 | 91.08 | 2.8 | 0 | 0 | 0 | Normal
2025-02-16 14:00 | 47 | 2 | Summer | 14 | 17.54 | -2 | 19.66 | 66.2 | 309.1 | 18.55 | 120 | 138.55 | 2 | 45 | 95 | 10.66 | 0 | 0 | 0 | Normal
2025-02-16 15:00 | 47 | 2 | Summer | 15 | 17.54 | -4.6 | 10.2 | 51.4 | 346.4 | 20.78 | 42.1 | 62.88 | 4.6 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-02-16 16:00 | 47 | 2 | Summer | 16 | 17.54 | -1 | 4.58 | 51.4 | 303.8 | 18.23 | 0.18 | 18.41 | 1 | 45 | 84.36 | -26.59 | 0 | 0 | 0 | Battery-supported
2025-02-16 17:00 | 47 | 2 | Summer | 17 | 17.54 | -1.7 | 10.19 | 65.9 | 207.2 | 12.43 | 41.91 | 54.34 | 1.7 | 45 | 87.8 | 9.34 | 0 | 0 | 0 | Normal
2025-02-16 18:00 | 47 | 2 | Summer | 18 | 17.54 | -3.1 | 3.82 | 13 | 281.6 | 16.9 | 0 | 16.9 | 3.1 | 45 | 76.56 | -28.1 | 0 | 0 | 0 | Battery-supported
2025-02-16 19:00 | 47 | 2 | Summer | 19 | 17.54 | -1.8 | 5.17 | 44.6 | 136 | 8.16 | 0.65 | 8.81 | 1.8 | 47.1 | 61.25 | -38.29 | 0 | 0 | 0 | Battery-supported
2025-02-16 20:00 | 47 | 2 | Summer | 20 | 17.54 | -1.7 | 8.35 | 16 | 79.2 | 4.75 | 15.97 | 20.72 | 1.7 | 45 | 51.53 | -24.28 | 0 | 0 | 0 | Battery-supported
2025-02-16 21:00 | 47 | 2 | Summer | 21 | 17.54 | -1.9 | 11.97 | 67.6 | 0 | 0 | 85.05 | 85.05 | 1.9 | 45 | 66.27 | 40.05 | 0 | 0 | 0 | Normal
2025-02-16 22:00 | 47 | 2 | Summer | 22 | 17.54 | 2.4 | 4.76 | 40.7 | 0 | 0 | 0.28 | 0.28 | 0 | 45 | 48.38 | -44.72 | 0 | 0 | 0 | Battery-supported
2025-02-16 23:00 | 47 | 2 | Summer | 23 | 17.54 | -1.9 | 6.25 | 34.4 | 0 | 0 | 2.91 | 2.91 | 1.9 | 45 | 31.55 | -42.09 | 0 | 0 | 0 | Battery-supported
2025-02-17 | 48 | 2 | Summer | 0 | 17.36 | -2.7 | 6.23 | 49.1 | 0 | 0 | 2.85 | 2.85 | 2.7 | 45 | 15 | -41.37 | 0.78 | 0.294 | 0 | Diesel-backup
2025-02-17 01:00 | 48 | 2 | Summer | 1 | 17.36 | -7.1 | 13.22 | 28.3 | 0 | 0 | 120 | 120 | 7.1 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-02-17 02:00 | 48 | 2 | Summer | 2 | 17.36 | -4.9 | 7.06 | 31.9 | 0 | 0 | 6.31 | 6.31 | 4.9 | 45 | 27.12 | -38.69 | 0 | 0 | 0 | Battery-supported
2025-02-17 03:00 | 48 | 2 | Summer | 3 | 17.36 | -3.9 | 18.77 | 10.7 | 0 | 0 | 120 | 120 | 3.9 | 45 | 54.72 | 75 | 0 | 0 | 0 | Normal
2025-02-17 04:00 | 48 | 2 | Summer | 4 | 17.36 | -5.1 | 5.18 | 47.1 | 51.9 | 3.11 | 0.66 | 3.77 | 5.1 | 45 | 38.23 | -41.23 | 0 | 0 | 0 | Battery-supported
2025-02-17 05:00 | 48 | 2 | Summer | 5 | 17.36 | -0.9 | 4.91 | 87.5 | 67.5 | 4.05 | 0.39 | 4.44 | 0.9 | 45 | 22.01 | -40.56 | 0 | 0 | 0 | Battery-supported
2025-02-17 06:00 | 48 | 2 | Summer | 6 | 17.36 | -4.5 | 15.32 | 98.8 | 79.2 | 4.75 | 120 | 124.75 | 4.5 | 45 | 51.36 | 79.75 | 0 | 0 | 0 | Normal
2025-02-17 07:00 | 48 | 2 | Summer | 7 | 17.36 | -1.5 | 9.73 | 37.4 | 291.4 | 17.48 | 33.84 | 51.32 | 1.5 | 45 | 53.68 | 6.32 | 0 | 0 | 0 | Normal
2025-02-17 08:00 | 48 | 2 | Summer | 8 | 17.36 | -4.2 | 25.06 | 73.2 | 221.6 | 13.3 | 120 | 133.3 | 4.2 | 49.85 | 84.39 | 83.45 | 0 | 0 | 0 | Normal
2025-02-17 09:00 | 48 | 2 | Summer | 9 | 17.36 | -4.3 | 14.99 | 21.2 | 472.4 | 28.34 | 120 | 148.34 | 4.3 | 48.02 | 95 | 28.83 | 0 | 0 | 0 | Normal
2025-02-17 10:00 | 48 | 2 | Summer | 10 | 17.36 | -4.4 | 2.89 | 23.4 | 505.7 | 30.34 | 0 | 30.34 | 4.4 | 45 | 89.14 | -14.66 | 0 | 0 | 0 | Battery-supported
2025-02-17 11:00 | 48 | 2 | Summer | 11 | 17.36 | -3.9 | 6.96 | 52.9 | 389.4 | 23.36 | 5.8 | 29.16 | 3.9 | 51.29 | 80.28 | -22.13 | 0 | 0 | 0 | Battery-supported
2025-02-17 12:00 | 48 | 2 | Summer | 12 | 17.36 | 0.1 | 8.36 | 86.6 | 230.1 | 13.81 | 16.07 | 29.88 | 0 | 47.26 | 73.33 | -17.38 | 0 | 0 | 0 | Battery-supported
2025-02-17 13:00 | 48 | 2 | Summer | 13 | 17.36 | -8.4 | 8.01 | 25.1 | 523.6 | 31.42 | 12.84 | 44.26 | 8.4 | 51.45 | 70.46 | -7.19 | 0 | 0 | 0 | Battery-supported
2025-02-17 14:00 | 48 | 2 | Summer | 14 | 17.36 | -7.3 | 6.33 | 44.4 | 409.1 | 24.55 | 3.17 | 27.72 | 7.3 | 48.07 | 62.32 | -20.35 | 0 | 0 | 0 | Battery-supported
2025-02-17 15:00 | 48 | 2 | Summer | 15 | 17.36 | -3.7 | 7.91 | 38.4 | 400 | 24 | 12 | 36 | 3.7 | 45 | 58.72 | -9 | 0 | 0 | 0 | Battery-supported
2025-02-17 16:00 | 48 | 2 | Summer | 16 | 17.36 | -2.1 | 8.17 | 61.4 | 265.2 | 15.91 | 14.25 | 30.16 | 2.1 | 51.79 | 50.06 | -21.63 | 0 | 0 | 0 | Battery-supported
2025-02-17 17:00 | 48 | 2 | Summer | 17 | 17.36 | -0.3 | 4.82 | 75.3 | 176.4 | 10.58 | 0.32 | 10.9 | 0.3 | 45 | 36.42 | -34.1 | 0 | 0 | 0 | Battery-supported
2025-02-17 18:00 | 48 | 2 | Summer | 18 | 17.36 | -0.5 | 12.91 | 55.2 | 179.1 | 10.75 | 116.62 | 127.37 | 0.5 | 45 | 66.74 | 82.37 | 0 | 0 | 0 | Normal
2025-02-17 19:00 | 48 | 2 | Summer | 19 | 17.36 | -2.3 | 17.56 | 64.8 | 100.8 | 6.05 | 120 | 126.05 | 2.3 | 46.99 | 95 | 76.8 | 0 | 0 | 0 | Normal
2025-02-17 20:00 | 48 | 2 | Summer | 20 | 17.36 | 0.9 | 10.72 | 43.9 | 53.9 | 3.23 | 52.68 | 55.91 | 0 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-02-17 21:00 | 48 | 2 | Summer | 21 | 17.36 | 0.8 | 8.94 | 65.6 | 0 | 0 | 22.53 | 22.53 | 0 | 45 | 86.01 | -22.47 | 0 | 0 | 0 | Battery-supported
2025-02-17 22:00 | 48 | 2 | Summer | 22 | 17.36 | -1.2 | 6.68 | 88.9 | 0 | 0 | 4.5 | 4.5 | 1.2 | 45.01 | 69.81 | -40.51 | 0 | 0 | 0 | Battery-supported
2025-02-17 23:00 | 48 | 2 | Summer | 23 | 17.36 | 0.3 | 8.32 | 9 | 0 | 0 | 15.67 | 15.67 | 0 | 45 | 58.08 | -29.33 | 0 | 0 | 0 | Battery-supported
2025-02-18 | 49 | 2 | Summer | 0 | 17.18 | -1.6 | 8.85 | 5.3 | 0 | 0 | 21.43 | 21.43 | 1.6 | 45 | 48.65 | -23.57 | 0 | 0 | 0 | Battery-supported
2025-02-18 01:00 | 49 | 2 | Summer | 1 | 17.18 | -3.8 | 3.62 | 19.8 | 0 | 0 | 0 | 0 | 3.8 | 45 | 30.65 | -45 | 0 | 0 | 0 | Battery-supported
2025-02-18 02:00 | 49 | 2 | Summer | 2 | 17.18 | -1.5 | 12.57 | 77.7 | 0 | 0 | 104.43 | 104.43 | 1.5 | 45 | 52.52 | 59.43 | 0 | 0 | 0 | Normal
2025-02-18 03:00 | 49 | 2 | Summer | 3 | 17.18 | -3.1 | 5.42 | 92.3 | 0 | 0 | 0.99 | 0.99 | 3.1 | 45 | 34.91 | -44.01 | 0 | 0 | 0 | Battery-supported
2025-02-18 04:00 | 49 | 2 | Summer | 4 | 17.18 | -3.7 | 15.83 | 48.9 | 44.7 | 2.68 | 120 | 122.68 | 3.7 | 45 | 63.5 | 77.68 | 0 | 0 | 0 | Normal
2025-02-18 05:00 | 49 | 2 | Summer | 5 | 17.18 | -0.8 | 0.35 | 4 | 182.4 | 10.94 | 0 | 10.94 | 0.8 | 45 | 49.88 | -34.06 | 0 | 0 | 0 | Battery-supported
2025-02-18 06:00 | 49 | 2 | Summer | 6 | 17.18 | -9.7 | 7.77 | 45.4 | 197.4 | 11.84 | 10.9 | 22.74 | 9.7 | 46.13 | 40.52 | -23.39 | 0 | 0 | 0 | Battery-supported
2025-02-18 07:00 | 49 | 2 | Summer | 7 | 17.18 | -7.6 | 12.7 | 62.1 | 213.9 | 12.83 | 108.99 | 121.82 | 7.6 | 45 | 68.79 | 76.82 | 0 | 0 | 0 | Normal
2025-02-18 08:00 | 49 | 2 | Summer | 8 | 17.18 | -7.1 | 10.66 | 41.3 | 337.1 | 20.23 | 51.37 | 71.6 | 7.1 | 46.81 | 77.91 | 24.79 | 0 | 0 | 0 | Normal
2025-02-18 09:00 | 49 | 2 | Summer | 9 | 17.18 | -5.2 | 2.93 | 71.3 | 260.4 | 15.62 | 0 | 15.62 | 5.2 | 52.09 | 63.32 | -36.47 | 0 | 0 | 0 | Battery-supported
2025-02-18 10:00 | 49 | 2 | Summer | 10 | 17.18 | -4.9 | 15.02 | 27 | 488.6 | 29.32 | 120 | 149.32 | 4.9 | 48.47 | 95 | 86.07 | 0 | 0 | 0 | Normal
2025-02-18 11:00 | 49 | 2 | Summer | 11 | 17.18 | -7.4 | 4.3 | 36.9 | 466.3 | 27.98 | 0.07 | 28.05 | 7.4 | 54.68 | 84.35 | -26.63 | 0 | 0 | 0 | Battery-supported
2025-02-18 12:00 | 49 | 2 | Summer | 12 | 17.18 | -5.9 | 5.19 | 80.9 | 257.7 | 15.46 | 0.68 | 16.14 | 5.9 | 50.05 | 70.78 | -33.91 | 0 | 0 | 0 | Battery-supported
2025-02-18 13:00 | 49 | 2 | Summer | 13 | 17.18 | -5.3 | 5.49 | 42.8 | 437.8 | 26.27 | 1.1 | 27.37 | 5.3 | 47.25 | 62.83 | -19.88 | 0 | 0 | 0 | Battery-supported
2025-02-18 14:00 | 49 | 2 | Summer | 14 | 17.18 | 2.4 | 2.18 | 59.2 | 340.4 | 20.42 | 0 | 20.42 | 0 | 45 | 53 | -24.58 | 0 | 0 | 0 | Battery-supported
2025-02-18 15:00 | 49 | 2 | Summer | 15 | 17.18 | 1.4 | 7.99 | 12.4 | 507.7 | 30.46 | 12.67 | 43.13 | 0 | 45 | 52.25 | -1.87 | 0 | 0 | 0 | Battery-supported
2025-02-18 16:00 | 49 | 2 | Summer | 16 | 17.18 | -3.2 | 13.16 | 47.3 | 314.9 | 18.89 | 120 | 138.89 | 3.2 | 51.25 | 84.5 | 87.64 | 0 | 0 | 0 | Normal
2025-02-18 17:00 | 49 | 2 | Summer | 17 | 17.18 | -2.7 | 15.61 | 29 | 313.4 | 18.8 | 120 | 138.8 | 2.7 | 46.2 | 95 | 28.52 | 0 | 0 | 0 | Normal
2025-02-18 18:00 | 49 | 2 | Summer | 18 | 17.18 | -4.2 | 6.35 | 80.4 | 118.7 | 7.12 | 3.24 | 10.36 | 4.2 | 48.04 | 79.93 | -37.68 | 0 | 0 | 0 | Battery-supported
2025-02-18 19:00 | 49 | 2 | Summer | 19 | 17.18 | -5.7 | 7.04 | 36 | 137.3 | 8.24 | 6.21 | 14.45 | 5.7 | 50.96 | 65.32 | -36.51 | 0 | 0 | 0 | Battery-supported
2025-02-18 20:00 | 49 | 2 | Summer | 20 | 17.18 | -1.8 | 11.09 | 38.2 | 50.4 | 3.02 | 61.2 | 64.22 | 1.8 | 45 | 72.4 | 19.22 | 0 | 0 | 0 | Normal
2025-02-18 21:00 | 49 | 2 | Summer | 21 | 17.18 | -3.7 | 6.46 | 58.3 | 0 | 0 | 3.63 | 3.63 | 3.7 | 45 | 55.85 | -41.37 | 0 | 0 | 0 | Battery-supported
2025-02-18 22:00 | 49 | 2 | Summer | 22 | 17.18 | -1.9 | 13.84 | 10 | 0 | 0 | 120 | 120 | 1.9 | 45 | 83.45 | 75 | 0 | 0 | 0 | Normal
2025-02-18 23:00 | 49 | 2 | Summer | 23 | 17.18 | -5.5 | 6.83 | 38.6 | 0 | 0 | 5.17 | 5.17 | 5.5 | 45 | 67.52 | -39.83 | 0 | 0 | 0 | Battery-supported
2025-02-19 | 50 | 2 | Summer | 0 | 17 | -4 | 3.92 | 22.6 | 0 | 0 | 0.01 | 0.01 | 4 | 45 | 49.52 | -44.99 | 0 | 0 | 0 | Battery-supported
2025-02-19 01:00 | 50 | 2 | Summer | 1 | 17 | -2.4 | 8.14 | 51.6 | 0 | 0 | 13.98 | 13.98 | 2.4 | 45 | 37.11 | -31.02 | 0 | 0 | 0 | Battery-supported
2025-02-19 02:00 | 50 | 2 | Summer | 2 | 17 | -2.3 | 2.51 | 49.4 | 0 | 0 | 0 | 0 | 2.3 | 46.95 | 18.33 | -46.95 | 0 | 0 | 0 | Battery-supported
2025-02-19 03:00 | 50 | 2 | Summer | 3 | 17 | -2.6 | 8.07 | 66.5 | 0 | 0 | 13.36 | 13.36 | 2.6 | 45 | 15 | -8.33 | 23.31 | 8.106 | 0 | Diesel-backup
2025-02-19 04:00 | 50 | 2 | Summer | 4 | 17 | -6.8 | 9 | 63.2 | 32 | 1.92 | 23.29 | 25.21 | 6.8 | 45 | 15 | 0 | 19.79 | 6.971 | 0 | Diesel-backup
2025-02-19 05:00 | 50 | 2 | Summer | 5 | 17 | -2.3 | 4.32 | 76.2 | 76.9 | 4.61 | 0.08 | 4.69 | 2.3 | 45 | 15 | 0 | 40.31 | 13.141 | 0 | Diesel-backup
2025-02-19 06:00 | 50 | 2 | Summer | 6 | 17 | -6.2 | 8.79 | 75.8 | 126.2 | 7.57 | 20.72 | 28.29 | 6.2 | 45.27 | 15 | 0 | 16.98 | 6.043 | 0 | Diesel-backup
2025-02-19 07:00 | 50 | 2 | Summer | 7 | 17 | -3.2 | 5.99 | 62.6 | 209.8 | 12.59 | 2.16 | 14.75 | 3.2 | 45 | 15 | 0 | 30.25 | 10.251 | 0 | Diesel-backup
2025-02-19 08:00 | 50 | 2 | Summer | 8 | 17 | -4.6 | 4.2 | 49.7 | 304 | 18.24 | 0.05 | 18.29 | 4.6 | 49.46 | 15 | 0 | 31.17 | 10.526 | 0 | Diesel-backup
2025-02-19 09:00 | 50 | 2 | Summer | 9 | 17 | -7.6 | 2.26 | 79.4 | 225.6 | 13.54 | 0 | 13.54 | 7.6 | 47.65 | 15 | 0 | 34.11 | 11.391 | 0 | Diesel-backup
2025-02-19 10:00 | 50 | 2 | Summer | 10 | 17 | -5.1 | 2.73 | 56 | 354.8 | 21.29 | 0 | 21.29 | 5.1 | 46.42 | 15 | 0 | 25.13 | 8.681 | 0 | Diesel-backup
2025-02-19 11:00 | 50 | 2 | Summer | 11 | 17 | -3.4 | 16.79 | 66.4 | 323.6 | 19.42 | 120 | 139.42 | 3.4 | 45 | 49.75 | 94.42 | 0 | 0 | 0 | Normal
2025-02-19 12:00 | 50 | 2 | Summer | 12 | 17 | -2.5 | 5.84 | 13.2 | 591.2 | 35.47 | 1.79 | 37.26 | 2.5 | 45 | 46.65 | -7.74 | 0 | 0 | 0 | Battery-supported
2025-02-19 13:00 | 50 | 2 | Summer | 13 | 17 | -3.8 | 8.87 | 35 | 475.7 | 28.54 | 21.67 | 50.21 | 3.8 | 45.97 | 48.21 | 4.24 | 0 | 0 | 0 | Normal
2025-02-19 14:00 | 50 | 2 | Summer | 14 | 17 | 0.3 | 6.33 | 52.7 | 369.9 | 22.19 | 3.17 | 25.36 | 0 | 46.68 | 39.68 | -21.32 | 0 | 0 | 0 | Battery-supported
2025-02-19 15:00 | 50 | 2 | Summer | 15 | 17 | -0.5 | 17.03 | 47.3 | 359.8 | 21.59 | 120 | 141.59 | 0.5 | 55.02 | 71.54 | 86.57 | 0 | 0 | 0 | Normal
2025-02-19 16:00 | 50 | 2 | Summer | 16 | 17 | -2.9 | 4.22 | 46.8 | 314.7 | 18.88 | 0.05 | 18.93 | 2.9 | 46.49 | 60.52 | -27.56 | 0 | 0 | 0 | Battery-supported
2025-02-19 17:00 | 50 | 2 | Summer | 17 | 17 | -0.4 | 7.43 | 54.6 | 233.5 | 14.01 | 8.5 | 22.51 | 0.4 | 45.56 | 51.3 | -23.05 | 0 | 0 | 0 | Battery-supported
2025-02-19 18:00 | 50 | 2 | Summer | 18 | 17 | 2.4 | 5.18 | 52 | 178.5 | 10.71 | 0.66 | 11.37 | 0 | 45 | 37.84 | -33.63 | 0 | 0 | 0 | Battery-supported
2025-02-19 19:00 | 50 | 2 | Summer | 19 | 17 | 2.6 | 12.65 | 0 | 179.7 | 10.78 | 107.22 | 118 | 0 | 45 | 64.71 | 73 | 0 | 0 | 0 | Normal
2025-02-19 20:00 | 50 | 2 | Summer | 20 | 17 | -4.3 | 8.82 | 47.3 | 39.2 | 2.35 | 21.07 | 23.42 | 4.3 | 53.43 | 52.7 | -30.01 | 0 | 0 | 0 | Battery-supported
2025-02-19 21:00 | 50 | 2 | Summer | 21 | 17 | -3.7 | 7.26 | 36.6 | 0 | 0 | 7.44 | 7.44 | 3.7 | 45 | 37.68 | -37.56 | 0 | 0 | 0 | Battery-supported
2025-02-19 22:00 | 50 | 2 | Summer | 22 | 17 | 1.5 | 3 | 68.9 | 0 | 0 | 0 | 0 | 0 | 45 | 19.68 | -45 | 0 | 0 | 0 | Battery-supported
2025-02-19 23:00 | 50 | 2 | Summer | 23 | 17 | -4.4 | 21.34 | 63.9 | 0 | 0 | 120 | 120 | 4.4 | 51 | 45.07 | 69 | 0 | 0 | 0 | Normal
2025-02-20 | 51 | 2 | Summer | 0 | 16.83 | -5.4 | 6.46 | 54.5 | 0 | 0 | 3.63 | 3.63 | 5.4 | 45.16 | 28.46 | -41.53 | 0 | 0 | 0 | Battery-supported
2025-02-20 01:00 | 51 | 2 | Summer | 1 | 16.83 | -3.9 | 3.76 | 11.2 | 0 | 0 | 0 | 0 | 3.9 | 45 | 15 | -33.65 | 11.35 | 4.12 | 0 | Diesel-backup
2025-02-20 02:00 | 51 | 2 | Summer | 2 | 16.83 | -2.3 | 2.27 | 75.7 | 0 | 0 | 0 | 0 | 2.3 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-02-20 03:00 | 51 | 2 | Summer | 3 | 16.83 | -3.8 | 2.67 | 24.2 | 0 | 0 | 0 | 0 | 3.8 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-02-20 04:00 | 51 | 2 | Summer | 4 | 16.83 | -5.4 | 7.24 | 48.5 | 32.3 | 1.94 | 7.32 | 9.26 | 5.4 | 48.95 | 15 | 0 | 39.69 | 12.971 | 0 | Diesel-backup
2025-02-20 05:00 | 51 | 2 | Summer | 5 | 16.83 | -5.8 | 12.8 | 55.4 | 100.1 | 6.01 | 112.58 | 118.59 | 5.8 | 49.73 | 40.34 | 68.86 | 0 | 0 | 0 | Normal
2025-02-20 06:00 | 51 | 2 | Summer | 6 | 16.83 | -6.1 | 8.49 | 35.1 | 210.6 | 12.64 | 17.39 | 30.03 | 6.1 | 45 | 34.35 | -14.97 | 0 | 0 | 0 | Battery-supported
2025-02-20 07:00 | 51 | 2 | Summer | 7 | 16.83 | -6.6 | 2.37 | 94.9 | 112.4 | 6.74 | 0 | 6.74 | 6.6 | 45 | 19.05 | -38.26 | 0 | 0 | 0 | Battery-supported
2025-02-20 08:00 | 51 | 2 | Summer | 8 | 16.83 | 0.3 | 7.23 | 57.2 | 275 | 16.5 | 7.26 | 23.76 | 0 | 45 | 15 | -10.12 | 11.12 | 4.04 | 0 | Diesel-backup
2025-02-20 09:00 | 51 | 2 | Summer | 9 | 16.83 | -4 | 15.02 | 85.3 | 200.2 | 12.01 | 120 | 132.01 | 4 | 50.05 | 45.16 | 81.96 | 0 | 0 | 0 | Normal
2025-02-20 10:00 | 51 | 2 | Summer | 10 | 16.83 | -2.6 | 5.73 | 31 | 468.7 | 28.12 | 1.55 | 29.67 | 2.6 | 52.82 | 35.9 | -23.15 | 0 | 0 | 0 | Battery-supported
2025-02-20 11:00 | 51 | 2 | Summer | 11 | 16.83 | -5.4 | 8.51 | 63.2 | 339.2 | 20.35 | 17.6 | 37.95 | 5.4 | 47.98 | 31.89 | -10.03 | 0 | 0 | 0 | Battery-supported
2025-02-20 12:00 | 51 | 2 | Summer | 12 | 16.83 | -4.4 | 5.89 | 16 | 577.1 | 34.63 | 1.91 | 36.54 | 4.4 | 46.01 | 28.1 | -9.47 | 0 | 0 | 0 | Battery-supported
2025-02-20 13:00 | 51 | 2 | Summer | 13 | 16.83 | -5.2 | 9.64 | 13.6 | 578.8 | 34.73 | 32.4 | 67.13 | 5.2 | 52.65 | 33.43 | 14.48 | 0 | 0 | 0 | Normal
2025-02-20 14:00 | 51 | 2 | Summer | 14 | 16.83 | -9.1 | 4.18 | 50.4 | 379.9 | 22.79 | 0.04 | 22.83 | 9.1 | 48.41 | 23.2 | -25.58 | 0 | 0 | 0 | Battery-supported
2025-02-20 15:00 | 51 | 2 | Summer | 15 | 16.83 | -5.9 | 0.39 | 44.2 | 371.4 | 22.28 | 0 | 22.28 | 5.9 | 47.95 | 15 | -20.49 | 5.18 | 1.92 | 0 | Diesel-backup
2025-02-20 16:00 | 51 | 2 | Summer | 16 | 16.83 | -6.5 | 3.13 | 40.8 | 334 | 20.04 | 0 | 20.04 | 6.5 | 49.52 | 15 | 0 | 29.48 | 10.019 | 0 | Diesel-backup
2025-02-20 17:00 | 51 | 2 | Summer | 17 | 16.83 | -7.1 | 5.27 | 32.7 | 294.6 | 17.68 | 0.78 | 18.46 | 7.1 | 49.81 | 15 | 0 | 31.35 | 10.58 | 0 | Diesel-backup
2025-02-20 18:00 | 51 | 2 | Summer | 18 | 16.83 | -4.6 | 6.79 | 24.5 | 233.3 | 14 | 4.98 | 18.98 | 4.6 | 52.72 | 15 | 0 | 33.74 | 11.283 | 0 | Diesel-backup
2025-02-20 19:00 | 51 | 2 | Summer | 19 | 16.83 | 1.1 | 5.41 | 85.5 | 61.4 | 3.68 | 0.98 | 4.66 | 0 | 45.14 | 15 | 0 | 40.48 | 13.188 | 0 | Diesel-backup
2025-02-20 20:00 | 51 | 2 | Summer | 20 | 16.83 | -1.8 | 5.34 | 31.2 | 38.9 | 2.33 | 0.87 | 3.2 | 1.8 | 45 | 15 | 0 | 41.8 | 13.547 | 0 | Diesel-backup
2025-02-20 21:00 | 51 | 2 | Summer | 21 | 16.83 | 1.1 | 12.86 | 81.5 | 0 | 0 | 114.77 | 114.77 | 0 | 45 | 40.68 | 69.77 | 0 | 0 | 0 | Normal
2025-02-20 22:00 | 51 | 2 | Summer | 22 | 16.83 | -1 | 3.5 | 92.6 | 0 | 0 | 0 | 0 | 1 | 47.19 | 21.8 | -47.19 | 0 | 0 | 0 | Battery-supported
2025-02-20 23:00 | 51 | 2 | Summer | 23 | 16.83 | -0.4 | 7.26 | 60.5 | 0 | 0 | 7.44 | 7.44 | 0.4 | 45 | 15 | -17 | 20.56 | 7.223 | 0 | Diesel-backup
2025-02-21 | 52 | 2 | Summer | 0 | 16.66 | -4.6 | 2.49 | 64.6 | 0 | 0 | 0 | 0 | 4.6 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-02-21 01:00 | 52 | 2 | Summer | 1 | 16.66 | -1.8 | 10.84 | 89 | 0 | 0 | 55.35 | 55.35 | 1.8 | 45 | 18.81 | 10.35 | 0 | 0 | 0 | Normal
2025-02-21 02:00 | 52 | 2 | Summer | 2 | 16.66 | -1.7 | 8.38 | 87.4 | 0 | 0 | 16.27 | 16.27 | 1.7 | 45 | 15 | -9.52 | 19.21 | 6.781 | 0 | Diesel-backup
2025-02-21 03:00 | 52 | 2 | Summer | 3 | 16.66 | -5 | 21.21 | 90 | 0 | 0 | 120 | 120 | 5 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-02-21 04:00 | 52 | 2 | Summer | 4 | 16.66 | -2.9 | 3.41 | 85.7 | 14.5 | 0.87 | 0 | 0.87 | 2.9 | 45 | 24.95 | -44.13 | 0 | 0 | 0 | Battery-supported
2025-02-21 05:00 | 52 | 2 | Summer | 5 | 16.66 | -3.2 | 17.58 | 85.4 | 58.5 | 3.51 | 120 | 123.51 | 3.2 | 45 | 53.84 | 78.51 | 0 | 0 | 0 | Normal
2025-02-21 06:00 | 52 | 2 | Summer | 6 | 16.66 | -5.9 | 3.75 | 44.9 | 185.1 | 11.11 | 0 | 11.11 | 5.9 | 45 | 40.28 | -33.89 | 0 | 0 | 0 | Battery-supported
2025-02-21 07:00 | 52 | 2 | Summer | 7 | 16.66 | -7.3 | 5.71 | 29.7 | 299.4 | 17.96 | 1.51 | 19.47 | 7.3 | 45 | 30.07 | -25.53 | 0 | 0 | 0 | Battery-supported
2025-02-21 08:00 | 52 | 2 | Summer | 8 | 16.66 | -7.5 | 2.81 | 36.7 | 346.6 | 20.8 | 0 | 20.8 | 7.5 | 56.9 | 15.63 | -36.1 | 0 | 0 | 0 | Battery-supported
2025-02-21 09:00 | 52 | 2 | Summer | 9 | 16.66 | -4.6 | 21.05 | 77.2 | 233.3 | 14 | 120 | 134 | 4.6 | 46.79 | 47.72 | 87.21 | 0 | 0 | 0 | Normal
2025-02-21 10:00 | 52 | 2 | Summer | 10 | 16.66 | -3.9 | 9.15 | 34.9 | 450.3 | 27.02 | 25.24 | 52.26 | 3.9 | 47.79 | 49.37 | 4.47 | 0 | 0 | 0 | Normal
2025-02-21 11:00 | 52 | 2 | Summer | 11 | 16.66 | -6.2 | 9.21 | 80.7 | 254.4 | 15.26 | 26.06 | 41.32 | 6.2 | 52.61 | 44.85 | -11.29 | 0 | 0 | 0 | Battery-supported
2025-02-21 12:00 | 52 | 2 | Summer | 12 | 16.66 | -4 | 3.99 | 6.3 | 624.9 | 37.49 | 0.02 | 37.51 | 4 | 52.55 | 38.84 | -15.04 | 0 | 0 | 0 | Battery-supported
2025-02-21 13:00 | 52 | 2 | Summer | 13 | 16.66 | -2.5 | 1.08 | 83.9 | 238.9 | 14.33 | 0 | 14.33 | 2.5 | 45 | 26.57 | -30.67 | 0 | 0 | 0 | Battery-supported
2025-02-21 14:00 | 52 | 2 | Summer | 14 | 16.66 | -2 | 5.56 | 46.3 | 398 | 23.88 | 1.22 | 25.1 | 2 | 45 | 18.61 | -19.9 | 0 | 0 | 0 | Battery-supported
2025-02-21 15:00 | 52 | 2 | Summer | 15 | 16.66 | 0.4 | 4.9 | 87.9 | 188.7 | 11.32 | 0.38 | 11.7 | 0 | 45 | 15 | -9.02 | 24.28 | 8.412 | 0 | Diesel-backup
2025-02-21 16:00 | 52 | 2 | Summer | 16 | 16.66 | 0.2 | 1.74 | 44 | 320.2 | 19.21 | 0 | 19.21 | 0 | 45 | 15 | 0 | 25.79 | 8.887 | 0 | Diesel-backup
2025-02-21 17:00 | 52 | 2 | Summer | 17 | 16.66 | -4.5 | 5.8 | 19.2 | 329.8 | 19.79 | 1.7 | 21.49 | 4.5 | 45.27 | 15 | 0 | 23.78 | 8.256 | 0 | Diesel-backup
2025-02-21 18:00 | 52 | 2 | Summer | 18 | 16.66 | 1.7 | 7.29 | 43.3 | 188.3 | 11.3 | 7.62 | 18.92 | 0 | 45 | 15 | 0 | 26.08 | 8.977 | 0 | Diesel-backup
2025-02-21 19:00 | 52 | 2 | Summer | 19 | 16.66 | -3.1 | 9.53 | 37 | 117.6 | 7.06 | 30.69 | 37.75 | 3.1 | 47.66 | 15 | 0 | 9.91 | 3.616 | 0 | Diesel-backup
2025-02-21 20:00 | 52 | 2 | Summer | 20 | 16.66 | 0.4 | 1.23 | 38.2 | 29 | 1.74 | 0 | 1.74 | 0 | 48.3 | 15 | 0 | 46.56 | 14.899 | 0 | Diesel-backup
2025-02-21 21:00 | 52 | 2 | Summer | 21 | 16.66 | -1.8 | 2.94 | 39.4 | 0 | 0 | 0 | 0 | 1.8 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-02-21 22:00 | 52 | 2 | Summer | 22 | 16.66 | -3 | 4.08 | 89.8 | 0 | 0 | 0.03 | 0.03 | 3 | 45 | 15 | 0 | 44.97 | 14.392 | 0 | Diesel-backup
2025-02-21 23:00 | 52 | 2 | Summer | 23 | 16.66 | -6.3 | 13.22 | 54.5 | 0 | 0 | 120 | 120 | 6.3 | 48.33 | 41.37 | 71.67 | 0 | 0 | 0 | Normal
2025-02-22 | 53 | 2 | Summer | 0 | 16.49 | -3.1 | 13.11 | 48.5 | 0 | 0 | 120 | 120 | 3.1 | 45 | 68.97 | 75 | 0 | 0 | 0 | Normal
2025-02-22 01:00 | 53 | 2 | Summer | 1 | 16.49 | -6.5 | 8.88 | 23.4 | 0 | 0 | 21.8 | 21.8 | 6.5 | 45 | 59.69 | -23.2 | 0 | 0 | 0 | Battery-supported
2025-02-22 02:00 | 53 | 2 | Summer | 2 | 16.49 | -1.3 | 5.75 | 35.5 | 0 | 0 | 1.59 | 1.59 | 1.3 | 45 | 42.33 | -43.41 | 0 | 0 | 0 | Battery-supported
2025-02-22 03:00 | 53 | 2 | Summer | 3 | 16.49 | -0.5 | 13.73 | 27.6 | 0 | 0 | 120 | 120 | 0.5 | 45 | 69.93 | 75 | 0 | 0 | 0 | Normal
2025-02-22 04:00 | 53 | 2 | Summer | 4 | 16.49 | -6 | 8.24 | 15.5 | 26.9 | 1.61 | 14.91 | 16.52 | 6 | 46.65 | 57.88 | -30.13 | 0 | 0 | 0 | Battery-supported
2025-02-22 05:00 | 53 | 2 | Summer | 5 | 16.49 | -3.9 | 13.29 | 94.9 | 44.4 | 2.66 | 120 | 122.66 | 3.9 | 45 | 86.46 | 77.66 | 0 | 0 | 0 | Normal
2025-02-22 06:00 | 53 | 2 | Summer | 6 | 16.49 | -6.4 | 9.13 | 54.4 | 161.1 | 9.67 | 24.98 | 34.65 | 6.4 | 45 | 82.32 | -10.35 | 0 | 0 | 0 | Battery-supported
2025-02-22 07:00 | 53 | 2 | Summer | 7 | 16.49 | -6.3 | 1.95 | 34.3 | 282.3 | 16.94 | 0 | 16.94 | 6.3 | 45 | 71.09 | -28.06 | 0 | 0 | 0 | Battery-supported
2025-02-22 08:00 | 53 | 2 | Summer | 8 | 16.49 | -3.3 | 1.07 | 76.2 | 203.2 | 12.19 | 0 | 12.19 | 3.3 | 50.86 | 55.63 | -38.67 | 0 | 0 | 0 | Battery-supported
2025-02-22 09:00 | 53 | 2 | Summer | 9 | 16.49 | -5 | 5.38 | 62.5 | 293.2 | 17.59 | 0.93 | 18.52 | 5 | 47.07 | 44.21 | -28.55 | 0 | 0 | 0 | Battery-supported
2025-02-22 10:00 | 53 | 2 | Summer | 10 | 16.49 | -0.9 | 11.65 | 14.1 | 544.6 | 32.68 | 75.77 | 108.45 | 0.9 | 45 | 67.56 | 63.45 | 0 | 0 | 0 | Normal
2025-02-22 11:00 | 53 | 2 | Summer | 11 | 16.49 | -5.6 | 4.87 | 81.5 | 250.5 | 15.03 | 0.36 | 15.39 | 5.6 | 47.57 | 54.68 | -32.18 | 0 | 0 | 0 | Battery-supported
2025-02-22 12:00 | 53 | 2 | Summer | 12 | 16.49 | -2 | 15.26 | 8 | 616.4 | 36.98 | 120 | 156.98 | 2 | 46.45 | 95 | 109.56 | 0 | 0 | 0 | Normal
2025-02-22 13:00 | 53 | 2 | Summer | 13 | 16.49 | -3.7 | 11.04 | 7.7 | 606.7 | 36.4 | 60 | 96.4 | 3.7 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-02-22 14:00 | 53 | 2 | Summer | 14 | 16.49 | -1.7 | 14.5 | 31.6 | 464.8 | 27.89 | 120 | 147.89 | 1.7 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-02-22 15:00 | 53 | 2 | Summer | 15 | 16.49 | -4.1 | 5.48 | 60.5 | 301.3 | 18.08 | 1.09 | 19.17 | 4.1 | 45.11 | 84.62 | -25.94 | 0 | 0 | 0 | Battery-supported
2025-02-22 16:00 | 53 | 2 | Summer | 16 | 16.49 | -2.8 | 3.6 | 42.8 | 322.1 | 19.33 | 0 | 19.33 | 2.8 | 45 | 74.36 | -25.67 | 0 | 0 | 0 | Battery-supported
2025-02-22 17:00 | 53 | 2 | Summer | 17 | 16.49 | -2.7 | 3.24 | 9.2 | 354 | 21.24 | 0 | 21.24 | 2.7 | 45 | 64.85 | -23.76 | 0 | 0 | 0 | Battery-supported
2025-02-22 18:00 | 53 | 2 | Summer | 18 | 16.49 | -4 | 9.64 | 76.6 | 115.7 | 6.94 | 32.4 | 39.34 | 4 | 50.13 | 60.54 | -10.79 | 0 | 0 | 0 | Battery-supported
2025-02-22 19:00 | 53 | 2 | Summer | 19 | 16.49 | -0.6 | 2.09 | 38.6 | 109.5 | 6.57 | 0 | 6.57 | 0.6 | 45 | 45.16 | -38.43 | 0 | 0 | 0 | Battery-supported
2025-02-22 20:00 | 53 | 2 | Summer | 20 | 16.49 | -0.5 | 2.2 | 53.5 | 18.3 | 1.1 | 0 | 1.1 | 0.5 | 45 | 27.6 | -43.9 | 0 | 0 | 0 | Battery-supported
2025-02-22 21:00 | 53 | 2 | Summer | 21 | 16.49 | -0.7 | 4.68 | 72 | 0 | 0 | 0.23 | 0.23 | 0.7 | 45 | 15 | -31.51 | 13.26 | 4.782 | 0 | Diesel-backup
2025-02-22 22:00 | 53 | 2 | Summer | 22 | 16.49 | 1.2 | 8.05 | 59.4 | 0 | 0 | 13.18 | 13.18 | 0 | 45 | 15 | 0 | 31.82 | 10.719 | 0 | Diesel-backup
2025-02-22 23:00 | 53 | 2 | Summer | 23 | 16.49 | 0.8 | 4.14 | 32.9 | 0 | 0 | 0.04 | 0.04 | 0 | 45 | 15 | 0 | 44.96 | 14.39 | 0 | Diesel-backup
2025-02-23 | 54 | 2 | Summer | 0 | 16.32 | -3.7 | 13.16 | 87.7 | 0 | 0 | 120 | 120 | 3.7 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-02-23 01:00 | 54 | 2 | Summer | 1 | 16.32 | -2.4 | 14.65 | 15.2 | 0 | 0 | 120 | 120 | 2.4 | 45 | 70.2 | 75 | 0 | 0 | 0 | Normal
2025-02-23 02:00 | 54 | 2 | Summer | 2 | 16.32 | -5 | 0.69 | 14 | 0 | 0 | 0 | 0 | 5 | 45 | 52.2 | -45 | 0 | 0 | 0 | Battery-supported
2025-02-23 03:00 | 54 | 2 | Summer | 3 | 16.32 | -3.9 | 9.26 | 36.9 | 0 | 0 | 26.75 | 26.75 | 3.9 | 45.59 | 44.66 | -18.84 | 0 | 0 | 0 | Battery-supported
2025-02-23 04:00 | 54 | 2 | Summer | 4 | 16.32 | -5.7 | 4.9 | 58.9 | 11.2 | 0.67 | 0.38 | 1.05 | 5.7 | 45 | 27.08 | -43.95 | 0 | 0 | 0 | Battery-supported
2025-02-23 05:00 | 54 | 2 | Summer | 5 | 16.32 | -1.1 | 11.99 | 70.3 | 68.6 | 4.12 | 85.65 | 89.77 | 1.1 | 45 | 43.56 | 44.77 | 0 | 0 | 0 | Normal
2025-02-23 06:00 | 54 | 2 | Summer | 6 | 16.32 | -4.1 | 9.45 | 86.8 | 92.4 | 5.54 | 29.48 | 35.02 | 4.1 | 45 | 39.57 | -9.98 | 0 | 0 | 0 | Battery-supported
2025-02-23 07:00 | 54 | 2 | Summer | 7 | 16.32 | -5.5 | 7.84 | 63.6 | 196.1 | 11.77 | 11.44 | 23.21 | 5.5 | 45 | 30.85 | -21.79 | 0 | 0 | 0 | Battery-supported
2025-02-23 08:00 | 54 | 2 | Summer | 8 | 16.32 | -2.5 | 6.51 | 60.3 | 257.9 | 15.47 | 3.82 | 19.29 | 2.5 | 45 | 20.57 | -25.71 | 0 | 0 | 0 | Battery-supported
2025-02-23 09:00 | 54 | 2 | Summer | 9 | 16.32 | -9.8 | 2.22 | 53 | 331.2 | 19.87 | 0 | 19.87 | 9.8 | 61.34 | 15 | -13.92 | 27.55 | 9.432 | 0 | Diesel-backup
2025-02-23 10:00 | 54 | 2 | Summer | 10 | 16.32 | -9.3 | 23.09 | 31.6 | 463.7 | 27.82 | 120 | 147.82 | 9.3 | 51.55 | 50.43 | 96.27 | 0 | 0 | 0 | Normal
2025-02-23 11:00 | 54 | 2 | Summer | 11 | 16.32 | -2.9 | 2.93 | 61.1 | 348.7 | 20.92 | 0 | 20.92 | 2.9 | 45.34 | 40.66 | -24.42 | 0 | 0 | 0 | Battery-supported
2025-02-23 12:00 | 54 | 2 | Summer | 12 | 16.32 | -4.2 | 17.79 | 0 | 655.9 | 39.35 | 120 | 159.35 | 4.2 | 47.01 | 82 | 112.34 | 0 | 0 | 0 | Normal
2025-02-23 13:00 | 54 | 2 | Summer | 13 | 16.32 | -3.4 | 10.54 | 53.8 | 383.8 | 23.03 | 48.83 | 71.86 | 3.4 | 45 | 91.88 | 26.86 | 0 | 0 | 0 | Normal
2025-02-23 14:00 | 54 | 2 | Summer | 14 | 16.32 | -6.5 | 5.07 | 31.8 | 462.9 | 27.77 | 0.54 | 28.31 | 6.5 | 45 | 85.21 | -16.69 | 0 | 0 | 0 | Battery-supported
2025-02-23 15:00 | 54 | 2 | Summer | 15 | 16.32 | -3.3 | 4.57 | 22.6 | 456.5 | 27.39 | 0.17 | 27.56 | 3.3 | 52.07 | 75.4 | -24.51 | 0 | 0 | 0 | Battery-supported
2025-02-23 16:00 | 54 | 2 | Summer | 16 | 16.32 | 1.6 | 2.14 | 64.5 | 242.9 | 14.57 | 0 | 14.57 | 0 | 45.41 | 63.07 | -30.84 | 0 | 0 | 0 | Battery-supported
2025-02-23 17:00 | 54 | 2 | Summer | 17 | 16.32 | -0.7 | 7.22 | 20.2 | 318 | 19.08 | 7.21 | 26.29 | 0.7 | 48.14 | 54.33 | -21.85 | 0 | 0 | 0 | Battery-supported
2025-02-23 18:00 | 54 | 2 | Summer | 18 | 16.32 | -1.9 | 2.07 | 68.6 | 128.7 | 7.72 | 0 | 7.72 | 1.9 | 45.84 | 39.08 | -38.12 | 0 | 0 | 0 | Battery-supported
2025-02-23 19:00 | 54 | 2 | Summer | 19 | 16.32 | -3.1 | 13.6 | 59.9 | 80 | 4.8 | 120 | 124.8 | 3.1 | 50.74 | 66.34 | 74.06 | 0 | 0 | 0 | Normal
2025-02-23 20:00 | 54 | 2 | Summer | 20 | 16.32 | -3 | 8.32 | 28.3 | 15.9 | 0.95 | 15.67 | 16.62 | 3 | 45 | 54.98 | -28.38 | 0 | 0 | 0 | Battery-supported
2025-02-23 21:00 | 54 | 2 | Summer | 21 | 16.32 | -6.8 | 6.93 | 87.2 | 0 | 0 | 5.65 | 5.65 | 6.8 | 45 | 39.24 | -39.35 | 0 | 0 | 0 | Battery-supported
2025-02-23 22:00 | 54 | 2 | Summer | 22 | 16.32 | -1.7 | 7.49 | 36.6 | 0 | 0 | 8.89 | 8.89 | 1.7 | 45 | 24.8 | -36.11 | 0 | 0 | 0 | Battery-supported
2025-02-23 23:00 | 54 | 2 | Summer | 23 | 16.32 | -0.7 | 8.53 | 14.2 | 0 | 0 | 17.81 | 17.81 | 0.7 | 45 | 15 | -24.5 | 2.69 | 1.007 | 0 | Diesel-backup
2025-02-24 | 55 | 2 | Summer | 0 | 16.15 | -6.5 | 5.69 | 78.9 | 0 | 0 | 1.47 | 1.47 | 6.5 | 45 | 15 | 0 | 43.53 | 14.012 | 0 | Diesel-backup
2025-02-24 01:00 | 55 | 2 | Summer | 1 | 16.15 | -4.8 | 6.2 | 87.8 | 0 | 0 | 2.75 | 2.75 | 4.8 | 45 | 15 | 0 | 42.25 | 13.669 | 0 | Diesel-backup
2025-02-24 02:00 | 55 | 2 | Summer | 2 | 16.15 | -6.3 | 18.93 | 69.3 | 0 | 0 | 120 | 120 | 6.3 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-02-24 03:00 | 55 | 2 | Summer | 3 | 16.15 | -6.2 | 12.86 | 73.6 | 0 | 0 | 114.77 | 114.77 | 6.2 | 45 | 68.28 | 69.77 | 0 | 0 | 0 | Normal
2025-02-24 04:00 | 55 | 2 | Summer | 4 | 16.15 | -4.4 | 10.3 | 65 | 4.9 | 0.29 | 44.01 | 44.3 | 4.4 | 45 | 68 | -0.7 | 0 | 0 | 0 | Battery-supported
2025-02-24 05:00 | 55 | 2 | Summer | 5 | 16.15 | -9.4 | 5.08 | 76.2 | 58.4 | 3.5 | 0.55 | 4.05 | 9.4 | 45 | 51.62 | -40.95 | 0 | 0 | 0 | Battery-supported
2025-02-24 06:00 | 55 | 2 | Summer | 6 | 16.15 | -3.7 | 1.51 | 42.8 | 174.9 | 10.49 | 0 | 10.49 | 3.7 | 45 | 37.81 | -34.51 | 0 | 0 | 0 | Battery-supported
2025-02-24 07:00 | 55 | 2 | Summer | 7 | 16.15 | -3.5 | 9.6 | 76.8 | 156.7 | 9.4 | 31.77 | 41.17 | 3.5 | 45 | 36.28 | -3.83 | 0 | 0 | 0 | Battery-supported
2025-02-24 08:00 | 55 | 2 | Summer | 8 | 16.15 | -5.8 | 7.5 | 80.9 | 183.7 | 11.02 | 8.96 | 19.98 | 5.8 | 54.82 | 22.34 | -34.84 | 0 | 0 | 0 | Battery-supported
2025-02-24 09:00 | 55 | 2 | Summer | 9 | 16.15 | -10.6 | 6.11 | 39.3 | 386.2 | 23.17 | 2.49 | 25.66 | 10.6 | 55.55 | 15 | -18.36 | 11.53 | 4.184 | 0 | Diesel-backup
2025-02-24 10:00 | 55 | 2 | Summer | 10 | 16.15 | -7.2 | 6.74 | 77.5 | 254.1 | 15.25 | 4.76 | 20.01 | 7.2 | 49.35 | 15 | 0 | 29.34 | 9.977 | 0 | Diesel-backup
2025-02-24 11:00 | 55 | 2 | Summer | 11 | 16.15 | -2.1 | 3.07 | 48.6 | 409.1 | 24.55 | 0 | 24.55 | 2.1 | 50.23 | 15 | 0 | 25.68 | 8.853 | 0 | Diesel-backup
2025-02-24 12:00 | 55 | 2 | Summer | 12 | 16.15 | -10.6 | 3.75 | 77.8 | 273.2 | 16.39 | 0 | 16.39 | 10.6 | 48.62 | 15 | 0 | 32.23 | 10.84 | 0 | Diesel-backup
2025-02-24 13:00 | 55 | 2 | Summer | 13 | 16.15 | -4.9 | 12.87 | 19.8 | 548.2 | 32.89 | 115.14 | 148.03 | 4.9 | 46.74 | 52.27 | 101.29 | 0 | 0 | 0 | Normal
2025-02-24 14:00 | 55 | 2 | Summer | 14 | 16.15 | -6.3 | 1.18 | 65.4 | 309.2 | 18.55 | 0 | 18.55 | 6.3 | 45.51 | 41.49 | -26.96 | 0 | 0 | 0 | Battery-supported
2025-02-24 15:00 | 55 | 2 | Summer | 15 | 16.15 | -1.6 | 11.82 | 17.6 | 475 | 28.5 | 80.61 | 109.11 | 1.6 | 45 | 65.08 | 64.11 | 0 | 0 | 0 | Normal
2025-02-24 16:00 | 55 | 2 | Summer | 16 | 16.15 | -4.5 | 15.74 | 56 | 271 | 16.26 | 120 | 136.26 | 4.5 | 45 | 95 | 81.3 | 0 | 0 | 0 | Normal
2025-02-24 17:00 | 55 | 2 | Summer | 17 | 16.15 | -1.8 | 9.48 | 41 | 255.7 | 15.34 | 29.93 | 45.27 | 1.8 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-02-24 18:00 | 55 | 2 | Summer | 18 | 16.15 | -1.2 | 9.21 | 61.8 | 138.3 | 8.3 | 26.06 | 34.36 | 1.2 | 45 | 90.74 | -10.64 | 0 | 0 | 0 | Battery-supported
2025-02-24 19:00 | 55 | 2 | Summer | 19 | 16.15 | 1.8 | 3.73 | 68 | 66.8 | 4.01 | 0 | 4.01 | 0 | 45 | 74.35 | -40.99 | 0 | 0 | 0 | Battery-supported
2025-02-24 20:00 | 55 | 2 | Summer | 20 | 16.15 | -2.7 | 4.13 | 47.3 | 6.2 | 0.37 | 0.03 | 0.4 | 2.7 | 46.74 | 55.81 | -46.34 | 0 | 0 | 0 | Battery-supported
2025-02-24 21:00 | 55 | 2 | Summer | 21 | 16.15 | -1.5 | 5.37 | 63 | 0 | 0 | 0.92 | 0.92 | 1.5 | 45 | 38.18 | -44.08 | 0 | 0 | 0 | Battery-supported
2025-02-24 22:00 | 55 | 2 | Summer | 22 | 16.15 | -5.7 | 2.61 | 47.7 | 0 | 0 | 0 | 0 | 5.7 | 45 | 20.18 | -45 | 0 | 0 | 0 | Battery-supported
2025-02-24 23:00 | 55 | 2 | Summer | 23 | 16.15 | -0.1 | 3.92 | 72.8 | 0 | 0 | 0.01 | 0.01 | 0.1 | 45 | 15 | -12.95 | 32.04 | 10.784 | 0 | Diesel-backup
2025-02-25 | 56 | 2 | Summer | 0 | 15.98 | -4.8 | 7.5 | 18.9 | 0 | 0 | 8.96 | 8.96 | 4.8 | 45 | 15 | 0 | 36.04 | 11.946 | 0 | Diesel-backup
2025-02-25 01:00 | 56 | 2 | Summer | 1 | 15.98 | -4.7 | 5.17 | 58.2 | 0 | 0 | 0.65 | 0.65 | 4.7 | 45 | 15 | 0 | 44.35 | 14.229 | 0 | Diesel-backup
2025-02-25 02:00 | 56 | 2 | Summer | 2 | 15.98 | -3.9 | 7.91 | 51.5 | 0 | 0 | 12 | 12 | 3.9 | 45 | 15 | 0 | 33 | 11.067 | 0 | Diesel-backup
2025-02-25 03:00 | 56 | 2 | Summer | 3 | 15.98 | -7.7 | 12.88 | 26 | 0 | 0 | 115.51 | 115.51 | 7.7 | 45 | 40.95 | 70.51 | 0 | 0 | 0 | Normal
2025-02-25 04:00 | 56 | 2 | Summer | 4 | 15.98 | -4.1 | 7.88 | 26.8 | 0 | 0 | 11.76 | 11.76 | 4.1 | 45 | 27.65 | -33.24 | 0 | 0 | 0 | Battery-supported
2025-02-25 05:00 | 56 | 2 | Summer | 5 | 15.98 | -2.8 | 9.29 | 55.6 | 74.1 | 4.45 | 27.17 | 31.62 | 2.8 | 45 | 22.3 | -13.38 | 0 | 0 | 0 | Battery-supported
2025-02-25 06:00 | 56 | 2 | Summer | 6 | 15.98 | -4.5 | 2.05 | 19.7 | 213.3 | 12.8 | 0 | 12.8 | 4.5 | 45 | 15 | -18.25 | 13.95 | 5.019 | 0 | Diesel-backup
2025-02-25 07:00 | 56 | 2 | Summer | 7 | 15.98 | -8.8 | 12.75 | 51.6 | 223 | 13.38 | 110.77 | 124.15 | 8.8 | 45 | 44.13 | 79.15 | 0 | 0 | 0 | Normal
2025-02-25 08:00 | 56 | 2 | Summer | 8 | 15.98 | -5.6 | 2.01 | 54.6 | 273.7 | 16.42 | 0 | 16.42 | 5.6 | 48.44 | 31.32 | -32.02 | 0 | 0 | 0 | Battery-supported
2025-02-25 09:00 | 56 | 2 | Summer | 9 | 15.98 | -3.7 | 4.93 | 13.5 | 490 | 29.4 | 0.41 | 29.81 | 3.7 | 45 | 25.24 | -15.19 | 0 | 0 | 0 | Battery-supported
2025-02-25 10:00 | 56 | 2 | Summer | 10 | 15.98 | -9.3 | 3.19 | 91.3 | 190.9 | 11.45 | 0 | 11.45 | 9.3 | 63.09 | 15 | -25.61 | 26.03 | 8.962 | 0 | Diesel-backup
2025-02-25 11:00 | 56 | 2 | Summer | 11 | 15.98 | -7.3 | 1.52 | 64.8 | 330.5 | 19.83 | 0 | 19.83 | 7.3 | 49.66 | 15 | 0 | 29.83 | 10.125 | 0 | Diesel-backup
2025-02-25 12:00 | 56 | 2 | Summer | 12 | 15.98 | -2.7 | 7.63 | 35.8 | 479.8 | 28.79 | 9.86 | 38.65 | 2.7 | 45.57 | 15 | 0 | 6.92 | 2.552 | 0 | Diesel-backup
2025-02-25 13:00 | 56 | 2 | Summer | 13 | 15.98 | -3.7 | 9.78 | 54.5 | 380.3 | 22.82 | 34.66 | 57.48 | 3.7 | 45 | 19.59 | 12.48 | 0 | 0 | 0 | Normal
2025-02-25 14:00 | 56 | 2 | Summer | 14 | 15.98 | -3 | 16.02 | 18.4 | 522.2 | 31.33 | 120 | 151.33 | 3 | 45 | 58.72 | 106.33 | 0 | 0 | 0 | Normal
2025-02-25 15:00 | 56 | 2 | Summer | 15 | 15.98 | 0.6 | 8.31 | 20.9 | 459.8 | 27.59 | 15.58 | 43.17 | 0 | 45 | 57.99 | -1.83 | 0 | 0 | 0 | Battery-supported
2025-02-25 16:00 | 56 | 2 | Summer | 16 | 15.98 | -2.1 | 3.91 | 38.4 | 329.9 | 19.79 | 0.01 | 19.8 | 2.1 | 45 | 47.91 | -25.2 | 0 | 0 | 0 | Battery-supported
2025-02-25 17:00 | 56 | 2 | Summer | 17 | 15.98 | -1.4 | 5.09 | 44.5 | 242.6 | 14.56 | 0.56 | 15.12 | 1.4 | 45 | 35.96 | -29.88 | 0 | 0 | 0 | Battery-supported
2025-02-25 18:00 | 56 | 2 | Summer | 18 | 15.98 | 3.4 | 1.73 | 35.1 | 184.4 | 11.06 | 0 | 11.06 | 0 | 47.11 | 21.54 | -36.05 | 0 | 0 | 0 | Battery-supported
2025-02-25 19:00 | 56 | 2 | Summer | 19 | 15.98 | -2.9 | 5.45 | 66.7 | 63.5 | 3.81 | 1.04 | 4.85 | 2.9 | 45 | 15 | -16.35 | 23.8 | 8.263 | 0 | Diesel-backup
2025-02-25 20:00 | 56 | 2 | Summer | 20 | 15.98 | -4.1 | 6.9 | 66 | 0 | 0 | 5.5 | 5.5 | 4.1 | 45.17 | 15 | 0 | 39.67 | 12.965 | 0 | Diesel-backup
2025-02-25 21:00 | 56 | 2 | Summer | 21 | 15.98 | -1.5 | 9.53 | 38.1 | 0 | 0 | 30.69 | 30.69 | 1.5 | 45 | 15 | 0 | 14.31 | 5.141 | 0 | Diesel-backup
2025-02-25 22:00 | 56 | 2 | Summer | 22 | 15.98 | -1.6 | 11.09 | 5.9 | 0 | 0 | 61.2 | 61.2 | 1.6 | 45 | 20.96 | 16.2 | 0 | 0 | 0 | Normal
2025-02-25 23:00 | 56 | 2 | Summer | 23 | 15.98 | -4 | 9.34 | 71.4 | 0 | 0 | 27.88 | 27.88 | 4 | 45 | 15 | -14.9 | 2.22 | 0.83 | 0 | Diesel-backup
2025-02-26 | 57 | 2 | Summer | 0 | 15.82 | -5.5 | 3.63 | 48.9 | 0 | 0 | 0 | 0 | 5.5 | 45.87 | 15 | 0 | 45.87 | 14.678 | 0 | Diesel-backup
2025-02-26 01:00 | 57 | 2 | Summer | 1 | 15.82 | 1.5 | 2.92 | 79.4 | 0 | 0 | 0 | 0 | 0 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-02-26 02:00 | 57 | 2 | Summer | 2 | 15.82 | -3.3 | 10.65 | 92.3 | 0 | 0 | 51.16 | 51.16 | 3.3 | 45 | 17.27 | 6.16 | 0 | 0 | 0 | Normal
2025-02-26 03:00 | 57 | 2 | Summer | 3 | 15.82 | -6 | 1.48 | 38.4 | 0 | 0 | 0 | 0 | 6 | 45 | 15 | -5.67 | 39.33 | 12.872 | 0 | Diesel-backup
2025-02-26 04:00 | 57 | 2 | Summer | 4 | 15.82 | -2.7 | 20.54 | 33.1 | 0 | 0 | 120 | 120 | 2.7 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-02-26 05:00 | 57 | 2 | Summer | 5 | 15.82 | -5.3 | 4.18 | 32.7 | 89 | 5.34 | 0.04 | 5.38 | 5.3 | 45 | 26.75 | -39.62 | 0 | 0 | 0 | Battery-supported
2025-02-26 06:00 | 57 | 2 | Summer | 6 | 15.82 | -5.9 | 13.82 | 77.6 | 101.5 | 6.09 | 120 | 126.09 | 5.9 | 45 | 56.59 | 81.09 | 0 | 0 | 0 | Normal
2025-02-26 07:00 | 57 | 2 | Summer | 7 | 15.82 | -4.2 | 4.72 | 49.5 | 225.2 | 13.51 | 0.25 | 13.76 | 4.2 | 45 | 44.1 | -31.24 | 0 | 0 | 0 | Battery-supported
2025-02-26 08:00 | 57 | 2 | Summer | 8 | 15.82 | -8.3 | 9.95 | 17.2 | 400.3 | 24.02 | 37.56 | 61.58 | 8.3 | 52.56 | 47.42 | 9.02 | 0 | 0 | 0 | Normal
2025-02-26 09:00 | 57 | 2 | Summer | 9 | 15.82 | -4.7 | 3 | 21.1 | 457.1 | 27.43 | 0 | 27.43 | 4.7 | 45 | 40.39 | -17.57 | 0 | 0 | 0 | Battery-supported
2025-02-26 10:00 | 57 | 2 | Summer | 10 | 15.82 | -1.1 | 7.18 | 27.2 | 481.7 | 28.9 | 6.98 | 35.88 | 1.1 | 45 | 36.74 | -9.12 | 0 | 0 | 0 | Battery-supported
2025-02-26 11:00 | 57 | 2 | Summer | 11 | 15.82 | -4 | 1.83 | 88.1 | 218.3 | 13.1 | 0 | 13.1 | 4 | 45.98 | 23.59 | -32.88 | 0 | 0 | 0 | Battery-supported
2025-02-26 12:00 | 57 | 2 | Summer | 12 | 15.82 | -5.6 | 8.6 | 84 | 242.6 | 14.56 | 18.57 | 33.13 | 5.6 | 45 | 18.84 | -11.87 | 0 | 0 | 0 | Battery-supported
2025-02-26 13:00 | 57 | 2 | Summer | 13 | 15.82 | -5.5 | 2.96 | 50.4 | 399.9 | 23.99 | 0 | 23.99 | 5.5 | 48.28 | 15 | -9.6 | 14.69 | 5.27 | 0 | Diesel-backup
2025-02-26 14:00 | 57 | 2 | Summer | 14 | 15.82 | -4.9 | 3.32 | 52.6 | 366.2 | 21.97 | 0 | 21.97 | 4.9 | 45 | 15 | 0 | 23.03 | 8.017 | 0 | Diesel-backup
2025-02-26 15:00 | 57 | 2 | Summer | 15 | 15.82 | -4.2 | 5.28 | 20.8 | 458.1 | 27.49 | 0.79 | 28.28 | 4.2 | 52.75 | 15 | 0 | 24.47 | 8.473 | 0 | Diesel-backup
2025-02-26 16:00 | 57 | 2 | Summer | 16 | 15.82 | -4.1 | 6.01 | 67 | 228.6 | 13.72 | 2.21 | 15.93 | 4.1 | 52.05 | 15 | 0 | 36.12 | 11.969 | 0 | Diesel-backup
2025-02-26 17:00 | 57 | 2 | Summer | 17 | 15.82 | -0.9 | 9.57 | 63.8 | 186.9 | 11.21 | 31.3 | 42.51 | 0.9 | 48.23 | 15 | 0 | 5.72 | 2.118 | 0 | Diesel-backup
2025-02-26 18:00 | 57 | 2 | Summer | 18 | 15.82 | -6.5 | 9 | 82 | 93.4 | 5.6 | 23.29 | 28.89 | 6.5 | 49.72 | 15 | 0 | 20.83 | 7.31 | 0 | Diesel-backup
2025-02-26 19:00 | 57 | 2 | Summer | 19 | 15.82 | -0.7 | 7.66 | 55 | 69.2 | 4.15 | 10.08 | 14.23 | 0.7 | 45 | 15 | 0 | 30.77 | 10.407 | 0 | Diesel-backup
2025-02-26 20:00 | 57 | 2 | Summer | 20 | 15.82 | -3.3 | 11.86 | 39.3 | 0 | 0 | 81.78 | 81.78 | 3.3 | 45.23 | 28.45 | 36.55 | 0 | 0 | 0 | Normal
2025-02-26 21:00 | 57 | 2 | Summer | 21 | 15.82 | -1.7 | 8.85 | 79.3 | 0 | 0 | 21.43 | 21.43 | 1.7 | 45 | 19.02 | -23.57 | 0 | 0 | 0 | Battery-supported
2025-02-26 22:00 | 57 | 2 | Summer | 22 | 15.82 | -5.2 | 9.24 | 25.7 | 0 | 0 | 26.47 | 26.47 | 5.2 | 46.39 | 15 | -10.06 | 9.86 | 3.6 | 0 | Diesel-backup
2025-02-26 23:00 | 57 | 2 | Summer | 23 | 15.82 | 0 | 3.3 | 68 | 0 | 0 | 0 | 0 | 0 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-02-27 | 58 | 2 | Summer | 0 | 15.65 | -0.6 | 12.44 | 88 | 0 | 0 | 100.01 | 100.01 | 0.6 | 45 | 35.24 | 55.01 | 0 | 0 | 0 | Normal
2025-02-27 01:00 | 58 | 2 | Summer | 1 | 15.65 | -1.6 | 11.55 | 38.4 | 0 | 0 | 73.01 | 73.01 | 1.6 | 45 | 45.55 | 28.01 | 0 | 0 | 0 | Normal
2025-02-27 02:00 | 58 | 2 | Summer | 2 | 15.65 | -7.5 | 7.91 | 69.8 | 0 | 0 | 12 | 12 | 7.5 | 45 | 32.35 | -33 | 0 | 0 | 0 | Battery-supported
2025-02-27 03:00 | 58 | 2 | Summer | 3 | 15.65 | -2.7 | 11.3 | 54.1 | 0 | 0 | 66.42 | 66.42 | 2.7 | 45 | 40.23 | 21.42 | 0 | 0 | 0 | Normal
2025-02-27 04:00 | 58 | 2 | Summer | 4 | 15.65 | -4 | 6.86 | 69.2 | 0 | 0 | 5.31 | 5.31 | 4 | 45 | 24.36 | -39.69 | 0 | 0 | 0 | Battery-supported
2025-02-27 05:00 | 58 | 2 | Summer | 5 | 15.65 | -8.7 | 16.58 | 66.1 | 54.6 | 3.28 | 120 | 123.28 | 8.7 | 46.05 | 52.78 | 77.23 | 0 | 0 | 0 | Normal
2025-02-27 06:00 | 58 | 2 | Summer | 6 | 15.65 | -5.5 | 7.47 | 63.8 | 122.6 | 7.36 | 8.76 | 16.12 | 5.5 | 45.38 | 41.07 | -29.26 | 0 | 0 | 0 | Battery-supported
2025-02-27 07:00 | 58 | 2 | Summer | 7 | 15.65 | -4.8 | 6.71 | 50.2 | 219.9 | 13.19 | 4.63 | 17.82 | 4.8 | 45 | 30.2 | -27.18 | 0 | 0 | 0 | Battery-supported
2025-02-27 08:00 | 58 | 2 | Summer | 8 | 15.65 | -4.4 | 8.91 | 63.2 | 239.8 | 14.39 | 22.16 | 36.55 | 4.4 | 50.52 | 24.61 | -13.97 | 0 | 0 | 0 | Battery-supported
2025-02-27 09:00 | 58 | 2 | Summer | 9 | 15.65 | -5.2 | 18.58 | 79.2 | 219.6 | 13.18 | 120 | 133.18 | 5.2 | 55.06 | 53.36 | 78.12 | 0 | 0 | 0 | Normal
2025-02-27 10:00 | 58 | 2 | Summer | 10 | 15.65 | -4.8 | 4.83 | 100 | 151 | 9.06 | 0.33 | 9.39 | 4.8 | 45.95 | 38.74 | -36.56 | 0 | 0 | 0 | Battery-supported
2025-02-27 11:00 | 58 | 2 | Summer | 11 | 15.65 | -2 | 8.56 | 69.8 | 306.2 | 18.37 | 18.13 | 36.5 | 2 | 45 | 35.34 | -8.5 | 0 | 0 | 0 | Battery-supported
2025-02-27 12:00 | 58 | 2 | Summer | 12 | 15.65 | -2.2 | 5.08 | 36.7 | 475.4 | 28.52 | 0.55 | 29.07 | 2.2 | 45.68 | 28.69 | -16.61 | 0 | 0 | 0 | Battery-supported
2025-02-27 13:00 | 58 | 2 | Summer | 13 | 15.65 | -10.8 | 6.71 | 51.7 | 393.6 | 23.62 | 4.63 | 28.25 | 10.8 | 53.2 | 18.71 | -24.95 | 0 | 0 | 0 | Battery-supported
2025-02-27 14:00 | 58 | 2 | Summer | 14 | 15.65 | -4.8 | 3.92 | 58.8 | 337.7 | 20.26 | 0.01 | 20.27 | 4.8 | 46.93 | 15 | -9.29 | 17.37 | 6.174 | 0 | Diesel-backup
2025-02-27 15:00 | 58 | 2 | Summer | 15 | 15.65 | -4.1 | 9.12 | 46.6 | 351.8 | 21.11 | 24.84 | 45.95 | 4.1 | 52.84 | 15 | 0 | 6.89 | 2.541 | 0 | Diesel-backup
2025-02-27 16:00 | 58 | 2 | Summer | 16 | 15.65 | -7.2 | 7.09 | 23.1 | 376.9 | 22.61 | 6.48 | 29.09 | 7.2 | 59.71 | 15 | 0 | 30.62 | 10.362 | 0 | Diesel-backup
2025-02-27 17:00 | 58 | 2 | Summer | 17 | 15.65 | -2.9 | 11.16 | 44.8 | 234.1 | 14.05 | 62.91 | 76.96 | 2.9 | 45 | 26.76 | 31.96 | 0 | 0 | 0 | Normal
2025-02-27 18:00 | 58 | 2 | Summer | 18 | 15.65 | -0.1 | 13 | 61.8 | 126.1 | 7.57 | 120 | 127.57 | 0.1 | 52.35 | 54.44 | 75.22 | 0 | 0 | 0 | Normal
2025-02-27 19:00 | 58 | 2 | Summer | 19 | 15.65 | -5.1 | 14.15 | 23.8 | 89 | 5.34 | 120 | 125.34 | 5.1 | 46.68 | 83.39 | 78.66 | 0 | 0 | 0 | Normal
2025-02-27 20:00 | 58 | 2 | Summer | 20 | 15.65 | -1.9 | 5.21 | 38.1 | 0 | 0 | 0.7 | 0.7 | 1.9 | 47.93 | 64.5 | -47.23 | 0 | 0 | 0 | Battery-supported
2025-02-27 21:00 | 58 | 2 | Summer | 21 | 15.65 | -4.7 | 8.92 | 2.8 | 0 | 0 | 22.28 | 22.28 | 4.7 | 45 | 55.41 | -22.72 | 0 | 0 | 0 | Battery-supported
2025-02-27 22:00 | 58 | 2 | Summer | 22 | 15.65 | -4.3 | 14.68 | 42.6 | 0 | 0 | 120 | 120 | 4.3 | 45 | 83.01 | 75 | 0 | 0 | 0 | Normal
2025-02-27 23:00 | 58 | 2 | Summer | 23 | 15.65 | 0.2 | 3.9 | 60.1 | 0 | 0 | 0.01 | 0.01 | 0 | 45 | 65.01 | -44.99 | 0 | 0 | 0 | Battery-supported
2025-02-28 | 59 | 2 | Summer | 0 | 15.49 | -4.7 | 7.59 | 25.5 | 0 | 0 | 9.58 | 9.58 | 4.7 | 45 | 50.85 | -35.42 | 0 | 0 | 0 | Battery-supported
2025-02-28 01:00 | 59 | 2 | Summer | 1 | 15.49 | -2.9 | 4.1 | 46.9 | 0 | 0 | 0.03 | 0.03 | 2.9 | 45 | 32.86 | -44.97 | 0 | 0 | 0 | Battery-supported
2025-02-28 02:00 | 59 | 2 | Summer | 2 | 15.49 | -8.4 | 18.49 | 100 | 0 | 0 | 120 | 120 | 8.4 | 45 | 60.46 | 75 | 0 | 0 | 0 | Normal
2025-02-28 03:00 | 59 | 2 | Summer | 3 | 15.49 | -0.6 | 14.63 | 54.9 | 0 | 0 | 120 | 120 | 0.6 | 45 | 88.06 | 75 | 0 | 0 | 0 | Normal
2025-02-28 04:00 | 59 | 2 | Summer | 4 | 15.49 | -3.7 | 9.88 | 51.1 | 0 | 0 | 36.35 | 36.35 | 3.7 | 45 | 84.6 | -8.65 | 0 | 0 | 0 | Battery-supported
2025-02-28 05:00 | 59 | 2 | Summer | 5 | 15.49 | -5.7 | 9.79 | 62.4 | 52.5 | 3.15 | 34.83 | 37.98 | 5.7 | 45 | 81.79 | -7.02 | 0 | 0 | 0 | Battery-supported
2025-02-28 06:00 | 59 | 2 | Summer | 6 | 15.49 | -4.3 | 4.37 | 39.3 | 160.3 | 9.62 | 0.09 | 9.71 | 4.3 | 45 | 67.67 | -35.29 | 0 | 0 | 0 | Battery-supported
2025-02-28 07:00 | 59 | 2 | Summer | 7 | 15.49 | -8.8 | 15.63 | 47.8 | 222.4 | 13.34 | 120 | 133.34 | 8.8 | 45 | 95 | 74.26 | 0 | 0 | 0 | Normal
2025-02-28 08:00 | 59 | 2 | Summer | 8 | 15.49 | -3.2 | 5.87 | 32.7 | 340.9 | 20.45 | 1.86 | 22.31 | 3.2 | 46.67 | 85.26 | -24.36 | 0 | 0 | 0 | Battery-supported
2025-02-28 09:00 | 59 | 2 | Summer | 9 | 15.49 | -6.4 | 4.67 | 42.3 | 367.3 | 22.04 | 0.22 | 22.26 | 6.4 | 46.36 | 75.62 | -24.1 | 0 | 0 | 0 | Battery-supported
2025-02-28 10:00 | 59 | 2 | Summer | 10 | 15.49 | -6 | 13.45 | 77.4 | 252.8 | 15.17 | 120 | 135.17 | 6 | 49.67 | 95 | 52.67 | 0 | 0 | 0 | Normal
2025-02-28 11:00 | 59 | 2 | Summer | 11 | 15.49 | -6.4 | 5.51 | 21.8 | 537.4 | 32.24 | 1.14 | 33.38 | 6.4 | 55.13 | 86.3 | -21.75 | 0 | 0 | 0 | Battery-supported
2025-02-28 12:00 | 59 | 2 | Summer | 12 | 15.49 | -6.3 | 4.8 | 51.7 | 401.6 | 24.1 | 0.31 | 24.41 | 6.3 | 51.57 | 75.44 | -27.16 | 0 | 0 | 0 | Battery-supported
2025-02-28 13:00 | 59 | 2 | Summer | 13 | 15.49 | -3.1 | 11.58 | 11.8 | 585.7 | 35.14 | 73.83 | 108.97 | 3.1 | 45 | 95 | 53.16 | 0 | 0 | 0 | Normal
2025-02-28 14:00 | 59 | 2 | Summer | 14 | 15.49 | -3.7 | 3.13 | 42.2 | 412.1 | 24.73 | 0 | 24.73 | 3.7 | 45.36 | 86.75 | -20.63 | 0 | 0 | 0 | Battery-supported
2025-02-28 15:00 | 59 | 2 | Summer | 15 | 15.49 | -2.5 | 9.95 | 59.1 | 299.7 | 17.98 | 37.56 | 55.54 | 2.5 | 45 | 90.63 | 10.54 | 0 | 0 | 0 | Normal
2025-02-28 16:00 | 59 | 2 | Summer | 16 | 15.49 | -3.6 | 7.64 | 66.6 | 226 | 13.56 | 9.93 | 23.49 | 3.6 | 50.12 | 79.97 | -26.63 | 0 | 0 | 0 | Battery-supported
2025-02-28 17:00 | 59 | 2 | Summer | 17 | 15.49 | -2.1 | 11.02 | 24.4 | 283.3 | 17 | 59.52 | 76.52 | 2.1 | 45 | 91.57 | 31.52 | 0 | 0 | 0 | Normal
2025-02-28 18:00 | 59 | 2 | Summer | 18 | 15.49 | -3.9 | 9.31 | 41.9 | 155.9 | 9.35 | 27.45 | 36.8 | 3.9 | 47.62 | 87.25 | -10.82 | 0 | 0 | 0 | Battery-supported
2025-02-28 19:00 | 59 | 2 | Summer | 19 | 15.49 | 2.1 | 25.18 | 65.6 | 50.2 | 3.01 | 120 | 123.01 | 0 | 45 | 95 | 21.07 | 0 | 0 | 0 | Normal
2025-02-28 20:00 | 59 | 2 | Summer | 20 | 15.49 | -6.2 | 8.08 | 18.5 | 0 | 0 | 13.45 | 13.45 | 6.2 | 46.08 | 81.95 | -32.63 | 0 | 0 | 0 | Battery-supported
2025-02-28 21:00 | 59 | 2 | Summer | 21 | 15.49 | -0.1 | 5.5 | 25.9 | 0 | 0 | 1.12 | 1.12 | 0.1 | 45 | 64.4 | -43.88 | 0 | 0 | 0 | Battery-supported
2025-02-28 22:00 | 59 | 2 | Summer | 22 | 15.49 | 0 | 7.13 | 36.1 | 0 | 0 | 6.69 | 6.69 | 0 | 45 | 49.07 | -38.31 | 0 | 0 | 0 | Battery-supported
2025-02-28 23:00 | 59 | 2 | Summer | 23 | 15.49 | -5.1 | 9.25 | 54.4 | 0 | 0 | 26.61 | 26.61 | 5.1 | 45 | 41.72 | -18.39 | 0 | 0 | 0 | Battery-supported
2025-03-01 | 60 | 3 | Autumn | 0 | 15.33 | 1.2 | 17.96 | 53.7 | 0 | 0 | 120 | 120 | 0 | 45 | 69.32 | 75 | 0 | 0 | 0 | Normal
2025-03-01 01:00 | 60 | 3 | Autumn | 1 | 15.33 | -1.8 | 10.36 | 55.4 | 0 | 0 | 45.18 | 45.18 | 1.8 | 45 | 69.38 | 0.18 | 0 | 0 | 0 | Normal
2025-03-01 02:00 | 60 | 3 | Autumn | 2 | 15.33 | -2.3 | 4.23 | 15.9 | 0 | 0 | 0.05 | 0.05 | 2.3 | 45 | 51.4 | -44.95 | 0 | 0 | 0 | Battery-supported
2025-03-01 03:00 | 60 | 3 | Autumn | 3 | 15.33 | -4.8 | 45 | 5.7 | 0 | 0 | 0 | 0 | 4.8 | 45 | 33.4 | -45 | 0 | 0 | 0 | Battery-supported
2025-03-01 04:00 | 60 | 3 | Autumn | 4 | 15.33 | -5.7 | 12.76 | 90.1 | 0 | 0 | 111.13 | 111.13 | 5.7 | 45 | 57.74 | 66.13 | 0 | 0 | 0 | Normal
2025-03-01 05:00 | 60 | 3 | Autumn | 5 | 15.33 | -5.9 | 4.06 | 26.9 | 71 | 4.26 | 0.02 | 4.28 | 5.9 | 45 | 41.45 | -40.72 | 0 | 0 | 0 | Battery-supported
2025-03-01 06:00 | 60 | 3 | Autumn | 6 | 15.33 | -4.9 | 3.34 | 14.3 | 196 | 11.76 | 0 | 11.76 | 4.9 | 45 | 28.15 | -33.24 | 0 | 0 | 0 | Battery-supported
2025-03-01 07:00 | 60 | 3 | Autumn | 7 | 15.33 | -2.8 | 2.91 | 37.9 | 243.7 | 14.62 | 0 | 14.62 | 2.8 | 45 | 16 | -30.38 | 0 | 0 | 0 | Battery-supported
2025-03-01 08:00 | 60 | 3 | Autumn | 8 | 15.33 | -5.5 | 6.92 | 73.8 | 200 | 12 | 5.6 | 17.6 | 5.5 | 52.42 | 15 | -2.51 | 32.31 | 10.865 | 0 | Diesel-backup
2025-03-01 09:00 | 60 | 3 | Autumn | 9 | 15.33 | -7.9 | 7.11 | 95.8 | 151 | 9.06 | 6.58 | 15.64 | 7.9 | 53.18 | 15 | 0 | 37.54 | 12.371 | 0 | Diesel-backup
2025-03-01 10:00 | 60 | 3 | Autumn | 10 | 15.33 | -3.9 | 4.61 | 79.5 | 242.7 | 14.56 | 0.19 | 14.75 | 3.9 | 45.13 | 15 | 0 | 30.38 | 10.29 | 0 | Diesel-backup
2025-03-01 11:00 | 60 | 3 | Autumn | 11 | 15.33 | -3.5 | 2.6 | 25 | 521.8 | 31.31 | 0 | 31.31 | 3.5 | 50.69 | 15 | 0 | 19.38 | 6.837 | 0 | Diesel-backup
2025-03-01 12:00 | 60 | 3 | Autumn | 12 | 15.33 | -3.7 | 3.39 | 64.7 | 337.5 | 20.25 | 0 | 20.25 | 3.7 | 47.94 | 15 | 0 | 27.69 | 9.474 | 0 | Diesel-backup
2025-03-01 13:00 | 60 | 3 | Autumn | 13 | 15.33 | -3.2 | 10.49 | 16.5 | 562.7 | 33.76 | 47.8 | 81.56 | 3.2 | 51.31 | 26.13 | 30.25 | 0 | 0 | 0 | Normal
2025-03-01 14:00 | 60 | 3 | Autumn | 14 | 15.33 | -5 | 5.95 | 13.6 | 540.2 | 32.41 | 2.06 | 34.47 | 5 | 45 | 21.92 | -10.53 | 0 | 0 | 0 | Battery-supported
2025-03-01 15:00 | 60 | 3 | Autumn | 15 | 15.33 | -6.1 | 3.67 | 59.2 | 297.7 | 17.86 | 0 | 17.86 | 6.1 | 46.37 | 15 | -17.3 | 11.21 | 4.072 | 0 | Diesel-backup
2025-03-01 16:00 | 60 | 3 | Autumn | 16 | 15.33 | -5.6 | 7.65 | 60.8 | 243.6 | 14.62 | 10 | 24.62 | 5.6 | 50.8 | 15 | 0 | 26.18 | 9.008 | 0 | Diesel-backup
2025-03-01 17:00 | 60 | 3 | Autumn | 17 | 15.33 | -7 | 8.55 | 82.6 | 129.6 | 7.78 | 18.03 | 25.81 | 7 | 50.27 | 15 | 0 | 24.46 | 8.47 | 0 | Diesel-backup
2025-03-01 18:00 | 60 | 3 | Autumn | 18 | 15.33 | -2.6 | 9.12 | 25.1 | 178 | 10.68 | 24.84 | 35.52 | 2.6 | 45 | 15 | 0 | 9.48 | 3.465 | 0 | Diesel-backup
2025-03-01 19:00 | 60 | 3 | Autumn | 19 | 15.33 | -3.2 | 7.47 | 76 | 38.3 | 2.3 | 8.76 | 11.06 | 3.2 | 53.68 | 15 | 0 | 42.62 | 13.768 | 0 | Diesel-backup
2025-03-01 20:00 | 60 | 3 | Autumn | 20 | 15.33 | -3.9 | 6.78 | 75.9 | 0 | 0 | 4.94 | 4.94 | 3.9 | 53.91 | 15 | 0 | 48.97 | 15.67 | 0 | Diesel-backup
2025-03-01 21:00 | 60 | 3 | Autumn | 21 | 15.33 | -9.5 | 14.14 | 73 | 0 | 0 | 120 | 120 | 9.5 | 45.27 | 42.5 | 74.73 | 0 | 0 | 0 | Normal
2025-03-01 22:00 | 60 | 3 | Autumn | 22 | 15.33 | -5.9 | 3.49 | 29.8 | 0 | 0 | 0 | 0 | 5.9 | 45 | 24.5 | -45 | 0 | 0 | 0 | Battery-supported
2025-03-01 23:00 | 60 | 3 | Autumn | 23 | 15.33 | -0.9 | 6.23 | 65.9 | 0 | 0 | 2.85 | 2.85 | 0.9 | 45 | 15 | -23.75 | 18.4 | 6.514 | 0 | Diesel-backup
2025-03-02 | 61 | 3 | Autumn | 0 | 15.17 | -5.3 | 1.71 | 72.8 | 0 | 0 | 0 | 0 | 5.3 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-03-02 01:00 | 61 | 3 | Autumn | 1 | 15.17 | -3.4 | 5.74 | 31.3 | 0 | 0 | 1.57 | 1.57 | 3.4 | 45 | 15 | 0 | 43.43 | 13.985 | 0 | Diesel-backup
2025-03-02 02:00 | 61 | 3 | Autumn | 2 | 15.17 | -7.6 | 8 | 94.6 | 0 | 0 | 12.75 | 12.75 | 7.6 | 53.18 | 15 | 0 | 40.43 | 13.174 | 0 | Diesel-backup
2025-03-02 03:00 | 61 | 3 | Autumn | 3 | 15.17 | -1.8 | 11.58 | 26.5 | 0 | 0 | 73.83 | 73.83 | 1.8 | 45 | 25.61 | 28.83 | 0 | 0 | 0 | Normal
2025-03-02 04:00 | 61 | 3 | Autumn | 4 | 15.17 | -5.6 | 1.75 | 17.8 | 0 | 0 | 0 | 0 | 5.6 | 45 | 15 | -26.52 | 18.48 | 6.54 | 0 | Diesel-backup
2025-03-02 05:00 | 61 | 3 | Autumn | 5 | 15.17 | -5 | 7.86 | 22.8 | 65.6 | 3.94 | 11.6 | 15.54 | 5 | 45 | 15 | 0 | 29.46 | 10.013 | 0 | Diesel-backup
2025-03-02 06:00 | 61 | 3 | Autumn | 6 | 15.17 | -0.8 | 19.54 | 16.4 | 185.4 | 11.12 | 120 | 131.12 | 0.8 | 45 | 46.69 | 86.12 | 0 | 0 | 0 | Normal
2025-03-02 07:00 | 61 | 3 | Autumn | 7 | 15.17 | -2.7 | 9.56 | 70.1 | 158.7 | 9.52 | 31.15 | 40.67 | 2.7 | 45 | 44.96 | -4.33 | 0 | 0 | 0 | Battery-supported
2025-03-02 08:00 | 61 | 3 | Autumn | 8 | 15.17 | -6.7 | 3.06 | 17.6 | 384.9 | 23.09 | 0 | 23.09 | 6.7 | 45 | 36.2 | -21.91 | 0 | 0 | 0 | Battery-supported
2025-03-02 09:00 | 61 | 3 | Autumn | 9 | 15.17 | -7.3 | 5.74 | 35.9 | 389.6 | 23.38 | 1.57 | 24.95 | 7.3 | 49.37 | 26.43 | -24.42 | 0 | 0 | 0 | Battery-supported
2025-03-02 10:00 | 61 | 3 | Autumn | 10 | 15.17 | -6.6 | 9.74 | 28.9 | 470.5 | 28.23 | 34.01 | 62.24 | 6.6 | 50.84 | 30.62 | 11.4 | 0 | 0 | 0 | Normal
2025-03-02 11:00 | 61 | 3 | Autumn | 11 | 15.17 | -4.5 | 4.77 | 79.5 | 259.2 | 15.55 | 0.29 | 15.84 | 4.5 | 54.36 | 15.22 | -38.52 | 0 | 0 | 0 | Battery-supported
2025-03-02 12:00 | 61 | 3 | Autumn | 12 | 15.17 | -5.6 | 8.42 | 68.5 | 319 | 19.14 | 16.67 | 35.81 | 5.6 | 45 | 15 | -0.54 | 8.65 | 3.171 | 0 | Diesel-backup
2025-03-02 13:00 | 61 | 3 | Autumn | 13 | 15.17 | -5.8 | 8.12 | 37.5 | 461.3 | 27.68 | 13.8 | 41.48 | 5.8 | 53.32 | 15 | 0 | 11.84 | 4.291 | 0 | Diesel-backup
2025-03-02 14:00 | 61 | 3 | Autumn | 14 | 15.17 | -1.3 | 6.88 | 1.1 | 595.5 | 35.73 | 5.4 | 41.13 | 1.3 | 45 | 15 | 0 | 3.87 | 1.442 | 0 | Diesel-backup
2025-03-02 15:00 | 61 | 3 | Autumn | 15 | 15.17 | -4.4 | 2.82 | 55.7 | 310.5 | 18.63 | 0 | 18.63 | 4.4 | 46.42 | 15 | 0 | 27.79 | 9.505 | 0 | Diesel-backup
2025-03-02 16:00 | 61 | 3 | Autumn | 16 | 15.17 | 1.2 | 4.43 | 73.6 | 198.6 | 11.92 | 0.11 | 12.03 | 0 | 45 | 15 | 0 | 32.97 | 11.058 | 0 | Diesel-backup
2025-03-02 17:00 | 61 | 3 | Autumn | 17 | 15.17 | -3.3 | 20.67 | 32 | 254.1 | 15.25 | 120 | 135.25 | 3.3 | 47.87 | 47.16 | 87.38 | 0 | 0 | 0 | Normal
2025-03-02 18:00 | 61 | 3 | Autumn | 18 | 15.17 | 0.7 | 5.5 | 64.2 | 109.6 | 6.58 | 1.12 | 7.7 | 0 | 45 | 32.24 | -37.3 | 0 | 0 | 0 | Battery-supported
2025-03-02 19:00 | 61 | 3 | Autumn | 19 | 15.17 | -2.3 | 5.94 | 42 | 54.1 | 3.25 | 2.03 | 5.28 | 2.3 | 54.37 | 15 | -43.09 | 6 | 2.22 | 0 | Diesel-backup
2025-03-02 20:00 | 61 | 3 | Autumn | 20 | 15.17 | -1 | 5.92 | 88.4 | 0 | 0 | 1.98 | 1.98 | 1 | 45 | 15 | 0 | 43.02 | 13.875 | 0 | Diesel-backup
2025-03-02 21:00 | 61 | 3 | Autumn | 21 | 15.17 | -4.7 | 11.41 | 72.2 | 0 | 0 | 69.27 | 69.27 | 4.7 | 45.91 | 23.6 | 23.36 | 0 | 0 | 0 | Normal
2025-03-02 22:00 | 61 | 3 | Autumn | 22 | 15.17 | -5.1 | 6.13 | 51 | 0 | 0 | 2.55 | 2.55 | 5.1 | 45 | 15 | -21.49 | 20.96 | 7.352 | 0 | Diesel-backup
2025-03-02 23:00 | 61 | 3 | Autumn | 23 | 15.17 | -2.5 | 6.98 | 82.7 | 0 | 0 | 5.9 | 5.9 | 2.5 | 45 | 15 | 0 | 39.1 | 12.807 | 0 | Diesel-backup
2025-03-03 | 62 | 3 | Autumn | 0 | 15.01 | -1.8 | 7.89 | 5.4 | 0 | 0 | 11.84 | 11.84 | 1.8 | 45 | 15 | 0 | 33.16 | 11.114 | 0 | Diesel-backup
2025-03-03 01:00 | 62 | 3 | Autumn | 1 | 15.01 | -4.2 | 12.2 | 80.5 | 0 | 0 | 92.17 | 92.17 | 4.2 | 45 | 32.36 | 47.17 | 0 | 0 | 0 | Normal
2025-03-03 02:00 | 62 | 3 | Autumn | 2 | 15.01 | -7.5 | 7.02 | 54.6 | 0 | 0 | 6.1 | 6.1 | 7.5 | 45 | 16.8 | -38.9 | 0 | 0 | 0 | Battery-supported
2025-03-03 03:00 | 62 | 3 | Autumn | 3 | 15.01 | -8.1 | 7.5 | 78.7 | 0 | 0 | 8.96 | 8.96 | 8.1 | 45 | 15 | -4.5 | 31.54 | 10.637 | 0 | Diesel-backup
2025-03-03 04:00 | 62 | 3 | Autumn | 4 | 15.01 | -8.6 | 4.94 | 44.8 | 0 | 0 | 0.42 | 0.42 | 8.6 | 45 | 15 | 0 | 44.58 | 14.29 | 0 | Diesel-backup
2025-03-03 05:00 | 62 | 3 | Autumn | 5 | 15.01 | -9.7 | 8.56 | 63.9 | 35.9 | 2.15 | 18.13 | 20.28 | 9.7 | 45.64 | 15 | 0 | 25.36 | 8.753 | 0 | Diesel-backup
2025-03-03 06:00 | 62 | 3 | Autumn | 6 | 15.01 | -5.8 | 10.05 | 34.2 | 151 | 9.06 | 39.33 | 48.39 | 5.8 | 45 | 16.25 | 3.39 | 0 | 0 | 0 | Normal
2025-03-03 07:00 | 62 | 3 | Autumn | 7 | 15.01 | -3.7 | 10.46 | 47.2 | 212 | 12.72 | 47.19 | 59.91 | 3.7 | 45 | 21.73 | 14.91 | 0 | 0 | 0 | Normal
2025-03-03 08:00 | 62 | 3 | Autumn | 8 | 15.01 | -6.2 | 18.93 | 44.6 | 292 | 17.52 | 120 | 137.52 | 6.2 | 45.38 | 55.64 | 92.14 | 0 | 0 | 0 | Normal
2025-03-03 09:00 | 62 | 3 | Autumn | 9 | 15.01 | -11.1 | 4.24 | 6.5 | 505 | 30.3 | 0.06 | 30.36 | 11.1 | 53.56 | 46.36 | -23.2 | 0 | 0 | 0 | Battery-supported
2025-03-03 10:00 | 62 | 3 | Autumn | 10 | 15.01 | -6.4 | 7.2 | 92.9 | 181.5 | 10.89 | 7.09 | 17.98 | 6.4 | 51.39 | 33 | -33.41 | 0 | 0 | 0 | Battery-supported
2025-03-03 11:00 | 62 | 3 | Autumn | 11 | 15.01 | -6.1 | 6.17 | 81.6 | 248.8 | 14.93 | 2.66 | 17.59 | 6.1 | 54.73 | 18.14 | -37.14 | 0 | 0 | 0 | Battery-supported
2025-03-03 12:00 | 62 | 3 | Autumn | 12 | 15.01 | -0.9 | 17.01 | 53.9 | 390.7 | 23.44 | 120 | 143.44 | 0.9 | 45 | 54.37 | 98.44 | 0 | 0 | 0 | Normal
2025-03-03 13:00 | 62 | 3 | Autumn | 13 | 15.01 | -8.3 | 10.7 | 11.8 | 584.7 | 35.08 | 52.24 | 87.32 | 8.3 | 56.49 | 65.71 | 30.83 | 0 | 0 | 0 | Normal
2025-03-03 14:00 | 62 | 3 | Autumn | 14 | 15.01 | -5.6 | 2.25 | 38.4 | 426.7 | 25.6 | 0 | 25.6 | 5.6 | 48.55 | 56.53 | -22.95 | 0 | 0 | 0 | Battery-supported
2025-03-03 15:00 | 62 | 3 | Autumn | 15 | 15.01 | -0.6 | 4.67 | 64.2 | 275.2 | 16.51 | 0.22 | 16.73 | 0.6 | 45 | 45.23 | -28.27 | 0 | 0 | 0 | Battery-supported
2025-03-03 16:00 | 62 | 3 | Autumn | 16 | 15.01 | -3 | 5.71 | 8.4 | 411.5 | 24.69 | 1.51 | 26.2 | 3 | 54.33 | 33.97 | -28.13 | 0 | 0 | 0 | Battery-supported
2025-03-03 17:00 | 62 | 3 | Autumn | 17 | 15.01 | -2.4 | 2.5 | 36.6 | 238 | 14.28 | 0 | 14.28 | 2.4 | 45 | 21.69 | -30.72 | 0 | 0 | 0 | Battery-supported
2025-03-03 18:00 | 62 | 3 | Autumn | 18 | 15.01 | -3.2 | 7.54 | 51.6 | 124.4 | 7.46 | 9.23 | 16.69 | 3.2 | 49.99 | 15 | -16.71 | 16.59 | 5.911 | 0 | Diesel-backup
2025-03-03 19:00 | 62 | 3 | Autumn | 19 | 15.01 | -2.5 | 5.08 | 89.3 | 22.8 | 1.37 | 0.55 | 1.92 | 2.5 | 45 | 15 | 0 | 43.08 | 13.891 | 0 | Diesel-backup
2025-03-03 20:00 | 62 | 3 | Autumn | 20 | 15.01 | -1.5 | 19.4 | 66.4 | 0 | 0 | 120 | 120 | 1.5 | 46.58 | 42.02 | 73.42 | 0 | 0 | 0 | Normal
2025-03-03 21:00 | 62 | 3 | Autumn | 21 | 15.01 | -5 | 8.52 | 5.1 | 0 | 0 | 17.71 | 17.71 | 5 | 45 | 31.1 | -27.29 | 0 | 0 | 0 | Battery-supported
2025-03-03 22:00 | 62 | 3 | Autumn | 22 | 15.01 | -1.5 | 5.57 | 100 | 0 | 0 | 1.24 | 1.24 | 1.5 | 45 | 15 | -40.26 | 3.5 | 1.307 | 0 | Diesel-backup
2025-03-03 23:00 | 62 | 3 | Autumn | 23 | 15.01 | -6.7 | 3.68 | 67.7 | 0 | 0 | 0 | 0 | 6.7 | 49.82 | 15 | 0 | 49.82 | 15.942 | 0 | Diesel-backup
2025-03-04 | 63 | 3 | Autumn | 0 | 14.85 | -3.4 | 6.85 | 36.5 | 0 | 0 | 5.26 | 5.26 | 3.4 | 45 | 15 | 0 | 39.74 | 12.984 | 0 | Diesel-backup
2025-03-04 01:00 | 63 | 3 | Autumn | 1 | 14.85 | -4.1 | 16.23 | 60.8 | 0 | 0 | 120 | 120 | 4.1 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-03-04 02:00 | 63 | 3 | Autumn | 2 | 14.85 | -6.2 | 6.24 | 28.4 | 0 | 0 | 2.88 | 2.88 | 6.2 | 47.5 | 24.75 | -44.62 | 0 | 0 | 0 | Battery-supported
2025-03-04 03:00 | 63 | 3 | Autumn | 3 | 14.85 | -5.3 | 6.88 | 0 | 0 | 0 | 5.4 | 5.4 | 5.3 | 45 | 15 | -24.38 | 15.22 | 5.451 | 0 | Diesel-backup
2025-03-04 04:00 | 63 | 3 | Autumn | 4 | 14.85 | -7 | 13.21 | 30.1 | 0 | 0 | 120 | 120 | 7 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-03-04 05:00 | 63 | 3 | Autumn | 5 | 14.85 | -8.3 | 8.4 | 40.6 | 40.8 | 2.45 | 16.47 | 18.92 | 8.3 | 46.82 | 31.44 | -27.9 | 0 | 0 | 0 | Battery-supported
2025-03-04 06:00 | 63 | 3 | Autumn | 6 | 14.85 | -6.9 | 11.35 | 46.9 | 126 | 7.56 | 67.7 | 75.26 | 6.9 | 45 | 42.58 | 30.26 | 0 | 0 | 0 | Normal
2025-03-04 07:00 | 63 | 3 | Autumn | 7 | 14.85 | -8.7 | 8.91 | 12.1 | 292.6 | 17.56 | 22.16 | 39.72 | 8.7 | 45 | 40.46 | -5.28 | 0 | 0 | 0 | Battery-supported
2025-03-04 08:00 | 63 | 3 | Autumn | 8 | 14.85 | -5.7 | 8.61 | 55.7 | 253.1 | 15.19 | 18.68 | 33.87 | 5.7 | 50.27 | 33.9 | -16.4 | 0 | 0 | 0 | Battery-supported
2025-03-04 09:00 | 63 | 3 | Autumn | 9 | 14.85 | -8.8 | 2.16 | 75.8 | 228 | 13.68 | 0 | 13.68 | 8.8 | 56.07 | 16.95 | -42.39 | 0 | 0 | 0 | Battery-supported
2025-03-04 10:00 | 63 | 3 | Autumn | 10 | 14.85 | -4.6 | 3.34 | 53.4 | 358.5 | 21.51 | 0 | 21.51 | 4.6 | 45 | 15 | -4.87 | 18.62 | 6.587 | 0 | Diesel-backup
2025-03-04 11:00 | 63 | 3 | Autumn | 11 | 14.85 | -8.5 | 7.87 | 40.7 | 445.8 | 26.75 | 11.68 | 38.43 | 8.5 | 51.15 | 15 | 0 | 12.72 | 4.596 | 0 | Diesel-backup
2025-03-04 12:00 | 63 | 3 | Autumn | 12 | 14.85 | -6.9 | 3.93 | 37.2 | 472.9 | 28.37 | 0.01 | 28.38 | 6.9 | 50.05 | 15 | 0 | 21.67 | 7.582 | 0 | Diesel-backup
2025-03-04 13:00 | 63 | 3 | Autumn | 13 | 14.85 | -6.6 | 6.85 | 30.2 | 496 | 29.76 | 5.26 | 35.02 | 6.6 | 50.83 | 15 | 0 | 15.81 | 5.65 | 0 | Diesel-backup
2025-03-04 14:00 | 63 | 3 | Autumn | 14 | 14.85 | -2 | 3.13 | 77.6 | 250 | 15 | 0 | 15 | 2 | 47.58 | 15 | 0 | 32.58 | 10.944 | 0 | Diesel-backup
2025-03-04 15:00 | 63 | 3 | Autumn | 15 | 14.85 | -3.8 | 13.28 | 58 | 298.2 | 17.89 | 120 | 137.89 | 3.8 | 45 | 49.18 | 92.89 | 0 | 0 | 0 | Normal
2025-03-04 16:00 | 63 | 3 | Autumn | 16 | 14.85 | -4.6 | 4.25 | 65.8 | 220.2 | 13.21 | 0.06 | 13.27 | 4.6 | 49.74 | 34.6 | -36.47 | 0 | 0 | 0 | Battery-supported
2025-03-04 17:00 | 63 | 3 | Autumn | 17 | 14.85 | -2.7 | 3.68 | 91.3 | 101.4 | 6.08 | 0 | 6.08 | 2.7 | 45 | 19.03 | -38.92 | 0 | 0 | 0 | Battery-supported
2025-03-04 18:00 | 63 | 3 | Autumn | 18 | 14.85 | -8.2 | 2.64 | 24.7 | 158.5 | 9.51 | 0 | 9.51 | 8.2 | 51.05 | 15 | -10.07 | 31.47 | 10.616 | 0 | Diesel-backup
2025-03-04 19:00 | 63 | 3 | Autumn | 19 | 14.85 | -3.5 | 10.43 | 35.1 | 43.2 | 2.59 | 46.58 | 49.17 | 3.5 | 45 | 16.53 | 4.17 | 0 | 0 | 0 | Normal
2025-03-04 20:00 | 63 | 3 | Autumn | 20 | 14.85 | 1 | 6.85 | 58.4 | 0 | 0 | 5.26 | 5.26 | 0 | 45 | 15 | -3.84 | 35.9 | 11.907 | 0 | Diesel-backup
2025-03-04 21:00 | 63 | 3 | Autumn | 21 | 14.85 | -3.1 | 13 | 45.5 | 0 | 0 | 120 | 120 | 3.1 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-03-04 22:00 | 63 | 3 | Autumn | 22 | 14.85 | -3.4 | 4.98 | 26.5 | 0 | 0 | 0.45 | 0.45 | 3.4 | 45 | 24.78 | -44.55 | 0 | 0 | 0 | Battery-supported
2025-03-04 23:00 | 63 | 3 | Autumn | 23 | 14.85 | -2.6 | 3.28 | 35.9 | 0 | 0 | 0 | 0 | 2.6 | 45 | 15 | -24.45 | 20.55 | 7.219 | 0 | Diesel-backup
2025-03-05 | 64 | 3 | Autumn | 0 | 14.69 | -2.3 | 6.68 | 60.9 | 0 | 0 | 4.5 | 4.5 | 2.3 | 45 | 15 | 0 | 40.5 | 13.193 | 0 | Diesel-backup
2025-03-05 01:00 | 64 | 3 | Autumn | 1 | 14.69 | -9 | 14.53 | 67.3 | 0 | 0 | 120 | 120 | 9 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-03-05 02:00 | 64 | 3 | Autumn | 2 | 14.69 | -8.7 | 2.13 | 4.1 | 0 | 0 | 0 | 0 | 8.7 | 45 | 24.6 | -45 | 0 | 0 | 0 | Battery-supported
2025-03-05 03:00 | 64 | 3 | Autumn | 3 | 14.69 | -4.9 | 8.31 | 55.1 | 0 | 0 | 15.58 | 15.58 | 4.9 | 45 | 15 | -24 | 5.42 | 2.009 | 0 | Diesel-backup
2025-03-05 04:00 | 64 | 3 | Autumn | 4 | 14.69 | -7.3 | 8.82 | 75.5 | 0 | 0 | 21.07 | 21.07 | 7.3 | 45 | 15 | 0 | 23.93 | 8.303 | 0 | Diesel-backup
2025-03-05 05:00 | 64 | 3 | Autumn | 5 | 14.69 | -3.2 | 15.9 | 36.1 | 35.1 | 2.11 | 120 | 122.11 | 3.2 | 45 | 43.38 | 77.11 | 0 | 0 | 0 | Normal
2025-03-05 06:00 | 64 | 3 | Autumn | 6 | 14.69 | -7 | 4.05 | 58.6 | 104.1 | 6.25 | 0.02 | 6.27 | 7 | 45 | 27.88 | -38.73 | 0 | 0 | 0 | Battery-supported
2025-03-05 07:00 | 64 | 3 | Autumn | 7 | 14.69 | -10.7 | 2.02 | 37.6 | 226.4 | 13.58 | 0 | 13.58 | 10.7 | 49.38 | 15 | -32.21 | 3.59 | 1.339 | 0 | Diesel-backup
2025-03-05 08:00 | 64 | 3 | Autumn | 8 | 14.69 | -9.3 | 5.32 | 25.5 | 348 | 20.88 | 0.84 | 21.72 | 9.3 | 50.3 | 15 | 0 | 28.58 | 9.746 | 0 | Diesel-backup
2025-03-05 09:00 | 64 | 3 | Autumn | 9 | 14.69 | -12.5 | 11.29 | 43.6 | 353.6 | 21.22 | 66.16 | 87.38 | 12.5 | 58.44 | 25.65 | 28.94 | 0 | 0 | 0 | Normal
2025-03-05 10:00 | 64 | 3 | Autumn | 10 | 14.69 | -6.8 | 7.14 | 45.3 | 394.1 | 23.65 | 6.75 | 30.4 | 6.8 | 52.3 | 16.89 | -21.9 | 0 | 0 | 0 | Battery-supported
2025-03-05 11:00 | 64 | 3 | Autumn | 11 | 14.69 | -6.5 | 9.37 | 32.6 | 484.4 | 29.06 | 28.31 | 57.37 | 6.5 | 46.78 | 20.79 | 10.59 | 0 | 0 | 0 | Normal
2025-03-05 12:00 | 64 | 3 | Autumn | 12 | 14.69 | -6.7 | 3.43 | 28.4 | 516 | 30.96 | 0 | 30.96 | 6.7 | 45 | 15.17 | -14.04 | 0 | 0 | 0 | Battery-supported
2025-03-05 13:00 | 64 | 3 | Autumn | 13 | 14.69 | -3 | 6.02 | 81.7 | 248.2 | 14.89 | 2.24 | 17.13 | 3 | 51.07 | 15 | -0.43 | 33.51 | 11.217 | 0 | Diesel-backup
2025-03-05 14:00 | 64 | 3 | Autumn | 14 | 14.69 | -2.4 | 7.3 | 72.6 | 271.7 | 16.3 | 7.68 | 23.98 | 2.4 | 45 | 15 | 0 | 21.02 | 7.372 | 0 | Diesel-backup
2025-03-05 15:00 | 64 | 3 | Autumn | 15 | 14.69 | -5 | 2.37 | 54.8 | 309.4 | 18.56 | 0 | 18.56 | 5 | 45.42 | 15 | 0 | 26.86 | 9.219 | 0 | Diesel-backup
2025-03-05 16:00 | 64 | 3 | Autumn | 16 | 14.69 | -9 | 7.28 | 57.7 | 243.8 | 14.63 | 7.56 | 22.19 | 9 | 50.8 | 15 | 0 | 28.61 | 9.755 | 0 | Diesel-backup
2025-03-05 17:00 | 64 | 3 | Autumn | 17 | 14.69 | -2.6 | 5.67 | 24 | 258.5 | 15.51 | 1.43 | 16.94 | 2.6 | 45 | 15 | 0 | 28.06 | 9.588 | 0 | Diesel-backup
2025-03-05 18:00 | 64 | 3 | Autumn | 18 | 14.69 | -2.5 | 28.51 | 30.1 | 143.8 | 8.63 | 0 | 8.63 | 2.5 | 48.02 | 15 | 0 | 39.39 | 12.888 | 0 | Diesel-backup
2025-03-05 19:00 | 64 | 3 | Autumn | 19 | 14.69 | -2.9 | 6.97 | 12 | 43.8 | 2.63 | 5.85 | 8.48 | 2.9 | 45.86 | 15 | 0 | 37.38 | 12.326 | 0 | Diesel-backup
2025-03-05 20:00 | 64 | 3 | Autumn | 20 | 14.69 | -1.4 | 16.4 | 40 | 0 | 0 | 120 | 120 | 1.4 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-03-05 21:00 | 64 | 3 | Autumn | 21 | 14.69 | -6.1 | 9.33 | 37.9 | 0 | 0 | 27.73 | 27.73 | 6.1 | 45.65 | 35.43 | -17.92 | 0 | 0 | 0 | Battery-supported
2025-03-05 22:00 | 64 | 3 | Autumn | 22 | 14.69 | 0.7 | 6.45 | 51.4 | 0 | 0 | 3.59 | 3.59 | 0 | 45 | 18.87 | -41.41 | 0 | 0 | 0 | Battery-supported
2025-03-05 23:00 | 64 | 3 | Autumn | 23 | 14.69 | -6.1 | 15.02 | 41.6 | 0 | 0 | 120 | 120 | 6.1 | 47.4 | 45.58 | 72.6 | 0 | 0 | 0 | Normal
2025-03-06 | 65 | 3 | Autumn | 0 | 14.53 | -2.8 | 3.1 | 67.8 | 0 | 0 | 0 | 0 | 2.8 | 45 | 27.58 | -45 | 0 | 0 | 0 | Battery-supported
2025-03-06 01:00 | 65 | 3 | Autumn | 1 | 14.53 | -8.5 | 5.26 | 26.9 | 0 | 0 | 0.76 | 0.76 | 8.5 | 45 | 15 | -31.46 | 12.78 | 4.616 | 0 | Diesel-backup
2025-03-06 02:00 | 65 | 3 | Autumn | 2 | 14.53 | -7.2 | 11.72 | 64.6 | 0 | 0 | 77.74 | 77.74 | 7.2 | 45 | 27.05 | 32.74 | 0 | 0 | 0 | Normal
2025-03-06 03:00 | 65 | 3 | Autumn | 3 | 14.53 | -2.2 | 1.22 | 41.1 | 0 | 0 | 0 | 0 | 2.2 | 45 | 15 | -30.12 | 14.88 | 5.335 | 0 | Diesel-backup
2025-03-06 04:00 | 65 | 3 | Autumn | 4 | 14.53 | -6.5 | 6.85 | 49.8 | 0 | 0 | 5.26 | 5.26 | 6.5 | 45 | 15 | 0 | 39.74 | 12.984 | 0 | Diesel-backup
2025-03-06 05:00 | 65 | 3 | Autumn | 5 | 14.53 | -4.4 | 6.81 | 46.8 | 24.3 | 1.46 | 5.08 | 6.54 | 4.4 | 45.49 | 15 | 0 | 38.95 | 12.766 | 0 | Diesel-backup
2025-03-06 06:00 | 65 | 3 | Autumn | 6 | 14.53 | -6 | 8.18 | 97.5 | 47.5 | 2.85 | 14.35 | 17.2 | 6 | 45 | 15 | 0 | 27.8 | 9.508 | 0 | Diesel-backup
2025-03-06 07:00 | 65 | 3 | Autumn | 7 | 14.53 | -6.9 | 6.08 | 78 | 128.1 | 7.69 | 2.4 | 10.09 | 6.9 | 45 | 15 | 0 | 34.91 | 11.622 | 0 | Diesel-backup
2025-03-06 08:00 | 65 | 3 | Autumn | 8 | 14.53 | -3.7 | 11.45 | 84.5 | 155.9 | 9.35 | 70.33 | 79.68 | 3.7 | 45.49 | 27.58 | 34.19 | 0 | 0 | 0 | Normal
2025-03-06 09:00 | 65 | 3 | Autumn | 9 | 14.53 | -7.1 | 4.21 | 53.3 | 313.8 | 18.83 | 0.05 | 18.88 | 7.1 | 52.28 | 15 | -31.45 | 1.95 | 0.73 | 0 | Diesel-backup
2025-03-06 10:00 | 65 | 3 | Autumn | 10 | 14.53 | -10.4 | 12.38 | 68.7 | 288.7 | 17.32 | 98.01 | 115.33 | 10.4 | 55.06 | 37.18 | 60.27 | 0 | 0 | 0 | Normal
2025-03-06 11:00 | 65 | 3 | Autumn | 11 | 14.53 | -8 | 3.37 | 29.9 | 497.1 | 29.83 | 0 | 29.83 | 8 | 54.19 | 27.44 | -24.36 | 0 | 0 | 0 | Battery-supported
2025-03-06 12:00 | 65 | 3 | Autumn | 12 | 14.53 | -4.7 | 8.57 | 66.8 | 327.2 | 19.63 | 18.24 | 37.87 | 4.7 | 45 | 24.58 | -7.13 | 0 | 0 | 0 | Battery-supported
2025-03-06 13:00 | 65 | 3 | Autumn | 13 | 14.53 | -4.7 | 14.05 | 61.4 | 345.7 | 20.74 | 120 | 140.74 | 4.7 | 56.7 | 55.51 | 84.04 | 0 | 0 | 0 | Normal
2025-03-06 14:00 | 65 | 3 | Autumn | 14 | 14.53 | -8.6 | 3.96 | 68 | 291.7 | 17.5 | 0.01 | 17.51 | 8.6 | 50.22 | 42.43 | -32.71 | 0 | 0 | 0 | Battery-supported
2025-03-06 15:00 | 65 | 3 | Autumn | 15 | 14.53 | -6.4 | 4.63 | 42 | 358 | 21.48 | 0.2 | 21.68 | 6.4 | 46.86 | 32.35 | -25.18 | 0 | 0 | 0 | Battery-supported
2025-03-06 16:00 | 65 | 3 | Autumn | 16 | 14.53 | -5.7 | 12.63 | 49.6 | 267.3 | 16.04 | 106.52 | 122.56 | 5.7 | 53.48 | 57.78 | 69.08 | 0 | 0 | 0 | Normal
2025-03-06 17:00 | 65 | 3 | Autumn | 17 | 14.53 | -4.9 | 7.84 | 34.4 | 228.8 | 13.73 | 11.44 | 25.17 | 4.9 | 51.51 | 47.24 | -26.34 | 0 | 0 | 0 | Battery-supported
2025-03-06 18:00 | 65 | 3 | Autumn | 18 | 14.53 | -6.9 | 2.04 | 28.9 | 138.7 | 8.32 | 0 | 8.32 | 6.9 | 47.32 | 31.64 | -39 | 0 | 0 | 0 | Battery-supported
2025-03-06 19:00 | 65 | 3 | Autumn | 19 | 14.53 | -5.1 | 8.02 | 28.3 | 29.5 | 1.77 | 12.92 | 14.69 | 5.1 | 50.81 | 17.19 | -36.12 | 0 | 0 | 0 | Battery-supported
2025-03-06 20:00 | 65 | 3 | Autumn | 20 | 14.53 | -5.3 | 10.34 | 54.8 | 0 | 0 | 44.79 | 44.79 | 5.3 | 46.6 | 16.47 | -1.81 | 0 | 0 | 0 | Battery-supported
2025-03-06 21:00 | 65 | 3 | Autumn | 21 | 14.53 | -2 | 12.93 | 34 | 0 | 0 | 117.37 | 117.37 | 2 | 45 | 43.1 | 72.37 | 0 | 0 | 0 | Normal
2025-03-06 22:00 | 65 | 3 | Autumn | 22 | 14.53 | -2.1 | 8.44 | 81.6 | 0 | 0 | 16.87 | 16.87 | 2.1 | 45 | 31.85 | -28.13 | 0 | 0 | 0 | Battery-supported
2025-03-06 23:00 | 65 | 3 | Autumn | 23 | 14.53 | -4.4 | 9.55 | 9.8 | 0 | 0 | 30.99 | 30.99 | 4.4 | 49.58 | 24.41 | -18.59 | 0 | 0 | 0 | Battery-supported
2025-03-07 | 66 | 3 | Autumn | 0 | 14.37 | -5.4 | 17.44 | 94 | 0 | 0 | 120 | 120 | 5.4 | 45.96 | 51.66 | 74.04 | 0 | 0 | 0 | Normal
2025-03-07 01:00 | 66 | 3 | Autumn | 1 | 14.37 | -4.6 | 11.96 | 98.9 | 0 | 0 | 84.75 | 84.75 | 4.6 | 45 | 66.29 | 39.75 | 0 | 0 | 0 | Normal
2025-03-07 02:00 | 66 | 3 | Autumn | 2 | 14.37 | -7.1 | 5.96 | 76.7 | 0 | 0 | 2.08 | 2.08 | 7.1 | 45.16 | 49.05 | -43.08 | 0 | 0 | 0 | Battery-supported
2025-03-07 03:00 | 66 | 3 | Autumn | 3 | 14.37 | -8.2 | 6.46 | 82.1 | 0 | 0 | 3.63 | 3.63 | 8.2 | 45 | 32.51 | -41.37 | 0 | 0 | 0 | Battery-supported
2025-03-07 04:00 | 66 | 3 | Autumn | 4 | 14.37 | -8.2 | 13.77 | 92.7 | 0 | 0 | 120 | 120 | 8.2 | 45 | 60.11 | 75 | 0 | 0 | 0 | Normal
2025-03-07 05:00 | 66 | 3 | Autumn | 5 | 14.37 | -7.8 | 8.37 | 44.5 | 17.6 | 1.06 | 16.17 | 17.23 | 7.8 | 45 | 49 | -27.77 | 0 | 0 | 0 | Battery-supported
2025-03-07 06:00 | 66 | 3 | Autumn | 6 | 14.37 | -9.2 | 7.64 | 68.1 | 82.2 | 4.93 | 9.93 | 14.86 | 9.2 | 45 | 36.94 | -30.14 | 0 | 0 | 0 | Battery-supported
2025-03-07 07:00 | 66 | 3 | Autumn | 7 | 14.37 | -6.4 | 5.84 | 26.4 | 241.8 | 14.51 | 1.79 | 16.3 | 6.4 | 45 | 25.46 | -28.7 | 0 | 0 | 0 | Battery-supported
2025-03-07 08:00 | 66 | 3 | Autumn | 8 | 14.37 | -5.2 | 13.47 | 84.3 | 154.6 | 9.28 | 120 | 129.28 | 5.2 | 45 | 56.48 | 84.28 | 0 | 0 | 0 | Normal
2025-03-07 09:00 | 66 | 3 | Autumn | 9 | 14.37 | -10.3 | 4.13 | 45.4 | 342.8 | 20.57 | 0.03 | 20.6 | 10.3 | 52.16 | 43.85 | -31.56 | 0 | 0 | 0 | Battery-supported
2025-03-07 10:00 | 66 | 3 | Autumn | 10 | 14.37 | -6.6 | 5.28 | 11.7 | 541.9 | 32.51 | 0.79 | 33.3 | 6.6 | 50.11 | 37.13 | -16.81 | 0 | 0 | 0 | Battery-supported
2025-03-07 11:00 | 66 | 3 | Autumn | 11 | 14.37 | -6.9 | 13.45 | 73.7 | 286.3 | 17.18 | 120 | 137.18 | 6.9 | 53.6 | 67.89 | 83.58 | 0 | 0 | 0 | Normal
2025-03-07 12:00 | 66 | 3 | Autumn | 12 | 14.37 | -5.3 | 13.35 | 82.6 | 249.4 | 14.96 | 120 | 134.96 | 5.3 | 45.17 | 95 | 73.68 | 0 | 0 | 0 | Normal
2025-03-07 13:00 | 66 | 3 | Autumn | 13 | 14.37 | -5.8 | 23.45 | 45.4 | 422.5 | 25.35 | 120 | 145.35 | 5.8 | 45.64 | 95 | 0 | 0 | 0 | 0 | Normal
2025-03-07 14:00 | 66 | 3 | Autumn | 14 | 14.37 | -8.5 | 6.88 | 35.8 | 434.8 | 26.09 | 5.4 | 31.49 | 8.5 | 48.07 | 88.37 | -16.58 | 0 | 0 | 0 | Battery-supported
2025-03-07 15:00 | 66 | 3 | Autumn | 15 | 14.37 | -7.7 | 5.9 | 74.5 | 229.6 | 13.78 | 1.93 | 15.71 | 7.7 | 49.43 | 74.88 | -33.72 | 0 | 0 | 0 | Battery-supported
2025-03-07 16:00 | 66 | 3 | Autumn | 16 | 14.37 | -4.5 | 6.28 | 84.4 | 154.2 | 9.25 | 3.01 | 12.26 | 4.5 | 45 | 61.78 | -32.74 | 0 | 0 | 0 | Battery-supported
2025-03-07 17:00 | 66 | 3 | Autumn | 17 | 14.37 | -2 | 2.25 | 16.5 | 264.3 | 15.86 | 0 | 15.86 | 2 | 50.31 | 48 | -34.45 | 0 | 0 | 0 | Battery-supported
2025-03-07 18:00 | 66 | 3 | Autumn | 18 | 14.37 | -8.9 | 1.41 | 33.5 | 125.8 | 7.55 | 0 | 7.55 | 8.9 | 55 | 29.02 | -47.45 | 0 | 0 | 0 | Battery-supported
2025-03-07 19:00 | 66 | 3 | Autumn | 19 | 14.37 | -3.1 | 8.45 | 70.7 | 12.4 | 0.74 | 16.98 | 17.72 | 3.1 | 56.96 | 15 | -35.06 | 4.18 | 1.556 | 0 | Diesel-backup
2025-03-07 20:00 | 66 | 3 | Autumn | 20 | 14.37 | -1.2 | 5.62 | 31.4 | 0 | 0 | 1.33 | 1.33 | 1.2 | 45 | 15 | 0 | 43.67 | 14.049 | 0 | Diesel-backup
2025-03-07 21:00 | 66 | 3 | Autumn | 21 | 14.37 | -4.2 | 4.33 | 40.9 | 0 | 0 | 0.08 | 0.08 | 4.2 | 45 | 15 | 0 | 44.92 | 14.379 | 0 | Diesel-backup
2025-03-07 22:00 | 66 | 3 | Autumn | 22 | 14.37 | -2.8 | 7.57 | 22.4 | 0 | 0 | 9.44 | 9.44 | 2.8 | 45 | 15 | 0 | 35.56 | 11.809 | 0 | Diesel-backup
2025-03-07 23:00 | 66 | 3 | Autumn | 23 | 14.37 | -5.8 | 8.57 | 72.5 | 0 | 0 | 18.24 | 18.24 | 5.8 | 46.68 | 15 | 0 | 28.44 | 9.704 | 0 | Diesel-backup
2025-03-08 | 67 | 3 | Autumn | 0 | 14.21 | -5 | 6.61 | 51.5 | 0 | 0 | 4.21 | 4.21 | 5 | 45 | 15 | 0 | 40.79 | 13.273 | 0 | Diesel-backup
2025-03-08 01:00 | 67 | 3 | Autumn | 1 | 14.21 | -8.7 | 6.72 | 46.4 | 0 | 0 | 4.67 | 4.67 | 8.7 | 45 | 15 | 0 | 40.33 | 13.147 | 0 | Diesel-backup
2025-03-08 02:00 | 67 | 3 | Autumn | 2 | 14.21 | -10.7 | 5.59 | 45.4 | 0 | 0 | 1.28 | 1.28 | 10.7 | 50.8 | 15 | 0 | 49.52 | 15.846 | 0 | Diesel-backup
2025-03-08 03:00 | 67 | 3 | Autumn | 3 | 14.21 | -3.8 | 10.86 | 33.7 | 0 | 0 | 55.8 | 55.8 | 3.8 | 45 | 18.97 | 10.8 | 0 | 0 | 0 | Normal
2025-03-08 04:00 | 67 | 3 | Autumn | 4 | 14.21 | -8.4 | 5.07 | 63.1 | 0 | 0 | 0.54 | 0.54 | 8.4 | 45 | 15 | -9.94 | 34.52 | 11.511 | 0 | Diesel-backup
2025-03-08 05:00 | 67 | 3 | Autumn | 5 | 14.21 | -7.6 | 3.74 | 69.2 | 7.4 | 0.44 | 0 | 0.44 | 7.6 | 45 | 15 | 0 | 44.56 | 14.284 | 0 | Diesel-backup
2025-03-08 06:00 | 67 | 3 | Autumn | 6 | 14.21 | -9.8 | 5.44 | 14.9 | 141 | 8.46 | 1.02 | 9.48 | 9.8 | 50.5 | 15 | 0 | 41.02 | 13.335 | 0 | Diesel-backup
2025-03-08 07:00 | 67 | 3 | Autumn | 7 | 14.21 | -10 | 8.25 | 79.5 | 118.9 | 7.13 | 15 | 22.13 | 10 | 45 | 15 | 0 | 22.87 | 7.966 | 0 | Diesel-backup
2025-03-08 08:00 | 67 | 3 | Autumn | 8 | 14.21 | -7.4 | 11.25 | 14.2 | 371.5 | 22.29 | 65.15 | 87.44 | 7.4 | 51.62 | 28.18 | 35.82 | 0 | 0 | 0 | Normal
2025-03-08 09:00 | 67 | 3 | Autumn | 9 | 14.21 | -8.5 | 19.45 | 75.4 | 224.6 | 13.48 | 120 | 133.48 | 8.5 | 53.65 | 57.56 | 79.83 | 0 | 0 | 0 | Normal
2025-03-08 10:00 | 67 | 3 | Autumn | 10 | 14.21 | -6 | 7.62 | 43.7 | 398.4 | 23.9 | 9.79 | 33.69 | 6 | 54.64 | 49.18 | -20.95 | 0 | 0 | 0 | Battery-supported
2025-03-08 11:00 | 67 | 3 | Autumn | 11 | 14.21 | -5.6 | 16.68 | 16.5 | 560.9 | 33.65 | 120 | 153.65 | 5.6 | 51.27 | 86.86 | 102.38 | 0 | 0 | 0 | Normal
2025-03-08 12:00 | 67 | 3 | Autumn | 12 | 14.21 | -5.5 | 4.79 | 36.4 | 476.6 | 28.6 | 0.3 | 28.9 | 5.5 | 47.53 | 79.4 | -18.63 | 0 | 0 | 0 | Battery-supported
2025-03-08 13:00 | 67 | 3 | Autumn | 13 | 14.21 | -5.4 | 4.24 | 40.2 | 446.9 | 26.81 | 0.06 | 26.87 | 5.4 | 45 | 72.15 | -18.13 | 0 | 0 | 0 | Battery-supported
2025-03-08 14:00 | 67 | 3 | Autumn | 14 | 14.21 | -2 | 9.35 | 58.1 | 334.7 | 20.08 | 28.02 | 48.1 | 2 | 47.81 | 72.26 | 0.29 | 0 | 0 | 0 | Normal
2025-03-08 15:00 | 67 | 3 | Autumn | 15 | 14.21 | -7.5 | 10.18 | 72.5 | 235.8 | 14.15 | 41.72 | 55.87 | 7.5 | 51.19 | 73.98 | 4.68 | 0 | 0 | 0 | Normal
2025-03-08 16:00 | 67 | 3 | Autumn | 16 | 14.21 | -4.9 | 8.09 | 31.2 | 318.4 | 19.1 | 13.53 | 32.63 | 4.9 | 55 | 65.03 | -22.37 | 0 | 0 | 0 | Battery-supported
2025-03-08 17:00 | 67 | 3 | Autumn | 17 | 14.21 | -1.9 | 29.16 | 43.9 | 197.6 | 11.86 | 0 | 11.86 | 1.9 | 47.2 | 50.9 | -35.34 | 0 | 0 | 0 | Battery-supported
2025-03-08 18:00 | 67 | 3 | Autumn | 18 | 14.21 | -1.4 | 4.97 | 52.3 | 96.5 | 5.79 | 0.44 | 6.23 | 1.4 | 45 | 35.39 | -38.77 | 0 | 0 | 0 | Battery-supported
2025-03-08 19:00 | 67 | 3 | Autumn | 19 | 14.21 | -7.2 | 14.89 | 20.1 | 13 | 0.78 | 120 | 120.78 | 7.2 | 45.21 | 63.2 | 75.57 | 0 | 0 | 0 | Normal
2025-03-08 20:00 | 67 | 3 | Autumn | 20 | 14.21 | -4.7 | 4.32 | 77.9 | 0 | 0 | 0.08 | 0.08 | 4.7 | 47.01 | 44.43 | -46.93 | 0 | 0 | 0 | Battery-supported
2025-03-08 21:00 | 67 | 3 | Autumn | 21 | 14.21 | -1.1 | 10.65 | 61.2 | 0 | 0 | 51.16 | 51.16 | 1.1 | 45 | 46.69 | 6.16 | 0 | 0 | 0 | Normal
2025-03-08 22:00 | 67 | 3 | Autumn | 22 | 14.21 | -3.1 | 7.42 | 59.1 | 0 | 0 | 8.43 | 8.43 | 3.1 | 45 | 32.06 | -36.57 | 0 | 0 | 0 | Battery-supported
2025-03-08 23:00 | 67 | 3 | Autumn | 23 | 14.21 | -4 | 8.42 | 3.1 | 0 | 0 | 16.67 | 16.67 | 4 | 45 | 20.73 | -28.33 | 0 | 0 | 0 | Battery-supported
2025-03-09 | 68 | 3 | Autumn | 0 | 14.05 | -5.4 | 9.44 | 2.8 | 0 | 0 | 29.33 | 29.33 | 5.4 | 45 | 15 | -14.33 | 1.34 | 0.503 | 0 | Diesel-backup
2025-03-09 01:00 | 68 | 3 | Autumn | 1 | 14.05 | -6.1 | 7.61 | 90.4 | 0 | 0 | 9.72 | 9.72 | 6.1 | 45 | 15 | 0 | 35.28 | 11.729 | 0 | Diesel-backup
2025-03-09 02:00 | 68 | 3 | Autumn | 2 | 14.05 | -5 | 6.73 | 24 | 0 | 0 | 4.72 | 4.72 | 5 | 45 | 15 | 0 | 40.28 | 13.133 | 0 | Diesel-backup
2025-03-09 03:00 | 68 | 3 | Autumn | 3 | 14.05 | -6.6 | 1.89 | 57.5 | 0 | 0 | 0 | 0 | 6.6 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-03-09 04:00 | 68 | 3 | Autumn | 4 | 14.05 | -6.5 | 12.32 | 46 | 0 | 0 | 96.03 | 96.03 | 6.5 | 45 | 33.78 | 51.03 | 0 | 0 | 0 | Normal
2025-03-09 05:00 | 68 | 3 | Autumn | 5 | 14.05 | -6.5 | 3 | 81.9 | 1.5 | 0.09 | 0 | 0.09 | 6.5 | 47.28 | 15 | -46.95 | 0.24 | 0.091 | 0 | Diesel-backup
2025-03-09 06:00 | 68 | 3 | Autumn | 6 | 14.05 | -8.4 | 5.7 | 77.7 | 62.3 | 3.74 | 1.49 | 5.23 | 8.4 | 45 | 15 | 0 | 39.77 | 12.993 | 0 | Diesel-backup
2025-03-09 07:00 | 68 | 3 | Autumn | 7 | 14.05 | -5.9 | 8.82 | 47.1 | 185.7 | 11.14 | 21.07 | 32.21 | 5.9 | 45 | 15 | 0 | 12.79 | 4.62 | 0 | Diesel-backup
2025-03-09 08:00 | 68 | 3 | Autumn | 8 | 14.05 | -0.7 | 3.41 | 79.3 | 166.3 | 9.98 | 0 | 9.98 | 0.7 | 45.28 | 15 | 0 | 35.3 | 11.734 | 0 | Diesel-backup
2025-03-09 09:00 | 68 | 3 | Autumn | 9 | 14.05 | -11 | 6.72 | 77.9 | 213.6 | 12.82 | 4.67 | 17.49 | 11 | 52.2 | 15 | 0 | 34.71 | 11.564 | 0 | Diesel-backup
2025-03-09 10:00 | 68 | 3 | Autumn | 10 | 14.05 | -6.2 | 11.52 | 17.5 | 513.7 | 30.82 | 72.2 | 103.02 | 6.2 | 49.85 | 34.57 | 53.17 | 0 | 0 | 0 | Normal
2025-03-09 11:00 | 68 | 3 | Autumn | 11 | 14.05 | -8.4 | 5.62 | 50.2 | 398.9 | 23.93 | 1.33 | 25.26 | 8.4 | 52.91 | 23.51 | -27.65 | 0 | 0 | 0 | Battery-supported
2025-03-09 12:00 | 68 | 3 | Autumn | 12 | 14.05 | -5.1 | 6.79 | 32 | 498.6 | 29.92 | 4.98 | 34.9 | 5.1 | 46.45 | 18.89 | -11.55 | 0 | 0 | 0 | Battery-supported
2025-03-09 13:00 | 68 | 3 | Autumn | 13 | 14.05 | -5.9 | 3.9 | 19.7 | 545.2 | 32.71 | 0.01 | 32.72 | 5.9 | 53.72 | 15 | -9.72 | 11.28 | 4.098 | 0 | Diesel-backup
2025-03-09 14:00 | 68 | 3 | Autumn | 14 | 14.05 | -4 | 6.05 | 60.5 | 323.1 | 19.39 | 2.32 | 21.71 | 4 | 56.72 | 15 | 0 | 35.01 | 11.651 | 0 | Diesel-backup
2025-03-09 15:00 | 68 | 3 | Autumn | 15 | 14.05 | -2.7 | 3.06 | 62.8 | 271.7 | 16.3 | 0 | 16.3 | 2.7 | 45 | 15 | 0 | 28.7 | 9.783 | 0 | Diesel-backup
2025-03-09 16:00 | 68 | 3 | Autumn | 16 | 14.05 | -4.5 | 8.21 | 69.3 | 197.4 | 11.84 | 14.62 | 26.46 | 4.5 | 51.21 | 15 | 0 | 24.75 | 8.562 | 0 | Diesel-backup
2025-03-09 17:00 | 68 | 3 | Autumn | 17 | 14.05 | -2.1 | 2.56 | 14.1 | 256.7 | 15.4 | 0 | 15.4 | 2.1 | 53.53 | 15 | 0 | 38.13 | 12.537 | 0 | Diesel-backup
2025-03-09 18:00 | 68 | 3 | Autumn | 18 | 14.05 | -9.5 | 4.86 | 69.7 | 71.3 | 4.28 | 0.35 | 4.63 | 9.5 | 58.29 | 15 | 0 | 53.66 | 17.171 | 0 | Diesel-backup
2025-03-09 19:00 | 68 | 3 | Autumn | 19 | 14.05 | -0.7 | 7.49 | 88.2 | 1.3 | 0.08 | 8.89 | 8.97 | 0.7 | 45 | 15 | 0 | 36.03 | 11.943 | 0 | Diesel-backup
2025-03-09 20:00 | 68 | 3 | Autumn | 20 | 14.05 | -3.3 | 6.44 | 47.1 | 0 | 0 | 3.56 | 3.56 | 3.3 | 45 | 15 | 0 | 41.44 | 13.45 | 0 | Diesel-backup
2025-03-09 21:00 | 68 | 3 | Autumn | 21 | 14.05 | -1.8 | 9.11 | 53.2 | 0 | 0 | 24.71 | 24.71 | 1.8 | 45 | 15 | 0 | 20.29 | 7.135 | 0 | Diesel-backup
2025-03-09 22:00 | 68 | 3 | Autumn | 22 | 14.05 | -7 | 6.8 | 16.8 | 0 | 0 | 5.03 | 5.03 | 7 | 45 | 15 | 0 | 39.97 | 13.048 | 0 | Diesel-backup
2025-03-09 23:00 | 68 | 3 | Autumn | 23 | 14.05 | -6.4 | 1.88 | 56.1 | 0 | 0 | 0 | 0 | 6.4 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-03-10 | 69 | 3 | Autumn | 0 | 13.9 | -4.8 | 3.38 | 18.2 | 0 | 0 | 0 | 0 | 4.8 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-03-10 01:00 | 69 | 3 | Autumn | 1 | 13.9 | -5.5 | 7.29 | 80.9 | 0 | 0 | 7.62 | 7.62 | 5.5 | 45 | 15 | 0 | 37.38 | 12.326 | 0 | Diesel-backup
2025-03-10 02:00 | 69 | 3 | Autumn | 2 | 13.9 | -5.2 | 13.33 | 44.4 | 0 | 0 | 120 | 120 | 5.2 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-03-10 03:00 | 69 | 3 | Autumn | 3 | 13.9 | -3.8 | 11.99 | 32.5 | 0 | 0 | 85.65 | 85.65 | 3.8 | 45 | 57.56 | 40.65 | 0 | 0 | 0 | Normal
2025-03-10 04:00 | 69 | 3 | Autumn | 4 | 13.9 | -10.5 | 28.91 | 93.9 | 0 | 0 | 0 | 0 | 10.5 | 45 | 39.56 | -45 | 0 | 0 | 0 | Battery-supported
2025-03-10 05:00 | 69 | 3 | Autumn | 5 | 13.9 | -4.7 | 5.24 | 84.3 | 0 | 0 | 0.74 | 0.74 | 4.7 | 45 | 21.86 | -44.26 | 0 | 0 | 0 | Battery-supported
2025-03-10 06:00 | 69 | 3 | Autumn | 6 | 13.9 | -7.1 | 11.33 | 82.3 | 53.4 | 3.2 | 67.19 | 70.39 | 7.1 | 45 | 31.2 | 25.39 | 0 | 0 | 0 | Normal
2025-03-10 07:00 | 69 | 3 | Autumn | 7 | 13.9 | -7.7 | 10.87 | 59.5 | 154.9 | 9.29 | 56.03 | 65.32 | 7.7 | 45 | 38.68 | 20.32 | 0 | 0 | 0 | Normal
2025-03-10 08:00 | 69 | 3 | Autumn | 8 | 13.9 | -10.6 | 17.15 | 24.4 | 331.3 | 19.88 | 120 | 139.88 | 10.6 | 48.4 | 72.34 | 91.48 | 0 | 0 | 0 | Normal
2025-03-10 09:00 | 69 | 3 | Autumn | 9 | 13.9 | -6.2 | 14.57 | 76.2 | 219.1 | 13.15 | 120 | 133.15 | 6.2 | 46.09 | 95 | 61.57 | 0 | 0 | 0 | Normal
2025-03-10 10:00 | 69 | 3 | Autumn | 10 | 13.9 | -12.4 | 8.6 | 30.4 | 455.7 | 27.34 | 18.57 | 45.91 | 12.4 | 59.24 | 89.67 | -13.33 | 0 | 0 | 0 | Battery-supported
2025-03-10 11:00 | 69 | 3 | Autumn | 11 | 13.9 | -5.5 | 10.28 | 29.5 | 498 | 29.88 | 43.62 | 73.5 | 5.5 | 45 | 95 | 14.49 | 0 | 0 | 0 | Normal
2025-03-10 12:00 | 69 | 3 | Autumn | 12 | 13.9 | -9.9 | 9.16 | 57.9 | 371 | 22.26 | 25.38 | 47.64 | 9.9 | 55.91 | 91.69 | -8.27 | 0 | 0 | 0 | Battery-supported
2025-03-10 13:00 | 69 | 3 | Autumn | 13 | 13.9 | -6.1 | 7.13 | 30.4 | 493.7 | 29.62 | 6.69 | 36.31 | 6.1 | 47.79 | 87.1 | -11.48 | 0 | 0 | 0 | Battery-supported
2025-03-10 14:00 | 69 | 3 | Autumn | 14 | 13.9 | -6.1 | 9.85 | 34.9 | 435.4 | 26.12 | 35.84 | 61.96 | 6.1 | 45 | 93.34 | 16.96 | 0 | 0 | 0 | Normal
2025-03-10 15:00 | 69 | 3 | Autumn | 15 | 13.9 | -2.9 | 8.08 | 74.7 | 224.8 | 13.49 | 13.45 | 26.94 | 2.9 | 45 | 86.12 | -18.06 | 0 | 0 | 0 | Battery-supported
2025-03-10 16:00 | 69 | 3 | Autumn | 16 | 13.9 | -5.5 | 7.88 | 35.9 | 296.3 | 17.78 | 11.76 | 29.54 | 5.5 | 51.44 | 77.36 | -21.9 | 0 | 0 | 0 | Battery-supported
2025-03-10 17:00 | 69 | 3 | Autumn | 17 | 13.9 | -6.3 | 17.6 | 10.6 | 257.4 | 15.44 | 120 | 135.44 | 6.3 | 58.53 | 95 | 47.94 | 0 | 0 | 0 | Normal
2025-03-10 18:00 | 69 | 3 | Autumn | 18 | 13.9 | -5.6 | 8.7 | 77.8 | 58.1 | 3.49 | 19.68 | 23.17 | 5.6 | 56.06 | 81.84 | -32.89 | 0 | 0 | 0 | Battery-supported
2025-03-10 19:00 | 69 | 3 | Autumn | 19 | 13.9 | -1.6 | 7.67 | 54.3 | 0 | 0 | 10.15 | 10.15 | 1.6 | 45 | 67.9 | -34.85 | 0 | 0 | 0 | Battery-supported
2025-03-10 20:00 | 69 | 3 | Autumn | 20 | 13.9 | -3.1 | 6.59 | 66.6 | 0 | 0 | 4.13 | 4.13 | 3.1 | 49.3 | 49.84 | -45.17 | 0 | 0 | 0 | Battery-supported
2025-03-10 21:00 | 69 | 3 | Autumn | 21 | 13.9 | -5.2 | 6.24 | 88.1 | 0 | 0 | 2.88 | 2.88 | 5.2 | 45 | 32.99 | -42.12 | 0 | 0 | 0 | Battery-supported
2025-03-10 22:00 | 69 | 3 | Autumn | 22 | 13.9 | -5 | 3.31 | 35.7 | 0 | 0 | 0 | 0 | 5 | 45 | 15 | -44.97 | 0.03 | 0.011 | 0 | Diesel-backup
2025-03-10 23:00 | 69 | 3 | Autumn | 23 | 13.9 | -8.2 | 7.13 | 52.1 | 0 | 0 | 6.69 | 6.69 | 8.2 | 47.22 | 15 | 0 | 40.53 | 13.201 | 0 | Diesel-backup
2025-03-11 | 70 | 3 | Autumn | 0 | 13.74 | -4.4 | 13.76 | 19.4 | 0 | 0 | 120 | 120 | 4.4 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-03-11 01:00 | 70 | 3 | Autumn | 1 | 13.74 | -9.5 | 5.16 | 89.8 | 0 | 0 | 0.64 | 0.64 | 9.5 | 45.42 | 24.69 | -44.78 | 0 | 0 | 0 | Battery-supported
2025-03-11 02:00 | 70 | 3 | Autumn | 2 | 13.74 | -4.3 | 22 | 73.3 | 0 | 0 | 120 | 120 | 4.3 | 45 | 52.29 | 75 | 0 | 0 | 0 | Normal
2025-03-11 03:00 | 70 | 3 | Autumn | 3 | 13.74 | -6.1 | 1.3 | 33 | 0 | 0 | 0 | 0 | 6.1 | 45 | 34.29 | -45 | 0 | 0 | 0 | Battery-supported
2025-03-11 04:00 | 70 | 3 | Autumn | 4 | 13.74 | -1.5 | 9.67 | 40.4 | 0 | 0 | 32.88 | 32.88 | 1.5 | 45 | 29.44 | -12.12 | 0 | 0 | 0 | Battery-supported
2025-03-11 05:00 | 70 | 3 | Autumn | 5 | 13.74 | -9.5 | 8.29 | 75.9 | 0 | 0 | 15.38 | 15.38 | 9.5 | 46.55 | 16.97 | -31.17 | 0 | 0 | 0 | Battery-supported
2025-03-11 06:00 | 70 | 3 | Autumn | 6 | 13.74 | -7.5 | 17.48 | 49.5 | 81.6 | 4.9 | 120 | 124.9 | 7.5 | 45.43 | 46.22 | 79.47 | 0 | 0 | 0 | Normal
2025-03-11 07:00 | 70 | 3 | Autumn | 7 | 13.74 | -3.5 | 4.8 | 39 | 192.5 | 11.55 | 0.31 | 11.86 | 3.5 | 45.44 | 32.78 | -33.58 | 0 | 0 | 0 | Battery-supported
2025-03-11 08:00 | 70 | 3 | Autumn | 8 | 13.74 | -4.9 | 3.05 | 78.5 | 164.7 | 9.88 | 0 | 9.88 | 4.9 | 45 | 18.74 | -35.12 | 0 | 0 | 0 | Battery-supported
2025-03-11 09:00 | 70 | 3 | Autumn | 9 | 13.74 | -9 | 6.4 | 60.7 | 276.4 | 16.58 | 3.41 | 19.99 | 9 | 59.04 | 15 | -9.34 | 29.71 | 10.088 | 0 | Diesel-backup
2025-03-11 10:00 | 70 | 3 | Autumn | 10 | 13.74 | -6.8 | 5.78 | 50.3 | 366.3 | 21.98 | 1.66 | 23.64 | 6.8 | 48.76 | 15 | 0 | 25.12 | 8.678 | 0 | Diesel-backup
2025-03-11 11:00 | 70 | 3 | Autumn | 11 | 13.74 | -7 | 2.25 | 51.8 | 390.6 | 23.44 | 0 | 23.44 | 7 | 50.32 | 15 | 0 | 26.88 | 9.225 | 0 | Diesel-backup
2025-03-11 12:00 | 70 | 3 | Autumn | 12 | 13.74 | -6.1 | 7.74 | 76.6 | 279.1 | 16.75 | 10.67 | 27.42 | 6.1 | 48.63 | 15 | 0 | 21.21 | 7.433 | 0 | Diesel-backup
2025-03-11 13:00 | 70 | 3 | Autumn | 13 | 13.74 | -7.9 | 5.48 | 51.8 | 390.4 | 23.42 | 1.09 | 24.51 | 7.9 | 51.91 | 15 | 0 | 27.4 | 9.385 | 0 | Diesel-backup
2025-03-11 14:00 | 70 | 3 | Autumn | 14 | 13.74 | -6.2 | 15.67 | 82.8 | 223.1 | 13.39 | 120 | 133.39 | 6.2 | 51.99 | 44.96 | 81.4 | 0 | 0 | 0 | Normal
2025-03-11 15:00 | 70 | 3 | Autumn | 15 | 13.74 | -9.1 | 7.82 | 32.5 | 383.8 | 23.03 | 11.28 | 34.31 | 9.1 | 56.25 | 36.18 | -21.94 | 0 | 0 | 0 | Battery-supported
2025-03-11 16:00 | 70 | 3 | Autumn | 16 | 13.74 | -4.9 | 4.41 | 22.9 | 331.6 | 19.9 | 0.11 | 20.01 | 4.9 | 46.92 | 25.42 | -26.91 | 0 | 0 | 0 | Battery-supported
2025-03-11 17:00 | 70 | 3 | Autumn | 17 | 13.74 | -3.9 | 7.23 | 76.7 | 115.6 | 6.94 | 7.26 | 14.2 | 3.9 | 47.25 | 15 | -26.04 | 7.01 | 2.585 | 0 | Diesel-backup
2025-03-11 18:00 | 70 | 3 | Autumn | 18 | 13.74 | -5.2 | 8.2 | 83.9 | 48 | 2.88 | 14.53 | 17.41 | 5.2 | 45 | 15 | 0 | 27.59 | 9.444 | 0 | Diesel-backup
2025-03-11 19:00 | 70 | 3 | Autumn | 19 | 13.74 | -8.1 | 10.22 | 67.2 | 0 | 0 | 42.47 | 42.47 | 8.1 | 53.81 | 15 | 0 | 11.34 | 4.117 | 0 | Diesel-backup
2025-03-11 20:00 | 70 | 3 | Autumn | 20 | 13.74 | -2.3 | 7.45 | 11.3 | 0 | 0 | 8.63 | 8.63 | 2.3 | 46.36 | 15 | 0 | 37.73 | 12.425 | 0 | Diesel-backup
2025-03-11 21:00 | 70 | 3 | Autumn | 21 | 13.74 | -3.7 | 21.39 | 27 | 0 | 0 | 120 | 120 | 3.7 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-03-11 22:00 | 70 | 3 | Autumn | 22 | 13.74 | -6.3 | 3.25 | 80.9 | 0 | 0 | 0 | 0 | 6.3 | 45 | 24.6 | -45 | 0 | 0 | 0 | Battery-supported
2025-03-11 23:00 | 70 | 3 | Autumn | 23 | 13.74 | -5.5 | 5.42 | 35.1 | 0 | 0 | 0.99 | 0.99 | 5.5 | 45 | 15 | -24 | 20.01 | 7.043 | 0 | Diesel-backup
2025-03-12 | 71 | 3 | Autumn | 0 | 13.58 | -8.7 | 4.44 | 64.1 | 0 | 0 | 0.12 | 0.12 | 8.7 | 48.93 | 15 | 0 | 48.81 | 15.619 | 0 | Diesel-backup
2025-03-12 01:00 | 71 | 3 | Autumn | 1 | 13.58 | -8 | 5.97 | 83.7 | 0 | 0 | 2.11 | 2.11 | 8 | 49.34 | 15 | 0 | 47.23 | 15.114 | 0 | Diesel-backup
2025-03-12 02:00 | 71 | 3 | Autumn | 2 | 13.58 | -7.3 | 8.82 | 13.6 | 0 | 0 | 21.07 | 21.07 | 7.3 | 45 | 15 | 0 | 23.93 | 8.303 | 0 | Diesel-backup
2025-03-12 03:00 | 71 | 3 | Autumn | 3 | 13.58 | -3.8 | 8.46 | 34.6 | 0 | 0 | 17.08 | 17.08 | 3.8 | 45 | 15 | 0 | 27.92 | 9.545 | 0 | Diesel-backup
2025-03-12 04:00 | 71 | 3 | Autumn | 4 | 13.58 | -8.3 | 10.11 | 45.2 | 0 | 0 | 40.42 | 40.42 | 8.3 | 46.49 | 15 | 0 | 6.07 | 2.245 | 0 | Diesel-backup
2025-03-12 05:00 | 71 | 3 | Autumn | 5 | 13.58 | -5.8 | 7.81 | 50.4 | 0 | 0 | 11.21 | 11.21 | 5.8 | 46.34 | 15 | 0 | 35.13 | 11.685 | 0 | Diesel-backup
2025-03-12 06:00 | 71 | 3 | Autumn | 6 | 13.58 | -8.6 | 8.1 | 32.2 | 90.6 | 5.44 | 13.62 | 19.06 | 8.6 | 45.5 | 15 | 0 | 26.44 | 9.089 | 0 | Diesel-backup
2025-03-12 07:00 | 71 | 3 | Autumn | 7 | 13.58 | -7.1 | 7.91 | 46.5 | 172.1 | 10.33 | 12 | 22.33 | 7.1 | 45 | 15 | 0 | 22.67 | 7.902 | 0 | Diesel-backup
2025-03-12 08:00 | 71 | 3 | Autumn | 8 | 13.58 | -8 | 5.62 | 66.6 | 197.7 | 11.86 | 1.33 | 13.19 | 8 | 54.14 | 15 | 0 | 40.95 | 13.316 | 0 | Diesel-backup
2025-03-12 09:00 | 71 | 3 | Autumn | 9 | 13.58 | -5.7 | 5.36 | 82.9 | 190.7 | 11.44 | 0.9 | 12.34 | 5.7 | 45 | 15 | 0 | 32.66 | 10.967 | 0 | Diesel-backup
2025-03-12 10:00 | 71 | 3 | Autumn | 10 | 13.58 | -8.6 | 4.38 | 73.4 | 264.1 | 15.85 | 0.1 | 15.95 | 8.6 | 47.63 | 15 | 0 | 31.68 | 10.678 | 0 | Diesel-backup
2025-03-12 11:00 | 71 | 3 | Autumn | 11 | 13.58 | -10.7 | 10.42 | 67.4 | 315.5 | 18.93 | 46.38 | 65.31 | 10.7 | 50.22 | 20.55 | 15.09 | 0 | 0 | 0 | Normal
2025-03-12 12:00 | 71 | 3 | Autumn | 12 | 13.58 | -9.9 | 1.53 | 70.5 | 309.3 | 18.56 | 0 | 18.56 | 9.9 | 50.21 | 15 | -13.88 | 17.77 | 6.305 | 0 | Diesel-backup
2025-03-12 13:00 | 71 | 3 | Autumn | 13 | 13.58 | -7.7 | 7.99 | 96.2 | 177.8 | 10.67 | 12.67 | 23.34 | 7.7 | 45 | 15 | 0 | 21.66 | 7.578 | 0 | Diesel-backup
2025-03-12 14:00 | 71 | 3 | Autumn | 14 | 13.58 | -8.9 | 11.53 | 87.7 | 200.8 | 12.05 | 72.47 | 84.52 | 8.9 | 49.64 | 27.84 | 34.88 | 0 | 0 | 0 | Normal
2025-03-12 15:00 | 71 | 3 | Autumn | 15 | 13.58 | -4.9 | 13.27 | 72.8 | 229.1 | 13.75 | 120 | 133.75 | 4.9 | 45.69 | 60.24 | 88.06 | 0 | 0 | 0 | Normal
2025-03-12 16:00 | 71 | 3 | Autumn | 16 | 13.58 | -6.4 | 1.15 | 93.4 | 118.3 | 7.1 | 0 | 7.1 | 6.4 | 48.35 | 43.74 | -41.25 | 0 | 0 | 0 | Battery-supported
2025-03-12 17:00 | 71 | 3 | Autumn | 17 | 13.58 | 0.1 | 5.73 | 79.6 | 106.4 | 6.38 | 1.55 | 7.93 | 0 | 45 | 28.91 | -37.07 | 0 | 0 | 0 | Battery-supported
2025-03-12 18:00 | 71 | 3 | Autumn | 18 | 13.58 | -8.7 | 4.55 | 66 | 60.4 | 3.62 | 0.16 | 3.78 | 8.7 | 46.7 | 15 | -34.78 | 8.14 | 2.987 | 0 | Diesel-backup
2025-03-12 19:00 | 71 | 3 | Autumn | 19 | 13.58 | -4.3 | 5.43 | 22.1 | 0 | 0 | 1.01 | 1.01 | 4.3 | 45.49 | 15 | 0 | 44.48 | 14.263 | 0 | Diesel-backup
2025-03-12 20:00 | 71 | 3 | Autumn | 20 | 13.58 | -7.1 | 14.85 | 19.2 | 0 | 0 | 120 | 120 | 7.1 | 49.73 | 40.86 | 70.27 | 0 | 0 | 0 | Normal
2025-03-12 21:00 | 71 | 3 | Autumn | 21 | 13.58 | -5.8 | 4.57 | 47.6 | 0 | 0 | 0.17 | 0.17 | 5.8 | 45 | 22.93 | -44.83 | 0 | 0 | 0 | Battery-supported
2025-03-12 22:00 | 71 | 3 | Autumn | 22 | 13.58 | -4.5 | 11.52 | 83.8 | 0 | 0 | 72.2 | 72.2 | 4.5 | 45 | 32.94 | 27.2 | 0 | 0 | 0 | Normal
2025-03-12 23:00 | 71 | 3 | Autumn | 23 | 13.58 | -10.2 | 8.06 | 70.6 | 0 | 0 | 13.27 | 13.27 | 10.2 | 46.15 | 19.78 | -32.88 | 0 | 0 | 0 | Battery-supported
2025-03-13 | 72 | 3 | Autumn | 0 | 13.43 | -5.1 | 5.31 | 48.5 | 0 | 0 | 0.83 | 0.83 | 5.1 | 45 | 15 | -11.96 | 32.21 | 10.834 | 0 | Diesel-backup
2025-03-13 01:00 | 72 | 3 | Autumn | 1 | 13.43 | -1.8 | 4.97 | 8.8 | 0 | 0 | 0.44 | 0.44 | 1.8 | 45 | 15 | 0 | 44.56 | 14.284 | 0 | Diesel-backup
2025-03-13 02:00 | 72 | 3 | Autumn | 2 | 13.43 | -7.3 | 8.58 | 37.9 | 0 | 0 | 18.35 | 18.35 | 7.3 | 45 | 15 | 0 | 26.65 | 9.154 | 0 | Diesel-backup
2025-03-13 03:00 | 72 | 3 | Autumn | 3 | 13.43 | -6.1 | 7.05 | 67 | 0 | 0 | 6.26 | 6.26 | 6.1 | 46.06 | 15 | 0 | 39.8 | 13.001 | 0 | Diesel-backup
2025-03-13 04:00 | 72 | 3 | Autumn | 4 | 13.43 | -4.8 | 2.15 | 32.7 | 0 | 0 | 0 | 0 | 4.8 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-03-13 05:00 | 72 | 3 | Autumn | 5 | 13.43 | -7.7 | 3.9 | 53.7 | 0 | 0 | 0.01 | 0.01 | 7.7 | 45 | 15 | 0 | 44.99 | 14.397 | 0 | Diesel-backup
2025-03-13 06:00 | 72 | 3 | Autumn | 6 | 13.43 | -8.9 | 8.71 | 31.2 | 83.6 | 5.02 | 19.79 | 24.81 | 8.9 | 45 | 15 | 0 | 20.19 | 7.102 | 0 | Diesel-backup
2025-03-13 07:00 | 72 | 3 | Autumn | 7 | 13.43 | -12.8 | 3.17 | 48.4 | 163.1 | 9.79 | 0 | 9.79 | 12.8 | 46.08 | 15 | 0 | 36.29 | 12.017 | 0 | Diesel-backup
2025-03-13 08:00 | 72 | 3 | Autumn | 8 | 13.43 | -6.4 | 12.5 | 36 | 284.1 | 17.05 | 102.03 | 119.08 | 6.4 | 46.18 | 41.83 | 72.9 | 0 | 0 | 0 | Normal
2025-03-13 09:00 | 72 | 3 | Autumn | 9 | 13.43 | -8 | 2.55 | 80.8 | 197.2 | 11.83 | 0 | 11.83 | 8 | 52.5 | 25.56 | -40.67 | 0 | 0 | 0 | Battery-supported
2025-03-13 10:00 | 72 | 3 | Autumn | 10 | 13.43 | -9.9 | 6.23 | 55 | 344 | 20.64 | 2.85 | 23.49 | 9.9 | 51.72 | 15 | -26.4 | 1.83 | 0.687 | 0 | Diesel-backup
2025-03-13 11:00 | 72 | 3 | Autumn | 11 | 13.43 | -7.1 | 10.64 | 26.1 | 513.2 | 30.79 | 50.95 | 81.74 | 7.1 | 45 | 28.52 | 36.74 | 0 | 0 | 0 | Normal
2025-03-13 12:00 | 72 | 3 | Autumn | 12 | 13.43 | -8.4 | 3.7 | 63.6 | 342.8 | 20.57 | 0 | 20.57 | 8.4 | 57.49 | 15 | -33.8 | 3.12 | 1.165 | 0 | Diesel-backup
2025-03-13 13:00 | 72 | 3 | Autumn | 13 | 13.43 | -7.9 | 3.02 | 23.7 | 524.9 | 31.49 | 0 | 31.49 | 7.9 | 51.61 | 15 | 0 | 20.12 | 7.079 | 0 | Diesel-backup
2025-03-13 14:00 | 72 | 3 | Autumn | 14 | 13.43 | -5 | 9.55 | 83.6 | 218.4 | 13.1 | 30.99 | 44.09 | 5 | 51.95 | 15 | 0 | 7.86 | 2.889 | 0 | Diesel-backup
2025-03-13 15:00 | 72 | 3 | Autumn | 15 | 13.43 | -8.9 | 11.77 | 63 | 264.4 | 15.86 | 79.16 | 95.02 | 8.9 | 47.52 | 32.48 | 47.5 | 0 | 0 | 0 | Normal
2025-03-13 16:00 | 72 | 3 | Autumn | 16 | 13.43 | -3.3 | 6.51 | 62.4 | 206.9 | 12.41 | 3.82 | 16.23 | 3.3 | 45 | 20.97 | -28.77 | 0 | 0 | 0 | Battery-supported
2025-03-13 17:00 | 72 | 3 | Autumn | 17 | 13.43 | -8.3 | 5.65 | 65.7 | 130 | 7.8 | 1.39 | 9.19 | 8.3 | 55.3 | 15 | -14.93 | 31.18 | 10.529 | 0 | Diesel-backup
2025-03-13 18:00 | 72 | 3 | Autumn | 18 | 13.43 | -6.5 | 2.47 | 34 | 81.4 | 4.88 | 0 | 4.88 | 6.5 | 46.5 | 15 | 0 | 41.62 | 13.498 | 0 | Diesel-backup
2025-03-13 19:00 | 72 | 3 | Autumn | 19 | 13.43 | -0.6 | 7.66 | 54.6 | 0 | 0 | 10.08 | 10.08 | 0.6 | 45 | 15 | 0 | 34.92 | 11.625 | 0 | Diesel-backup
2025-03-13 20:00 | 72 | 3 | Autumn | 20 | 13.43 | -2.3 | 1.9 | 22.3 | 0 | 0 | 0 | 0 | 2.3 | 45.04 | 15 | 0 | 45.04 | 14.413 | 0 | Diesel-backup
2025-03-13 21:00 | 72 | 3 | Autumn | 21 | 13.43 | -4.7 | 15.02 | 34 | 0 | 0 | 120 | 120 | 4.7 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-03-13 22:00 | 72 | 3 | Autumn | 22 | 13.43 | -7.1 | 6.7 | 26.2 | 0 | 0 | 4.59 | 4.59 | 7.1 | 45 | 26.44 | -40.41 | 0 | 0 | 0 | Battery-supported
2025-03-13 23:00 | 72 | 3 | Autumn | 23 | 13.43 | -6.4 | 3.96 | 27.7 | 0 | 0 | 0.01 | 0.01 | 6.4 | 45 | 15 | -28.59 | 16.4 | 5.848 | 0 | Diesel-backup
2025-03-14 | 73 | 3 | Autumn | 0 | 13.27 | -5.6 | 4.95 | 43.5 | 0 | 0 | 0.43 | 0.43 | 5.6 | 45 | 15 | 0 | 44.57 | 14.287 | 0 | Diesel-backup
2025-03-14 01:00 | 73 | 3 | Autumn | 1 | 13.27 | -6 | 8.04 | 69 | 0 | 0 | 13.1 | 13.1 | 6 | 45 | 15 | 0 | 31.9 | 10.743 | 0 | Diesel-backup
2025-03-14 02:00 | 73 | 3 | Autumn | 2 | 13.27 | -6.7 | 5.49 | 47.4 | 0 | 0 | 1.1 | 1.1 | 6.7 | 45 | 15 | 0 | 43.9 | 14.11 | 0 | Diesel-backup
2025-03-14 03:00 | 73 | 3 | Autumn | 3 | 13.27 | -7 | 7.26 | 81.3 | 0 | 0 | 7.44 | 7.44 | 7 | 45 | 15 | 0 | 37.56 | 12.377 | 0 | Diesel-backup
2025-03-14 04:00 | 73 | 3 | Autumn | 4 | 13.27 | -7.7 | 3.6 | 63.1 | 0 | 0 | 0 | 0 | 7.7 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-03-14 05:00 | 73 | 3 | Autumn | 5 | 13.27 | -10.7 | 13.52 | 79.3 | 0 | 0 | 120 | 120 | 10.7 | 48.13 | 41.45 | 71.87 | 0 | 0 | 0 | Normal
2025-03-14 06:00 | 73 | 3 | Autumn | 6 | 13.27 | -8.9 | 5.02 | 23.9 | 80.8 | 4.85 | 0.49 | 5.34 | 8.9 | 45 | 25.58 | -39.66 | 0 | 0 | 0 | Battery-supported
2025-03-14 07:00 | 73 | 3 | Autumn | 7 | 13.27 | -5.9 | 1.47 | 79.7 | 99.8 | 5.99 | 0 | 5.99 | 5.9 | 45 | 15 | -26.46 | 12.55 | 4.537 | 0 | Diesel-backup
2025-03-14 08:00 | 73 | 3 | Autumn | 8 | 13.27 | -11 | 5.79 | 55.3 | 224.2 | 13.45 | 1.68 | 15.13 | 11 | 54.8 | 15 | 0 | 39.67 | 12.965 | 0 | Diesel-backup
2025-03-14 09:00 | 73 | 3 | Autumn | 9 | 13.27 | -8.4 | 4.54 | 22.2 | 414.6 | 24.88 | 0.16 | 25.04 | 8.4 | 49.24 | 15 | 0 | 24.2 | 8.388 | 0 | Diesel-backup
2025-03-14 10:00 | 73 | 3 | Autumn | 10 | 13.27 | -9.6 | 13.01 | 59.6 | 322.8 | 19.37 | 120 | 139.37 | 9.6 | 56.49 | 45.5 | 82.88 | 0 | 0 | 0 | Normal
2025-03-14 11:00 | 73 | 3 | Autumn | 11 | 13.27 | -7.3 | 3.98 | 68.9 | 308.3 | 18.5 | 0.02 | 18.52 | 7.3 | 48.8 | 33.39 | -30.28 | 0 | 0 | 0 | Battery-supported
2025-03-14 12:00 | 73 | 3 | Autumn | 12 | 13.27 | -8.1 | 5.44 | 9.1 | 611 | 36.66 | 1.02 | 37.68 | 8.1 | 48.86 | 28.92 | -11.18 | 0 | 0 | 0 | Battery-supported
2025-03-14 13:00 | 73 | 3 | Autumn | 13 | 13.27 | -3.6 | 8.17 | 60.3 | 349.3 | 20.96 | 14.25 | 35.21 | 3.6 | 51.02 | 22.59 | -15.81 | 0 | 0 | 0 | Battery-supported
2025-03-14 14:00 | 73 | 3 | Autumn | 14 | 13.27 | -5.4 | 10.22 | 46.4 | 380.4 | 22.82 | 42.47 | 65.29 | 5.4 | 48.95 | 28.6 | 16.34 | 0 | 0 | 0 | Normal
2025-03-14 15:00 | 73 | 3 | Autumn | 15 | 13.27 | -9 | 15.63 | 57.8 | 281.8 | 16.91 | 120 | 136.91 | 9 | 45 | 62.43 | 91.91 | 0 | 0 | 0 | Normal
2025-03-14 16:00 | 73 | 3 | Autumn | 16 | 13.27 | -4.3 | 4.21 | 65.9 | 193.9 | 11.63 | 0.05 | 11.68 | 4.3 | 45 | 49.1 | -33.32 | 0 | 0 | 0 | Battery-supported
2025-03-14 17:00 | 73 | 3 | Autumn | 17 | 13.27 | -7.1 | 14.66 | 11.3 | 226.8 | 13.61 | 120 | 133.61 | 7.1 | 56.47 | 77.49 | 77.14 | 0 | 0 | 0 | Normal
2025-03-14 18:00 | 73 | 3 | Autumn | 18 | 13.27 | -6.5 | 12.73 | 74.9 | 43.2 | 2.59 | 110.06 | 112.65 | 6.5 | 49.83 | 95 | 47.59 | 0 | 0 | 0 | Normal
2025-03-14 19:00 | 73 | 3 | Autumn | 19 | 13.27 | -4.4 | 4.49 | 55.7 | 0 | 0 | 0.14 | 0.14 | 4.4 | 46.7 | 76.38 | -46.56 | 0 | 0 | 0 | Battery-supported
2025-03-14 20:00 | 73 | 3 | Autumn | 20 | 13.27 | -6.1 | 4.15 | 62.7 | 0 | 0 | 0.04 | 0.04 | 6.1 | 45 | 58.39 | -44.96 | 0 | 0 | 0 | Battery-supported
2025-03-14 21:00 | 73 | 3 | Autumn | 21 | 13.27 | -3.1 | 9.21 | 19.3 | 0 | 0 | 26.06 | 26.06 | 3.1 | 45 | 50.82 | -18.94 | 0 | 0 | 0 | Battery-supported
2025-03-14 22:00 | 73 | 3 | Autumn | 22 | 13.27 | -6.9 | 7.16 | 38.5 | 0 | 0 | 6.86 | 6.86 | 6.9 | 45 | 35.56 | -38.14 | 0 | 0 | 0 | Battery-supported
2025-03-14 23:00 | 73 | 3 | Autumn | 23 | 13.27 | -6.8 | 9.2 | 17.9 | 0 | 0 | 25.92 | 25.92 | 6.8 | 45 | 27.93 | -19.08 | 0 | 0 | 0 | Battery-supported
2025-03-15 | 74 | 3 | Autumn | 0 | 13.12 | -7.4 | 5.93 | 86.1 | 0 | 0 | 2.01 | 2.01 | 7.4 | 45 | 15 | -32.32 | 10.67 | 3.883 | 0 | Diesel-backup
2025-03-15 01:00 | 74 | 3 | Autumn | 1 | 13.12 | -7.5 | 7.62 | 81.2 | 0 | 0 | 9.79 | 9.79 | 7.5 | 45 | 15 | 0 | 35.21 | 11.708 | 0 | Diesel-backup
2025-03-15 02:00 | 74 | 3 | Autumn | 2 | 13.12 | -4.3 | 6.77 | 38.7 | 0 | 0 | 4.89 | 4.89 | 4.3 | 45 | 15 | 0 | 40.11 | 13.086 | 0 | Diesel-backup
2025-03-15 03:00 | 74 | 3 | Autumn | 3 | 13.12 | -5.7 | 9.16 | 70.9 | 0 | 0 | 25.38 | 25.38 | 5.7 | 45 | 15 | 0 | 19.62 | 6.916 | 0 | Diesel-backup
2025-03-15 04:00 | 74 | 3 | Autumn | 4 | 13.12 | -3.7 | 4.07 | 9.7 | 0 | 0 | 0.03 | 0.03 | 3.7 | 45 | 15 | 0 | 44.97 | 14.392 | 0 | Diesel-backup
2025-03-15 05:00 | 74 | 3 | Autumn | 5 | 13.12 | -2.7 | 7.97 | 31.2 | 0 | 0 | 12.5 | 12.5 | 2.7 | 45 | 15 | 0 | 32.5 | 10.92 | 0 | Diesel-backup
2025-03-15 06:00 | 74 | 3 | Autumn | 6 | 13.12 | -10.2 | 15.51 | 78.1 | 36.3 | 2.18 | 120 | 122.18 | 10.2 | 45 | 43.4 | 77.18 | 0 | 0 | 0 | Normal
2025-03-15 07:00 | 74 | 3 | Autumn | 7 | 13.12 | -8 | 15.01 | 18.2 | 206.6 | 12.4 | 120 | 132.4 | 8 | 45 | 75.57 | 87.4 | 0 | 0 | 0 | Normal
2025-03-15 08:00 | 74 | 3 | Autumn | 8 | 13.12 | -10.8 | 8.52 | 43 | 255.7 | 15.34 | 17.71 | 33.05 | 10.8 | 54.63 | 66.93 | -21.58 | 0 | 0 | 0 | Battery-supported
2025-03-15 09:00 | 74 | 3 | Autumn | 9 | 13.12 | -9.8 | 4.01 | 49.2 | 311.4 | 18.68 | 0.02 | 18.7 | 9.8 | 52.48 | 53.42 | -33.78 | 0 | 0 | 0 | Battery-supported
2025-03-15 10:00 | 74 | 3 | Autumn | 10 | 13.12 | -9.4 | 19.68 | 68.1 | 284.8 | 17.09 | 120 | 137.09 | 9.4 | 58.34 | 82.4 | 78.75 | 0 | 0 | 0 | Normal
2025-03-15 11:00 | 74 | 3 | Autumn | 11 | 13.12 | -10.1 | 9.16 | 32.6 | 481.7 | 28.9 | 25.38 | 54.28 | 10.1 | 52.04 | 83.23 | 2.24 | 0 | 0 | 0 | Normal
2025-03-15 12:00 | 74 | 3 | Autumn | 12 | 13.12 | -9.7 | 18.6 | 86 | 232.9 | 13.97 | 120 | 133.97 | 9.7 | 47.4 | 95 | 32 | 0 | 0 | 0 | Normal
2025-03-15 13:00 | 74 | 3 | Autumn | 13 | 13.12 | -7.4 | 9.38 | 69.7 | 304.1 | 18.25 | 28.45 | 46.7 | 7.4 | 50.4 | 93.52 | -3.7 | 0 | 0 | 0 | Battery-supported
2025-03-15 14:00 | 74 | 3 | Autumn | 14 | 13.12 | -9.4 | 1.05 | 17.7 | 504.7 | 30.28 | 0 | 30.28 | 9.4 | 50.1 | 85.59 | -19.82 | 0 | 0 | 0 | Battery-supported
2025-03-15 15:00 | 74 | 3 | Autumn | 15 | 13.12 | -4.4 | 19.61 | 0 | 493.8 | 29.63 | 120 | 149.63 | 4.4 | 45 | 95 | 25.57 | 0 | 0 | 0 | Normal
2025-03-15 16:00 | 74 | 3 | Autumn | 16 | 13.12 | -7.9 | 11.76 | 61.8 | 202.4 | 12.14 | 78.88 | 91.02 | 7.9 | 49.68 | 95 | 0 | 0 | 0 | 0 | Normal
2025-03-15 17:00 | 74 | 3 | Autumn | 17 | 13.12 | 0.6 | 7.45 | 47.3 | 154.4 | 9.26 | 8.63 | 17.89 | 0 | 48.9 | 82.6 | -31.01 | 0 | 0 | 0 | Battery-supported
2025-03-15 18:00 | 74 | 3 | Autumn | 18 | 13.12 | -6.4 | 2.06 | 12.3 | 79.5 | 4.77 | 0 | 4.77 | 6.4 | 47.92 | 65.34 | -43.15 | 0 | 0 | 0 | Battery-supported
2025-03-15 19:00 | 74 | 3 | Autumn | 19 | 13.12 | -5.1 | 12.5 | 66.9 | 0 | 0 | 102.03 | 102.03 | 5.1 | 52.43 | 83.59 | 49.6 | 0 | 0 | 0 | Normal
2025-03-15 20:00 | 74 | 3 | Autumn | 20 | 13.12 | -8 | 9.33 | 36.1 | 0 | 0 | 27.73 | 27.73 | 8 | 53.87 | 73.13 | -26.14 | 0 | 0 | 0 | Battery-supported
2025-03-15 21:00 | 74 | 3 | Autumn | 21 | 13.12 | -1.5 | 22.77 | 76.2 | 0 | 0 | 120 | 120 | 1.5 | 45.97 | 95 | 59.42 | 0 | 0 | 0 | Normal
2025-03-15 22:00 | 74 | 3 | Autumn | 22 | 13.12 | -2.9 | 17.57 | 27.1 | 0 | 0 | 120 | 120 | 2.9 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-03-15 23:00 | 74 | 3 | Autumn | 23 | 13.12 | -5 | 18.3 | 57.6 | 0 | 0 | 120 | 120 | 5 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-03-16 | 75 | 3 | Autumn | 0 | 12.96 | -9.1 | 8.42 | 63.8 | 0 | 0 | 16.67 | 16.67 | 9.1 | 45 | 83.67 | -28.33 | 0 | 0 | 0 | Battery-supported
2025-03-16 01:00 | 75 | 3 | Autumn | 1 | 12.96 | -6 | 8.2 | 56.1 | 0 | 0 | 14.53 | 14.53 | 6 | 45 | 71.48 | -30.47 | 0 | 0 | 0 | Battery-supported
2025-03-16 02:00 | 75 | 3 | Autumn | 2 | 12.96 | -9.3 | 9.42 | 58.9 | 0 | 0 | 29.04 | 29.04 | 9.3 | 45 | 65.1 | -15.96 | 0 | 0 | 0 | Battery-supported
2025-03-16 03:00 | 75 | 3 | Autumn | 3 | 12.96 | -4 | 4.85 | 59.9 | 0 | 0 | 0.34 | 0.34 | 4 | 45 | 47.23 | -44.66 | 0 | 0 | 0 | Battery-supported
2025-03-16 04:00 | 75 | 3 | Autumn | 4 | 12.96 | -5.8 | 7.61 | 61.7 | 0 | 0 | 9.72 | 9.72 | 5.8 | 45 | 33.12 | -35.28 | 0 | 0 | 0 | Battery-supported
2025-03-16 05:00 | 75 | 3 | Autumn | 5 | 12.96 | -7.7 | 6.71 | 23.7 | 0 | 0 | 4.63 | 4.63 | 7.7 | 45 | 16.97 | -40.37 | 0 | 0 | 0 | Battery-supported
2025-03-16 06:00 | 75 | 3 | Autumn | 6 | 12.96 | -13.5 | 14.53 | 11.7 | 69.8 | 4.19 | 120 | 124.19 | 13.5 | 45 | 46.11 | 79.19 | 0 | 0 | 0 | Normal
2025-03-16 07:00 | 75 | 3 | Autumn | 7 | 12.96 | -10.5 | 16.21 | 10.7 | 212 | 12.72 | 120 | 132.72 | 10.5 | 45 | 78.39 | 87.72 | 0 | 0 | 0 | Normal
2025-03-16 08:00 | 75 | 3 | Autumn | 8 | 12.96 | -6.8 | 10.94 | 80.3 | 147.5 | 8.85 | 57.64 | 66.49 | 6.8 | 56.39 | 82.11 | 10.1 | 0 | 0 | 0 | Normal
2025-03-16 09:00 | 75 | 3 | Autumn | 9 | 12.96 | -5.6 | 4.33 | 26.7 | 391.8 | 23.51 | 0.08 | 23.59 | 5.6 | 47.32 | 72.62 | -23.73 | 0 | 0 | 0 | Battery-supported
2025-03-16 10:00 | 75 | 3 | Autumn | 10 | 12.96 | -5.7 | 20.39 | 27.9 | 459 | 27.54 | 120 | 147.54 | 5.7 | 51.77 | 95 | 60.82 | 0 | 0 | 0 | Normal
2025-03-16 11:00 | 75 | 3 | Autumn | 11 | 12.96 | -11.4 | 12.5 | 88.5 | 213.9 | 12.83 | 102.03 | 114.86 | 11.4 | 51.61 | 95 | 0 | 0 | 0 | 0 | Normal
2025-03-16 12:00 | 75 | 3 | Autumn | 12 | 12.96 | -6.9 | 9.04 | 70.1 | 310.9 | 18.65 | 23.8 | 42.45 | 6.9 | 53.46 | 90.6 | -11.01 | 0 | 0 | 0 | Battery-supported
2025-03-16 13:00 | 75 | 3 | Autumn | 13 | 12.96 | -5 | 10.35 | 82.7 | 242 | 14.52 | 44.99 | 59.51 | 5 | 49.61 | 94.24 | 9.9 | 0 | 0 | 0 | Normal
2025-03-16 14:00 | 75 | 3 | Autumn | 14 | 12.96 | -10.5 | 2.86 | 62.8 | 307.1 | 18.43 | 0 | 18.43 | 10.5 | 61.46 | 77.03 | -43.03 | 0 | 0 | 0 | Battery-supported
2025-03-16 15:00 | 75 | 3 | Autumn | 15 | 12.96 | -6.5 | 6.72 | 11.3 | 448.7 | 26.92 | 4.67 | 31.59 | 6.5 | 54.77 | 67.76 | -23.18 | 0 | 0 | 0 | Battery-supported
2025-03-16 16:00 | 75 | 3 | Autumn | 16 | 12.96 | -5.5 | 15.23 | 2.3 | 364.8 | 21.89 | 120 | 141.89 | 5.5 | 51.44 | 95 | 74.03 | 0 | 0 | 0 | Normal
2025-03-16 17:00 | 75 | 3 | Autumn | 17 | 12.96 | -6.5 | 2.76 | 77.1 | 97.3 | 5.84 | 0 | 5.84 | 6.5 | 47.15 | 78.48 | -41.31 | 0 | 0 | 0 | Battery-supported
2025-03-16 18:00 | 75 | 3 | Autumn | 18 | 12.96 | -9.6 | 2.7 | 20.6 | 64.6 | 3.88 | 0 | 3.88 | 9.6 | 47.9 | 60.87 | -44.02 | 0 | 0 | 0 | Battery-supported
2025-03-16 19:00 | 75 | 3 | Autumn | 19 | 12.96 | -6.1 | 12.55 | 43.5 | 0 | 0 | 103.74 | 103.74 | 6.1 | 48.54 | 81.18 | 55.2 | 0 | 0 | 0 | Normal
2025-03-16 20:00 | 75 | 3 | Autumn | 20 | 12.96 | -6.1 | 9.93 | 51.4 | 0 | 0 | 37.21 | 37.21 | 6.1 | 49.18 | 76.39 | -11.97 | 0 | 0 | 0 | Battery-supported
2025-03-16 21:00 | 75 | 3 | Autumn | 21 | 12.96 | -5.7 | 2.78 | 69.8 | 0 | 0 | 0 | 0 | 5.7 | 45 | 58.39 | -45 | 0 | 0 | 0 | Battery-supported
2025-03-16 22:00 | 75 | 3 | Autumn | 22 | 12.96 | -6.8 | 6.35 | 43.2 | 0 | 0 | 3.24 | 3.24 | 6.8 | 45 | 41.69 | -41.76 | 0 | 0 | 0 | Battery-supported
2025-03-16 23:00 | 75 | 3 | Autumn | 23 | 12.96 | -6.8 | 9.04 | 25.1 | 0 | 0 | 23.8 | 23.8 | 6.8 | 45 | 33.21 | -21.2 | 0 | 0 | 0 | Battery-supported
2025-03-17 | 76 | 3 | Autumn | 0 | 12.81 | -6.4 | 8.45 | 39.8 | 0 | 0 | 16.98 | 16.98 | 6.4 | 45 | 22 | -28.02 | 0 | 0 | 0 | Battery-supported
2025-03-17 01:00 | 76 | 3 | Autumn | 1 | 12.81 | -5.7 | 9.5 | 9.6 | 0 | 0 | 30.23 | 30.23 | 5.7 | 46.8 | 15.37 | -16.57 | 0 | 0 | 0 | Battery-supported
2025-03-17 02:00 | 76 | 3 | Autumn | 2 | 12.81 | -7.7 | 6.08 | 88 | 0 | 0 | 2.4 | 2.4 | 7.7 | 45 | 15 | -0.93 | 41.67 | 13.511 | 0 | Diesel-backup
2025-03-17 03:00 | 76 | 3 | Autumn | 3 | 12.81 | -8.3 | 8.71 | 58.6 | 0 | 0 | 19.79 | 19.79 | 8.3 | 45 | 15 | 0 | 25.21 | 8.706 | 0 | Diesel-backup
2025-03-17 04:00 | 76 | 3 | Autumn | 4 | 12.81 | -7.6 | 10.97 | 20.3 | 0 | 0 | 58.34 | 58.34 | 7.6 | 46.7 | 19.28 | 11.64 | 0 | 0 | 0 | Normal
2025-03-17 05:00 | 76 | 3 | Autumn | 5 | 12.81 | -12.3 | 10.48 | 61.5 | 0 | 0 | 47.6 | 47.6 | 12.3 | 48.14 | 19.07 | -0.54 | 0 | 0 | 0 | Battery-supported
2025-03-17 06:00 | 76 | 3 | Autumn | 6 | 12.81 | -7.3 | 6.19 | 33.7 | 48.6 | 2.92 | 2.72 | 5.64 | 7.3 | 45 | 15 | -10.17 | 29.19 | 9.932 | 0 | Diesel-backup
2025-03-17 07:00 | 76 | 3 | Autumn | 7 | 12.81 | -8.5 | 11.56 | 93.4 | 66.3 | 3.98 | 73.29 | 77.27 | 8.5 | 45 | 26.88 | 32.27 | 0 | 0 | 0 | Normal
2025-03-17 08:00 | 76 | 3 | Autumn | 8 | 12.81 | -8.4 | 4.02 | 67.3 | 180.7 | 10.84 | 0.02 | 10.86 | 8.4 | 56.44 | 15 | -29.69 | 15.89 | 5.677 | 0 | Diesel-backup
2025-03-17 09:00 | 76 | 3 | Autumn | 9 | 12.81 | -6.4 | 5 | 35.3 | 357.4 | 21.44 | 0.47 | 21.91 | 6.4 | 56.16 | 15 | 0 | 34.25 | 11.431 | 0 | Diesel-backup
2025-03-17 10:00 | 76 | 3 | Autumn | 10 | 12.81 | -12.6 | 12.58 | 62.9 | 305.8 | 18.35 | 104.78 | 123.13 | 12.6 | 52.91 | 40.84 | 70.22 | 0 | 0 | 0 | Normal
2025-03-17 11:00 | 76 | 3 | Autumn | 11 | 12.81 | -12.4 | 11.42 | 27.3 | 506.2 | 30.37 | 69.53 | 99.9 | 12.4 | 56.59 | 56.78 | 43.31 | 0 | 0 | 0 | Normal
2025-03-17 12:00 | 76 | 3 | Autumn | 12 | 12.81 | -7.2 | 6.54 | 68.9 | 316.9 | 19.01 | 3.93 | 22.94 | 7.2 | 51.96 | 45.17 | -29.02 | 0 | 0 | 0 | Battery-supported
2025-03-17 13:00 | 76 | 3 | Autumn | 13 | 12.81 | -7.4 | 4.94 | 63.5 | 333.3 | 20 | 0.42 | 20.42 | 7.4 | 45 | 35.34 | -24.58 | 0 | 0 | 0 | Battery-supported
2025-03-17 14:00 | 76 | 3 | Autumn | 14 | 12.81 | -6.7 | 5.37 | 30.5 | 446.3 | 26.78 | 0.92 | 27.7 | 6.7 | 49.53 | 26.61 | -21.83 | 0 | 0 | 0 | Battery-supported
2025-03-17 15:00 | 76 | 3 | Autumn | 15 | 12.81 | -7.7 | 10.69 | 82.8 | 184.2 | 11.05 | 52.02 | 63.07 | 7.7 | 45 | 33.26 | 18.07 | 0 | 0 | 0 | Normal
2025-03-17 16:00 | 76 | 3 | Autumn | 16 | 12.81 | -4.8 | 9.56 | 42 | 250 | 15 | 31.15 | 46.15 | 4.8 | 47.73 | 32.62 | -1.58 | 0 | 0 | 0 | Battery-supported
2025-03-17 17:00 | 76 | 3 | Autumn | 17 | 12.81 | -3.9 | 4.74 | 18.8 | 190.3 | 11.42 | 0.27 | 11.69 | 3.9 | 55.95 | 15 | -44.06 | 0.2 | 0.075 | 0 | Diesel-backup
2025-03-17 18:00 | 76 | 3 | Autumn | 18 | 12.81 | -4.7 | 11.37 | 48.3 | 41.5 | 2.49 | 68.22 | 70.71 | 4.7 | 45 | 24.46 | 25.71 | 0 | 0 | 0 | Normal
2025-03-17 19:00 | 76 | 3 | Autumn | 19 | 12.81 | -6.2 | 6.36 | 6.1 | 0 | 0 | 3.27 | 3.27 | 6.2 | 56.71 | 15 | -23.65 | 29.79 | 10.112 | 0 | Diesel-backup
2025-03-17 20:00 | 76 | 3 | Autumn | 20 | 12.81 | -10.2 | 4.11 | 49.4 | 0 | 0 | 0.03 | 0.03 | 10.2 | 60.31 | 15 | 0 | 60.28 | 19.29 | 0 | Diesel-backup
2025-03-17 21:00 | 76 | 3 | Autumn | 21 | 12.81 | -3.9 | 5.72 | 34.4 | 0 | 0 | 1.53 | 1.53 | 3.9 | 45 | 15 | 0 | 43.47 | 13.996 | 0 | Diesel-backup
2025-03-17 22:00 | 76 | 3 | Autumn | 22 | 12.81 | -3 | 7.98 | 48.8 | 0 | 0 | 12.58 | 12.58 | 3 | 45 | 15 | 0 | 32.42 | 10.896 | 0 | Diesel-backup
2025-03-17 23:00 | 76 | 3 | Autumn | 23 | 12.81 | -4.6 | 11.15 | 32.4 | 0 | 0 | 62.66 | 62.66 | 4.6 | 45 | 21.5 | 17.66 | 0 | 0 | 0 | Normal
2025-03-18 | 77 | 3 | Autumn | 0 | 12.66 | -8.4 | 10.78 | 65.2 | 0 | 0 | 54 | 54 | 8.4 | 45 | 24.81 | 9 | 0 | 0 | 0 | Normal
2025-03-18 01:00 | 77 | 3 | Autumn | 1 | 12.66 | -5.3 | 7.14 | 21.4 | 0 | 0 | 6.75 | 6.75 | 5.3 | 45 | 15 | -24.53 | 13.72 | 4.941 | 0 | Diesel-backup
2025-03-18 02:00 | 77 | 3 | Autumn | 2 | 12.66 | -5.3 | 8.58 | 37.2 | 0 | 0 | 18.35 | 18.35 | 5.3 | 45 | 15 | 0 | 26.65 | 9.154 | 0 | Diesel-backup
2025-03-18 03:00 | 77 | 3 | Autumn | 3 | 12.66 | -4.2 | 6.77 | 94.8 | 0 | 0 | 4.89 | 4.89 | 4.2 | 45 | 15 | 0 | 40.11 | 13.086 | 0 | Diesel-backup
2025-03-18 04:00 | 77 | 3 | Autumn | 4 | 12.66 | -9.9 | 4.76 | 65.7 | 0 | 0 | 0.28 | 0.28 | 9.9 | 45.07 | 15 | 0 | 44.79 | 14.345 | 0 | Diesel-backup
2025-03-18 05:00 | 77 | 3 | Autumn | 5 | 12.66 | -8.8 | 7.3 | 24.7 | 0 | 0 | 7.68 | 7.68 | 8.8 | 45 | 15 | 0 | 37.32 | 12.309 | 0 | Diesel-backup
2025-03-18 06:00 | 77 | 3 | Autumn | 6 | 12.66 | -6.9 | 2.07 | 11.2 | 48.8 | 2.93 | 0 | 2.93 | 6.9 | 45 | 15 | 0 | 42.07 | 13.62 | 0 | Diesel-backup
2025-03-18 07:00 | 77 | 3 | Autumn | 7 | 12.66 | -8.5 | 16.5 | 37.6 | 152.4 | 9.14 | 120 | 129.14 | 8.5 | 46.44 | 45.43 | 82.7 | 0 | 0 | 0 | Normal
2025-03-18 08:00 | 77 | 3 | Autumn | 8 | 12.66 | -11.2 | 8.45 | 76.6 | 152.5 | 9.15 | 16.98 | 26.13 | 11.2 | 58.69 | 32.41 | -32.56 | 0 | 0 | 0 | Battery-supported
2025-03-18 09:00 | 77 | 3 | Autumn | 9 | 12.66 | -7.7 | 9.81 | 75 | 210.8 | 12.65 | 35.16 | 47.81 | 7.7 | 48.78 | 32.02 | -0.97 | 0 | 0 | 0 | Battery-supported
2025-03-18 10:00 | 77 | 3 | Autumn | 10 | 12.66 | -7.2 | 4.9 | 94.1 | 169.9 | 10.19 | 0.38 | 10.57 | 7.2 | 54.32 | 15 | -42.55 | 1.2 | 0.45 | 0 | Diesel-backup
2025-03-18 11:00 | 77 | 3 | Autumn | 11 | 12.66 | -8.1 | 8.4 | 21 | 535.5 | 32.13 | 16.47 | 48.6 | 8.1 | 59.77 | 15 | 0 | 11.17 | 4.058 | 0 | Diesel-backup
2025-03-18 12:00 | 77 | 3 | Autumn | 12 | 12.66 | -7.5 | 9.24 | 26.1 | 527.3 | 31.64 | 26.47 | 58.11 | 7.5 | 50.62 | 17.76 | 7.49 | 0 | 0 | 0 | Normal
2025-03-18 13:00 | 77 | 3 | Autumn | 13 | 12.66 | -8.2 | 6.58 | 66.6 | 318.3 | 19.1 | 4.09 | 23.19 | 8.2 | 51.67 | 15 | -6.89 | 21.59 | 7.555 | 0 | Diesel-backup
2025-03-18 14:00 | 77 | 3 | Autumn | 14 | 12.66 | -4 | 6.79 | 25.3 | 467.5 | 28.05 | 4.98 | 33.03 | 4 | 49.71 | 15 | 0 | 16.68 | 5.942 | 0 | Diesel-backup
2025-03-18 15:00 | 77 | 3 | Autumn | 15 | 12.66 | -8.8 | 3.2 | 73.9 | 214.9 | 12.89 | 0 | 12.89 | 8.8 | 45 | 15 | 0 | 32.11 | 10.805 | 0 | Diesel-backup
2025-03-18 16:00 | 77 | 3 | Autumn | 16 | 12.66 | -7.8 | 19.48 | 76.7 | 152.2 | 9.13 | 120 | 129.13 | 7.8 | 45.34 | 45.83 | 83.79 | 0 | 0 | 0 | Normal
2025-03-18 17:00 | 77 | 3 | Autumn | 17 | 12.66 | -6.1 | 4.85 | 40.5 | 147.8 | 8.87 | 0.34 | 9.21 | 6.1 | 46.9 | 30.76 | -37.69 | 0 | 0 | 0 | Battery-supported
2025-03-18 18:00 | 77 | 3 | Autumn | 18 | 12.66 | -4 | 5.26 | 46.6 | 34.7 | 2.08 | 0.76 | 2.84 | 4 | 45.64 | 15 | -39.4 | 3.4 | 1.27 | 0 | Diesel-backup
2025-03-18 19:00 | 77 | 3 | Autumn | 19 | 12.66 | -9.1 | 17.09 | 54.8 | 0 | 0 | 120 | 120 | 9.1 | 52.55 | 39.82 | 67.45 | 0 | 0 | 0 | Normal
2025-03-18 20:00 | 77 | 3 | Autumn | 20 | 12.66 | -8.6 | 10.07 | 58.1 | 0 | 0 | 39.69 | 39.69 | 8.6 | 52.67 | 34.63 | -12.98 | 0 | 0 | 0 | Battery-supported
2025-03-18 21:00 | 77 | 3 | Autumn | 21 | 12.66 | -10.2 | 11.24 | 62.1 | 0 | 0 | 64.9 | 64.9 | 10.2 | 45 | 41.95 | 19.9 | 0 | 0 | 0 | Normal
2025-03-18 22:00 | 77 | 3 | Autumn | 22 | 12.66 | -5.8 | 3.05 | 26 | 0 | 0 | 0 | 0 | 5.8 | 45.41 | 23.79 | -45.41 | 0 | 0 | 0 | Battery-supported
2025-03-18 23:00 | 77 | 3 | Autumn | 23 | 12.66 | -8.6 | 8.34 | 84.2 | 0 | 0 | 15.87 | 15.87 | 8.6 | 45 | 15 | -21.97 | 7.16 | 2.637 | 0 | Diesel-backup
2025-03-19 | 78 | 3 | Autumn | 0 | 12.5 | -7.5 | 3.09 | 91.2 | 0 | 0 | 0 | 0 | 7.5 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-03-19 01:00 | 78 | 3 | Autumn | 1 | 12.5 | -5.5 | 4.42 | 45.4 | 0 | 0 | 0.11 | 0.11 | 5.5 | 45 | 15 | 0 | 44.89 | 14.371 | 0 | Diesel-backup
2025-03-19 02:00 | 78 | 3 | Autumn | 2 | 12.5 | -8.8 | 21.12 | 61.1 | 0 | 0 | 120 | 120 | 8.8 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-03-19 03:00 | 78 | 3 | Autumn | 3 | 12.5 | -7.3 | 3.91 | 69.9 | 0 | 0 | 0.01 | 0.01 | 7.3 | 45 | 24.6 | -44.99 | 0 | 0 | 0 | Battery-supported
2025-03-19 04:00 | 78 | 3 | Autumn | 4 | 12.5 | -8.8 | 10.98 | 92.2 | 0 | 0 | 58.58 | 58.58 | 8.8 | 45 | 29.6 | 13.58 | 0 | 0 | 0 | Normal
2025-03-19 05:00 | 78 | 3 | Autumn | 5 | 12.5 | -7 | 4.15 | 56.5 | 0 | 0 | 0.04 | 0.04 | 7 | 45 | 15 | -36.5 | 8.46 | 3.102 | 0 | Diesel-backup
2025-03-19 06:00 | 78 | 3 | Autumn | 6 | 12.5 | -7.6 | 4.49 | 12.2 | 37.5 | 2.25 | 0.14 | 2.39 | 7.6 | 45 | 15 | 0 | 42.61 | 13.766 | 0 | Diesel-backup
2025-03-19 07:00 | 78 | 3 | Autumn | 7 | 12.5 | -10.4 | 28.24 | 99.7 | 51.2 | 3.07 | 0 | 3.07 | 10.4 | 52.3 | 15 | 0 | 49.23 | 15.754 | 0 | Diesel-backup
2025-03-19 08:00 | 78 | 3 | Autumn | 8 | 12.5 | -9.3 | 7.19 | 37.8 | 251.9 | 15.11 | 7.03 | 22.14 | 9.3 | 50.03 | 15 | 0 | 27.89 | 9.536 | 0 | Diesel-backup
2025-03-19 09:00 | 78 | 3 | Autumn | 9 | 12.5 | -6.5 | 2.91 | 35.7 | 350 | 21 | 0 | 21 | 6.5 | 45 | 15 | 0 | 24 | 8.325 | 0 | Diesel-backup
2025-03-19 10:00 | 78 | 3 | Autumn | 10 | 12.5 | -7.8 | 11.24 | 56.5 | 331.2 | 19.87 | 64.9 | 84.77 | 7.8 | 53.06 | 26.67 | 31.71 | 0 | 0 | 0 | Normal
2025-03-19 11:00 | 78 | 3 | Autumn | 11 | 12.5 | -11.5 | 14.79 | 49.1 | 401.3 | 24.08 | 120 | 144.08 | 11.5 | 52.59 | 60.34 | 91.49 | 0 | 0 | 0 | Normal
2025-03-19 12:00 | 78 | 3 | Autumn | 12 | 12.5 | -6.7 | 11.83 | 24.7 | 534.2 | 32.05 | 80.9 | 112.95 | 6.7 | 51.45 | 82.97 | 61.5 | 0 | 0 | 0 | Normal
2025-03-19 13:00 | 78 | 3 | Autumn | 13 | 12.5 | -10.2 | 6.82 | 18.8 | 545.7 | 32.74 | 5.12 | 37.86 | 10.2 | 55.84 | 75.78 | -17.98 | 0 | 0 | 0 | Battery-supported
2025-03-19 14:00 | 78 | 3 | Autumn | 14 | 12.5 | -4.3 | 6.95 | 78.6 | 236 | 14.16 | 5.75 | 19.91 | 4.3 | 45.27 | 65.63 | -25.36 | 0 | 0 | 0 | Battery-supported
2025-03-19 15:00 | 78 | 3 | Autumn | 15 | 12.5 | -4.8 | 5.48 | 78.2 | 197.9 | 11.87 | 1.09 | 12.96 | 4.8 | 49.46 | 51.03 | -36.5 | 0 | 0 | 0 | Battery-supported
2025-03-19 16:00 | 78 | 3 | Autumn | 16 | 12.5 | -6 | 3.6 | 17.4 | 305.6 | 18.34 | 0 | 18.34 | 6 | 48.86 | 38.83 | -30.52 | 0 | 0 | 0 | Battery-supported
2025-03-19 17:00 | 78 | 3 | Autumn | 17 | 12.5 | -6 | 9.17 | 4.6 | 195.8 | 11.75 | 25.51 | 37.26 | 6 | 45 | 35.73 | -7.74 | 0 | 0 | 0 | Battery-supported
2025-03-19 18:00 | 78 | 3 | Autumn | 18 | 12.5 | -6.6 | 6.62 | 64.9 | 21.2 | 1.27 | 4.25 | 5.52 | 6.6 | 47.5 | 18.94 | -41.98 | 0 | 0 | 0 | Battery-supported
2025-03-19 19:00 | 78 | 3 | Autumn | 19 | 12.5 | -4.5 | 3.12 | 29.1 | 0 | 0 | 0 | 0 | 4.5 | 45 | 15 | -9.84 | 35.16 | 11.693 | 0 | Diesel-backup
2025-03-19 20:00 | 78 | 3 | Autumn | 20 | 12.5 | -6.7 | 7.29 | 19.8 | 0 | 0 | 7.62 | 7.62 | 6.7 | 45 | 15 | 0 | 37.38 | 12.326 | 0 | Diesel-backup
2025-03-19 21:00 | 78 | 3 | Autumn | 21 | 12.5 | -5.4 | 4.89 | 62.9 | 0 | 0 | 0.38 | 0.38 | 5.4 | 45 | 15 | 0 | 44.62 | 14.3 | 0 | Diesel-backup
2025-03-19 22:00 | 78 | 3 | Autumn | 22 | 12.5 | -4.2 | 8.89 | 33.9 | 0 | 0 | 21.92 | 21.92 | 4.2 | 45 | 15 | 0 | 23.08 | 8.033 | 0 | Diesel-backup
2025-03-19 23:00 | 78 | 3 | Autumn | 23 | 12.5 | -7.6 | 8.39 | 23.8 | 0 | 0 | 16.37 | 16.37 | 7.6 | 45 | 15 | 0 | 28.63 | 9.762 | 0 | Diesel-backup
2025-03-20 | 79 | 3 | Autumn | 0 | 12.35 | -8.2 | 6.09 | 46.9 | 0 | 0 | 2.43 | 2.43 | 8.2 | 45 | 15 | 0 | 42.57 | 13.755 | 0 | Diesel-backup
2025-03-20 01:00 | 79 | 3 | Autumn | 1 | 12.35 | -9.8 | 7.53 | 48 | 0 | 0 | 9.16 | 9.16 | 9.8 | 45 | 15 | 0 | 35.84 | 11.889 | 0 | Diesel-backup
2025-03-20 02:00 | 79 | 3 | Autumn | 2 | 12.35 | -9.9 | 7.91 | 41.1 | 0 | 0 | 12 | 12 | 9.9 | 45 | 15 | 0 | 33 | 11.067 | 0 | Diesel-backup
2025-03-20 03:00 | 79 | 3 | Autumn | 3 | 12.35 | -12 | 12.71 | 47.1 | 0 | 0 | 109.34 | 109.34 | 12 | 46.99 | 37.94 | 62.35 | 0 | 0 | 0 | Normal
2025-03-20 04:00 | 79 | 3 | Autumn | 4 | 12.35 | -6.7 | 7.37 | 61.5 | 0 | 0 | 8.11 | 8.11 | 6.7 | 45 | 23.19 | -36.89 | 0 | 0 | 0 | Battery-supported
2025-03-20 05:00 | 79 | 3 | Autumn | 5 | 12.35 | -4.7 | 5.58 | 82.6 | 0 | 0 | 1.26 | 1.26 | 4.7 | 45 | 15 | -20.47 | 23.27 | 8.093 | 0 | Diesel-backup
2025-03-20 06:00 | 79 | 3 | Autumn | 6 | 12.35 | -5.7 | 6.46 | 59.5 | 16 | 0.96 | 3.63 | 4.59 | 5.7 | 45 | 15 | 0 | 40.41 | 13.169 | 0 | Diesel-backup
2025-03-20 07:00 | 79 | 3 | Autumn | 7 | 12.35 | -12.6 | 18.81 | 72.1 | 88.6 | 5.32 | 120 | 125.32 | 12.6 | 45.31 | 44.44 | 80.01 | 0 | 0 | 0 | Normal
2025-03-20 08:00 | 79 | 3 | Autumn | 8 | 12.35 | -7.5 | 4.27 | 57.5 | 196 | 11.76 | 0.06 | 11.82 | 7.5 | 47.8 | 30.05 | -35.98 | 0 | 0 | 0 | Battery-supported
2025-03-20 09:00 | 79 | 3 | Autumn | 9 | 12.35 | -5.9 | 6.71 | 71 | 221.5 | 13.29 | 4.63 | 17.92 | 5.9 | 48.09 | 17.98 | -30.17 | 0 | 0 | 0 | Battery-supported
2025-03-20 10:00 | 79 | 3 | Autumn | 10 | 12.35 | -9.9 | 6.65 | 64.5 | 295.8 | 17.75 | 4.37 | 22.12 | 9.9 | 45 | 15 | -7.46 | 15.42 | 5.519 | 0 | Diesel-backup
2025-03-20 11:00 | 79 | 3 | Autumn | 11 | 12.35 | -8.4 | 6.82 | 18.9 | 544.7 | 32.68 | 5.12 | 37.8 | 8.4 | 52.57 | 15 | 0 | 14.77 | 5.298 | 0 | Diesel-backup
2025-03-20 12:00 | 79 | 3 | Autumn | 12 | 12.35 | -12.7 | 2.34 | 89.9 | 213.8 | 12.83 | 0 | 12.83 | 12.7 | 50.67 | 15 | 0 | 37.84 | 12.456 | 0 | Diesel-backup
2025-03-20 13:00 | 79 | 3 | Autumn | 13 | 12.35 | -7.4 | 3.53 | 23.7 | 521.9 | 31.31 | 0 | 31.31 | 7.4 | 55.24 | 15 | 0 | 23.93 | 8.303 | 0 | Diesel-backup
2025-03-20 14:00 | 79 | 3 | Autumn | 14 | 12.35 | -9.9 | 6.44 | 38.3 | 408.4 | 24.5 | 3.56 | 28.06 | 9.9 | 46.05 | 15 | 0 | 17.99 | 6.379 | 0 | Diesel-backup
2025-03-20 15:00 | 79 | 3 | Autumn | 15 | 12.35 | -6.7 | 5.41 | 77.6 | 198.1 | 11.89 | 0.98 | 12.87 | 6.7 | 51.18 | 15 | 0 | 38.31 | 12.587 | 0 | Diesel-backup
2025-03-20 16:00 | 79 | 3 | Autumn | 16 | 12.35 | -10.3 | 8.9 | 85.1 | 124.6 | 7.48 | 22.04 | 29.52 | 10.3 | 45.34 | 15 | 0 | 15.82 | 5.653 | 0 | Diesel-backup
2025-03-20 17:00 | 79 | 3 | Autumn | 17 | 12.35 | -5.3 | 13.74 | 54.2 | 114.5 | 6.87 | 120 | 126.87 | 5.3 | 45.72 | 44.86 | 81.15 | 0 | 0 | 0 | Normal
2025-03-20 18:00 | 79 | 3 | Autumn | 18 | 12.35 | -4 | 9.3 | 40.4 | 20.2 | 1.21 | 27.31 | 28.52 | 4 | 48.58 | 36.84 | -20.06 | 0 | 0 | 0 | Battery-supported
2025-03-20 19:00 | 79 | 3 | Autumn | 19 | 12.35 | -7.8 | 8.08 | 57.4 | 0 | 0 | 13.45 | 13.45 | 7.8 | 54.47 | 20.43 | -41.02 | 0 | 0 | 0 | Battery-supported
2025-03-20 20:00 | 79 | 3 | Autumn | 20 | 12.35 | -8.6 | 9.83 | 32 | 0 | 0 | 35.5 | 35.5 | 8.6 | 55.07 | 15 | -13.58 | 5.99 | 2.217 | 0 | Diesel-backup
2025-03-20 21:00 | 79 | 3 | Autumn | 21 | 12.35 | -10.9 | 8.52 | 20.7 | 0 | 0 | 17.71 | 17.71 | 10.9 | 48.65 | 15 | 0 | 30.94 | 10.458 | 0 | Diesel-backup
2025-03-20 22:00 | 79 | 3 | Autumn | 22 | 12.35 | -6.9 | 7.49 | 59.2 | 0 | 0 | 8.89 | 8.89 | 6.9 | 45.09 | 15 | 0 | 36.2 | 11.992 | 0 | Diesel-backup
2025-03-20 23:00 | 79 | 3 | Autumn | 23 | 12.35 | -7.8 | 12.45 | 23 | 0 | 0 | 100.34 | 100.34 | 7.8 | 46.33 | 34.88 | 54.01 | 0 | 0 | 0 | Normal
2025-03-21 | 80 | 3 | Autumn | 0 | 12.19 | -10.4 | 0.49 | 26 | 0 | 0 | 0 | 0 | 10.4 | 45 | 16.88 | -45 | 0 | 0 | 0 | Battery-supported
2025-03-21 01:00 | 80 | 3 | Autumn | 1 | 12.19 | -6.4 | 6.35 | 32.4 | 0 | 0 | 3.24 | 3.24 | 6.4 | 45 | 15 | -4.69 | 37.07 | 12.239 | 0 | Diesel-backup
2025-03-21 02:00 | 80 | 3 | Autumn | 2 | 12.19 | -8.8 | 3.51 | 30.9 | 0 | 0 | 0 | 0 | 8.8 | 46.48 | 15 | 0 | 46.48 | 14.874 | 0 | Diesel-backup
2025-03-21 03:00 | 80 | 3 | Autumn | 3 | 12.19 | -10.5 | 5.32 | 61.8 | 0 | 0 | 0.84 | 0.84 | 10.5 | 49.85 | 15 | 0 | 49.01 | 15.683 | 0 | Diesel-backup
2025-03-21 04:00 | 80 | 3 | Autumn | 4 | 12.19 | -9.7 | 4.89 | 67.2 | 0 | 0 | 0.38 | 0.38 | 9.7 | 45 | 15 | 0 | 44.62 | 14.3 | 0 | Diesel-backup
2025-03-21 05:00 | 80 | 3 | Autumn | 5 | 12.19 | -6.5 | 21.7 | 25 | 0 | 0 | 120 | 120 | 6.5 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-03-21 06:00 | 80 | 3 | Autumn | 6 | 12.19 | -7.7 | 14.24 | 44.5 | 10.8 | 0.65 | 120 | 120.65 | 7.7 | 45 | 70.44 | 75.65 | 0 | 0 | 0 | Normal
2025-03-21 07:00 | 80 | 3 | Autumn | 7 | 12.19 | -9.5 | 8.17 | 53.4 | 109.6 | 6.58 | 14.25 | 20.83 | 9.5 | 45 | 60.77 | -24.17 | 0 | 0 | 0 | Battery-supported
2025-03-21 08:00 | 80 | 3 | Autumn | 8 | 12.19 | -7.9 | 4.97 | 15 | 299.4 | 17.96 | 0.44 | 18.4 | 7.9 | 52.68 | 47.06 | -34.28 | 0 | 0 | 0 | Battery-supported
2025-03-21 09:00 | 80 | 3 | Autumn | 9 | 12.19 | -11.8 | 12.42 | 64.7 | 241.8 | 14.51 | 99.34 | 113.85 | 11.8 | 59.23 | 67.16 | 54.62 | 0 | 0 | 0 | Normal
2025-03-21 10:00 | 80 | 3 | Autumn | 10 | 12.19 | -9 | 7.99 | 61.6 | 306.9 | 18.41 | 12.67 | 31.08 | 9 | 53.84 | 58.06 | -22.76 | 0 | 0 | 0 | Battery-supported
2025-03-21 11:00 | 80 | 3 | Autumn | 11 | 12.19 | -8.5 | 6.36 | 67.2 | 314.4 | 18.86 | 3.27 | 22.13 | 8.5 | 51.32 | 46.38 | -29.19 | 0 | 0 | 0 | Battery-supported
2025-03-21 12:00 | 80 | 3 | Autumn | 12 | 12.19 | -9.5 | 8.03 | 86.5 | 230.2 | 13.81 | 13.01 | 26.82 | 9.5 | 60.07 | 33.08 | -33.25 | 0 | 0 | 0 | Battery-supported
2025-03-21 13:00 | 80 | 3 | Autumn | 13 | 12.19 | -7.2 | 6.47 | 47.7 | 407.3 | 24.44 | 3.67 | 28.11 | 7.2 | 50.13 | 24.27 | -22.02 | 0 | 0 | 0 | Battery-supported
2025-03-21 14:00 | 80 | 3 | Autumn | 14 | 12.19 | -9.5 | 9.8 | 18.3 | 492.5 | 29.55 | 35 | 64.55 | 9.5 | 57.98 | 26.69 | 6.57 | 0 | 0 | 0 | Normal
2025-03-21 15:00 | 80 | 3 | Autumn | 15 | 12.19 | -6.3 | 3.3 | 61.5 | 253 | 15.18 | 0 | 15.18 | 6.3 | 45 | 15 | -29.22 | 0.6 | 0.225 | 0 | Diesel-backup
2025-03-21 16:00 | 80 | 3 | Autumn | 16 | 12.19 | -5.8 | 9.76 | 39.5 | 237.4 | 14.24 | 34.33 | 48.57 | 5.8 | 49.63 | 15 | 0 | 1.06 | 0.399 | 0 | Diesel-backup
2025-03-21 17:00 | 80 | 3 | Autumn | 17 | 12.19 | -13.1 | 6.46 | 38.2 | 130.4 | 7.82 | 3.63 | 11.45 | 13.1 | 52.14 | 15 | 0 | 40.69 | 13.245 | 0 | Diesel-backup
2025-03-21 18:00 | 80 | 3 | Autumn | 18 | 12.19 | -3.8 | 12.58 | 26 | 13.1 | 0.79 | 104.78 | 105.57 | 3.8 | 45 | 37.29 | 60.57 | 0 | 0 | 0 | Normal
2025-03-21 19:00 | 80 | 3 | Autumn | 19 | 12.19 | -13 | 14.42 | 33.7 | 0 | 0 | 120 | 120 | 13 | 52.74 | 62.04 | 67.26 | 0 | 0 | 0 | Normal
2025-03-21 20:00 | 80 | 3 | Autumn | 20 | 12.19 | -7.6 | 16.15 | 61.9 | 0 | 0 | 120 | 120 | 7.6 | 50.84 | 87.49 | 69.16 | 0 | 0 | 0 | Normal
2025-03-21 21:00 | 80 | 3 | Autumn | 21 | 12.19 | -4.1 | 24.95 | 69.9 | 0 | 0 | 120 | 120 | 4.1 | 45 | 95 | 20.4 | 0 | 0 | 0 | Normal
2025-03-21 22:00 | 80 | 3 | Autumn | 22 | 12.19 | -7.2 | 22.59 | 42.2 | 0 | 0 | 120 | 120 | 7.2 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-03-21 23:00 | 80 | 3 | Autumn | 23 | 12.19 | -9.9 | 15.84 | 33.6 | 0 | 0 | 120 | 120 | 9.9 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-03-22 | 81 | 3 | Autumn | 0 | 12.04 | -9.6 | 12.4 | 83.5 | 0 | 0 | 98.67 | 98.67 | 9.6 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-03-22 01:00 | 81 | 3 | Autumn | 1 | 12.04 | -5.3 | 3.62 | 24.2 | 0 | 0 | 0 | 0 | 5.3 | 45 | 77 | -45 | 0 | 0 | 0 | Battery-supported
2025-03-22 02:00 | 81 | 3 | Autumn | 2 | 12.04 | -12.2 | 1.37 | 45 | 0 | 0 | 0 | 0 | 12.2 | 49.01 | 57.4 | -49.01 | 0 | 0 | 0 | Battery-supported
2025-03-22 03:00 | 81 | 3 | Autumn | 3 | 12.04 | -5.9 | 13.35 | 45.2 | 0 | 0 | 120 | 120 | 5.9 | 45 | 85 | 75 | 0 | 0 | 0 | Normal
2025-03-22 04:00 | 81 | 3 | Autumn | 4 | 12.04 | -8.8 | 4.46 | 18.1 | 0 | 0 | 0.12 | 0.12 | 8.8 | 46.27 | 66.54 | -46.15 | 0 | 0 | 0 | Battery-supported
2025-03-22 05:00 | 81 | 3 | Autumn | 5 | 12.04 | -11.6 | 31.33 | 91.5 | 0 | 0 | 0 | 0 | 11.6 | 53.41 | 45.17 | -53.41 | 0 | 0 | 0 | Battery-supported
2025-03-22 06:00 | 81 | 3 | Autumn | 6 | 12.04 | -10.5 | 2.71 | 14.8 | 2.9 | 0.17 | 0 | 0.17 | 10.5 | 45 | 27.24 | -44.83 | 0 | 0 | 0 | Battery-supported
2025-03-22 07:00 | 81 | 3 | Autumn | 7 | 12.04 | -11.6 | 12.11 | 49.6 | 108.3 | 6.5 | 89.33 | 95.83 | 11.6 | 45 | 45.95 | 50.83 | 0 | 0 | 0 | Normal
2025-03-22 08:00 | 81 | 3 | Autumn | 8 | 12.04 | -7.5 | 8.57 | 24 | 270.4 | 16.22 | 18.24 | 34.46 | 7.5 | 50.36 | 39.59 | -15.9 | 0 | 0 | 0 | Battery-supported
2025-03-22 09:00 | 81 | 3 | Autumn | 9 | 12.04 | -7.8 | 2.93 | 46.3 | 303.5 | 18.21 | 0 | 18.21 | 7.8 | 50.32 | 26.74 | -32.11 | 0 | 0 | 0 | Battery-supported
2025-03-22 10:00 | 81 | 3 | Autumn | 10 | 12.04 | -13 | 8.54 | 73.6 | 254.9 | 15.29 | 17.92 | 33.21 | 13 | 56.53 | 17.41 | -23.32 | 0 | 0 | 0 | Battery-supported
2025-03-22 11:00 | 81 | 3 | Autumn | 11 | 12.04 | -9.9 | 4.82 | 70.6 | 298.2 | 17.89 | 0.32 | 18.21 | 9.9 | 56.24 | 15 | -6.03 | 32 | 10.771 | 0 | Diesel-backup
2025-03-22 12:00 | 81 | 3 | Autumn | 12 | 12.04 | -10.6 | 7.28 | 50.8 | 406 | 24.36 | 7.56 | 31.92 | 10.6 | 52.58 | 15 | 0 | 20.66 | 7.255 | 0 | Diesel-backup
2025-03-22 13:00 | 81 | 3 | Autumn | 13 | 12.04 | -5.5 | 7.34 | 15.7 | 559.3 | 33.56 | 7.93 | 41.49 | 5.5 | 52.63 | 15 | 0 | 11.14 | 4.048 | 0 | Diesel-backup
2025-03-22 14:00 | 81 | 3 | Autumn | 14 | 12.04 | -10.9 | 4.86 | 80.2 | 226.4 | 13.58 | 0.35 | 13.93 | 10.9 | 50.81 | 15 | 0 | 36.88 | 12.185 | 0 | Diesel-backup
2025-03-22 15:00 | 81 | 3 | Autumn | 15 | 12.04 | -4 | 6.14 | 75.6 | 201.3 | 12.08 | 2.58 | 14.66 | 4 | 45 | 15 | 0 | 30.34 | 10.278 | 0 | Diesel-backup
2025-03-22 16:00 | 81 | 3 | Autumn | 16 | 12.04 | -7.3 | 4.57 | 59 | 183.9 | 11.03 | 0.17 | 11.2 | 7.3 | 45.86 | 15 | 0 | 34.66 | 11.55 | 0 | Diesel-backup
2025-03-22 17:00 | 81 | 3 | Autumn | 17 | 12.04 | -9.4 | 2.16 | 57.3 | 98.3 | 5.9 | 0 | 5.9 | 9.4 | 45 | 15 | 0 | 39.1 | 12.807 | 0 | Diesel-backup
2025-03-22 18:00 | 81 | 3 | Autumn | 18 | 12.04 | -8.1 | 8.13 | 50.7 | 2 | 0.12 | 13.89 | 14.01 | 8.1 | 45 | 15 | 0 | 30.99 | 10.473 | 0 | Diesel-backup
2025-03-22 19:00 | 81 | 3 | Autumn | 19 | 12.04 | -8.3 | 15.85 | 47.9 | 0 | 0 | 120 | 120 | 8.3 | 54.88 | 38.96 | 65.12 | 0 | 0 | 0 | Normal
2025-03-22 20:00 | 81 | 3 | Autumn | 20 | 12.04 | -9.3 | 4.74 | 51.3 | 0 | 0 | 0.27 | 0.27 | 9.3 | 56.71 | 16.39 | -56.44 | 0 | 0 | 0 | Battery-supported
2025-03-22 21:00 | 81 | 3 | Autumn | 21 | 12.04 | -6.3 | 20.28 | 87.4 | 0 | 0 | 120 | 120 | 6.3 | 45 | 43.99 | 75 | 0 | 0 | 0 | Normal
2025-03-22 22:00 | 81 | 3 | Autumn | 22 | 12.04 | -9.3 | 22.62 | 47.5 | 0 | 0 | 120 | 120 | 9.3 | 48.03 | 70.47 | 71.97 | 0 | 0 | 0 | Normal
2025-03-22 23:00 | 81 | 3 | Autumn | 23 | 12.04 | -11.7 | 5.83 | 64.7 | 0 | 0 | 1.77 | 1.77 | 11.7 | 45 | 53.18 | -43.23 | 0 | 0 | 0 | Battery-supported
2025-03-23 | 82 | 3 | Autumn | 0 | 11.88 | -8.2 | 6.71 | 67.2 | 0 | 0 | 4.63 | 4.63 | 8.2 | 45 | 37.03 | -40.37 | 0 | 0 | 0 | Battery-supported
2025-03-23 01:00 | 82 | 3 | Autumn | 1 | 11.88 | -11.7 | 5.92 | 36.1 | 0 | 0 | 1.98 | 1.98 | 11.7 | 45 | 19.83 | -43.02 | 0 | 0 | 0 | Battery-supported
2025-03-23 02:00 | 82 | 3 | Autumn | 2 | 11.88 | -9.8 | 3.67 | 15.5 | 0 | 0 | 0 | 0 | 9.8 | 49.01 | 15 | -12.06 | 36.95 | 12.204 | 0 | Diesel-backup
2025-03-23 03:00 | 82 | 3 | Autumn | 3 | 11.88 | -10.5 | 6.73 | 35 | 0 | 0 | 4.72 | 4.72 | 10.5 | 52.73 | 15 | 0 | 48.01 | 15.363 | 0 | Diesel-backup
2025-03-23 04:00 | 82 | 3 | Autumn | 4 | 11.88 | -10.8 | 6.28 | 29.2 | 0 | 0 | 3.01 | 3.01 | 10.8 | 45 | 15 | 0 | 41.99 | 13.599 | 0 | Diesel-backup
2025-03-23 05:00 | 82 | 3 | Autumn | 5 | 11.88 | -4.8 | 8.08 | 80.3 | 0 | 0 | 13.45 | 13.45 | 4.8 | 45 | 15 | 0 | 31.55 | 10.639 | 0 | Diesel-backup
2025-03-23 06:00 | 82 | 3 | Autumn | 6 | 11.88 | -9.3 | 8.33 | 36.7 | 0 | 0 | 15.77 | 15.77 | 9.3 | 48.46 | 15 | 0 | 32.69 | 10.976 | 0 | Diesel-backup
2025-03-23 07:00 | 82 | 3 | Autumn | 7 | 11.88 | -9 | 3.49 | 72.4 | 73.9 | 4.43 | 0 | 4.43 | 9 | 52.99 | 15 | 0 | 48.56 | 15.539 | 0 | Diesel-backup
2025-03-23 08:00 | 82 | 3 | Autumn | 8 | 11.88 | -13.5 | 10.8 | 60.8 | 175.3 | 10.52 | 54.45 | 64.97 | 13.5 | 61.25 | 16.37 | 3.72 | 0 | 0 | 0 | Normal
2025-03-23 09:00 | 82 | 3 | Autumn | 9 | 11.88 | -11 | 6.69 | 40.6 | 320.1 | 19.21 | 4.54 | 23.75 | 11 | 49.16 | 15 | -3.42 | 21.99 | 7.684 | 0 | Diesel-backup
2025-03-23 10:00 | 82 | 3 | Autumn | 10 | 11.88 | -9 | 3.95 | 86.5 | 199 | 11.94 | 0.01 | 11.95 | 9 | 55.5 | 15 | 0 | 43.55 | 14.017 | 0 | Diesel-backup
2025-03-23 11:00 | 82 | 3 | Autumn | 11 | 11.88 | -11.4 | 6.6 | 86.6 | 221.7 | 13.3 | 4.17 | 17.47 | 11.4 | 51.82 | 15 | 0 | 34.35 | 11.46 | 0 | Diesel-backup
2025-03-23 12:00 | 82 | 3 | Autumn | 12 | 11.88 | -6.9 | 8.52 | 26.4 | 526.2 | 31.57 | 17.71 | 49.28 | 6.9 | 55.5 | 15 | 0 | 6.22 | 2.299 | 0 | Diesel-backup
2025-03-23 13:00 | 82 | 3 | Autumn | 13 | 11.88 | -11.2 | 17.57 | 68 | 310.3 | 18.62 | 120 | 138.62 | 11.2 | 56.73 | 45.14 | 81.89 | 0 | 0 | 0 | Normal
2025-03-23 14:00 | 82 | 3 | Autumn | 14 | 11.88 | -8.8 | 16.02 | 9.1 | 527.9 | 31.67 | 120 | 151.67 | 8.8 | 47.71 | 83.39 | 103.96 | 0 | 0 | 0 | Normal
2025-03-23 15:00 | 82 | 3 | Autumn | 15 | 11.88 | -9 | 5.55 | 54.1 | 273.6 | 16.42 | 1.21 | 17.63 | 9 | 56.42 | 67.88 | -38.79 | 0 | 0 | 0 | Battery-supported
2025-03-23 16:00 | 82 | 3 | Autumn | 16 | 11.88 | -7 | 6.96 | 61.2 | 174.4 | 10.46 | 5.8 | 16.26 | 7 | 52.12 | 53.53 | -35.86 | 0 | 0 | 0 | Battery-supported
2025-03-23 17:00 | 82 | 3 | Autumn | 17 | 11.88 | -8.5 | 4.5 | 26.9 | 129.1 | 7.75 | 0.14 | 7.89 | 8.5 | 53.09 | 35.45 | -45.2 | 0 | 0 | 0 | Battery-supported
2025-03-23 18:00 | 82 | 3 | Autumn | 18 | 11.88 | -7.4 | 9.33 | 46.2 | 0 | 0 | 27.73 | 27.73 | 7.4 | 50.52 | 26.34 | -22.79 | 0 | 0 | 0 | Battery-supported
2025-03-23 19:00 | 82 | 3 | Autumn | 19 | 11.88 | -7.2 | 5.74 | 18.2 | 0 | 0 | 1.57 | 1.57 | 7.2 | 48.11 | 15 | -28.34 | 18.2 | 6.448 | 0 | Diesel-backup
2025-03-23 20:00 | 82 | 3 | Autumn | 20 | 11.88 | -8.3 | 6.82 | 16.8 | 0 | 0 | 5.12 | 5.12 | 8.3 | 53.77 | 15 | 0 | 48.65 | 15.568 | 0 | Diesel-backup
2025-03-23 21:00 | 82 | 3 | Autumn | 21 | 11.88 | -5.6 | 13.66 | 80.8 | 0 | 0 | 120 | 120 | 5.6 | 49.41 | 40.98 | 70.59 | 0 | 0 | 0 | Normal
2025-03-23 22:00 | 82 | 3 | Autumn | 22 | 11.88 | -6.3 | 3.48 | 79.3 | 0 | 0 | 0 | 0 | 6.3 | 48.93 | 21.41 | -48.93 | 0 | 0 | 0 | Battery-supported
2025-03-23 23:00 | 82 | 3 | Autumn | 23 | 11.88 | -7.3 | 16.04 | 93.3 | 0 | 0 | 120 | 120 | 7.3 | 45 | 49.01 | 75 | 0 | 0 | 0 | Normal
2025-03-24 | 83 | 3 | Autumn | 0 | 11.73 | -8.5 | 9.9 | 69.7 | 0 | 0 | 36.69 | 36.69 | 8.5 | 45 | 45.68 | -8.31 | 0 | 0 | 0 | Battery-supported
2025-03-24 01:00 | 83 | 3 | Autumn | 1 | 11.73 | -6.2 | 15.68 | 55.3 | 0 | 0 | 120 | 120 | 6.2 | 45 | 73.28 | 75 | 0 | 0 | 0 | Normal
2025-03-24 02:00 | 83 | 3 | Autumn | 2 | 11.73 | -8.8 | 11.8 | 51.6 | 0 | 0 | 80.03 | 80.03 | 8.8 | 45 | 86.17 | 35.03 | 0 | 0 | 0 | Normal
2025-03-24 03:00 | 83 | 3 | Autumn | 3 | 11.73 | -9.4 | 13.02 | 11.8 | 0 | 0 | 120 | 120 | 9.4 | 45.54 | 95 | 23.99 | 0 | 0 | 0 | Normal
2025-03-24 04:00 | 83 | 3 | Autumn | 4 | 11.73 | -8.8 | 7.87 | 85.1 | 0 | 0 | 11.68 | 11.68 | 8.8 | 47.39 | 80.72 | -35.71 | 0 | 0 | 0 | Battery-supported
2025-03-24 05:00 | 83 | 3 | Autumn | 5 | 11.73 | -5.7 | 3.9 | 21.1 | 0 | 0 | 0.01 | 0.01 | 5.7 | 45 | 62.72 | -44.99 | 0 | 0 | 0 | Battery-supported
2025-03-24 06:00 | 83 | 3 | Autumn | 6 | 11.73 | -12.6 | 5.31 | 68 | 0 | 0 | 0.83 | 0.83 | 12.6 | 50.56 | 42.83 | -49.73 | 0 | 0 | 0 | Battery-supported
2025-03-24 07:00 | 83 | 3 | Autumn | 7 | 11.73 | -8.1 | 4.69 | 64 | 78.3 | 4.7 | 0.24 | 4.94 | 8.1 | 45 | 26.8 | -40.06 | 0 | 0 | 0 | Battery-supported
2025-03-24 08:00 | 83 | 3 | Autumn | 8 | 11.73 | -14 | 1.8 | 76.8 | 133.2 | 7.99 | 0 | 7.99 | 14 | 54.91 | 15 | -29.51 | 17.41 | 6.186 | 0 | Diesel-backup
2025-03-24 09:00 | 83 | 3 | Autumn | 9 | 11.73 | -9.3 | 13.7 | 65.3 | 232.4 | 13.94 | 120 | 133.94 | 9.3 | 47.97 | 46.64 | 85.97 | 0 | 0 | 0 | Normal
2025-03-24 10:00 | 83 | 3 | Autumn | 10 | 11.73 | -6.2 | 7.35 | 34 | 420.2 | 25.21 | 7.99 | 33.2 | 6.2 | 50.24 | 39.82 | -17.04 | 0 | 0 | 0 | Battery-supported
2025-03-24 11:00 | 83 | 3 | Autumn | 11 | 11.73 | -8.3 | 4.45 | 30 | 490.2 | 29.41 | 0.12 | 29.53 | 8.3 | 54.76 | 29.73 | -25.23 | 0 | 0 | 0 | Battery-supported
2025-03-24 12:00 | 83 | 3 | Autumn | 12 | 11.73 | -8.7 | 22.29 | 16.3 | 575.7 | 34.54 | 120 | 154.54 | 8.7 | 55.98 | 66 | 98.56 | 0 | 0 | 0 | Normal
2025-03-24 13:00 | 83 | 3 | Autumn | 13 | 11.73 | -9.9 | 27.7 | 17.9 | 547.8 | 32.87 | 120 | 152.87 | 9.9 | 45 | 95 | 78.81 | 0 | 0 | 0 | Normal
2025-03-24 14:00 | 83 | 3 | Autumn | 14 | 11.73 | -8.3 | 3.2 | 23.9 | 462.7 | 27.76 | 0 | 27.76 | 8.3 | 53.18 | 84.83 | -25.42 | 0 | 0 | 0 | Battery-supported
2025-03-24 15:00 | 83 | 3 | Autumn | 15 | 11.73 | -8.5 | 6.76 | 31.2 | 348.9 | 20.93 | 4.85 | 25.78 | 8.5 | 47.33 | 76.21 | -21.55 | 0 | 0 | 0 | Battery-supported
2025-03-24 16:00 | 83 | 3 | Autumn | 16 | 11.73 | -9.3 | 6.49 | 65.1 | 160.9 | 9.65 | 3.74 | 13.39 | 9.3 | 54.66 | 59.7 | -41.27 | 0 | 0 | 0 | Battery-supported
2025-03-24 17:00 | 83 | 3 | Autumn | 17 | 11.73 | -7.9 | 4.22 | 47.4 | 97.1 | 5.83 | 0.05 | 5.88 | 7.9 | 46.71 | 43.37 | -40.83 | 0 | 0 | 0 | Battery-supported
2025-03-24 18:00 | 83 | 3 | Autumn | 18 | 11.73 | -6.6 | 13.52 | 81.7 | 0 | 0 | 120 | 120 | 6.6 | 52.54 | 68.2 | 67.46 | 0 | 0 | 0 | Normal
2025-03-24 19:00 | 83 | 3 | Autumn | 19 | 11.73 | -8.6 | 1.82 | 44.2 | 0 | 0 | 0 | 0 | 8.6 | 49.01 | 48.59 | -49.01 | 0 | 0 | 0 | Battery-supported
2025-03-24 20:00 | 83 | 3 | Autumn | 20 | 11.73 | -8.6 | 19.13 | 28.8 | 0 | 0 | 120 | 120 | 8.6 | 49.1 | 74.68 | 70.9 | 0 | 0 | 0 | Normal
2025-03-24 21:00 | 83 | 3 | Autumn | 21 | 11.73 | -9.9 | 8.07 | 41.3 | 0 | 0 | 13.36 | 13.36 | 9.9 | 48.11 | 60.78 | -34.75 | 0 | 0 | 0 | Battery-supported
2025-03-24 22:00 | 83 | 3 | Autumn | 22 | 11.73 | -6.2 | 21.26 | 31.5 | 0 | 0 | 120 | 120 | 6.2 | 45 | 88.38 | 75 | 0 | 0 | 0 | Normal
2025-03-24 23:00 | 83 | 3 | Autumn | 23 | 11.73 | -6.1 | 7.67 | 60.1 | 0 | 0 | 10.15 | 10.15 | 6.1 | 45 | 74.44 | -34.85 | 0 | 0 | 0 | Battery-supported
2025-03-25 | 84 | 3 | Autumn | 0 | 11.58 | -7.3 | 6.5 | 31 | 0 | 0 | 3.78 | 3.78 | 7.3 | 45.27 | 57.85 | -41.49 | 0 | 0 | 0 | Battery-supported
2025-03-25 01:00 | 84 | 3 | Autumn | 1 | 11.58 | -6 | 14.17 | 26.7 | 0 | 0 | 120 | 120 | 6 | 45 | 85.45 | 75 | 0 | 0 | 0 | Normal
2025-03-25 02:00 | 84 | 3 | Autumn | 2 | 11.58 | -8.3 | 21.26 | 58.4 | 0 | 0 | 120 | 120 | 8.3 | 45 | 95 | 25.96 | 0 | 0 | 0 | Normal
2025-03-25 03:00 | 84 | 3 | Autumn | 3 | 11.58 | -8 | 19.34 | 18.4 | 0 | 0 | 120 | 120 | 8 | 48.1 | 95 | 0 | 0 | 0 | 0 | Normal
2025-03-25 04:00 | 84 | 3 | Autumn | 4 | 11.58 | -8.6 | 2.45 | 74.5 | 0 | 0 | 0 | 0 | 8.6 | 46.92 | 76.23 | -46.92 | 0 | 0 | 0 | Battery-supported
2025-03-25 05:00 | 84 | 3 | Autumn | 5 | 11.58 | -9.8 | 16.55 | 60.3 | 0 | 0 | 120 | 120 | 9.8 | 51.37 | 95 | 51 | 0 | 0 | 0 | Normal
2025-03-25 06:00 | 84 | 3 | Autumn | 6 | 11.58 | -11 | 6.3 | 76.9 | 0 | 0 | 3.07 | 3.07 | 11 | 45 | 78.23 | -41.93 | 0 | 0 | 0 | Battery-supported
2025-03-25 07:00 | 84 | 3 | Autumn | 7 | 11.58 | -5.1 | 7.22 | 59.4 | 77.2 | 4.63 | 7.21 | 11.84 | 5.1 | 45 | 64.96 | -33.16 | 0 | 0 | 0 | Battery-supported
2025-03-25 08:00 | 84 | 3 | Autumn | 8 | 11.58 | -11 | 6.22 | 52.3 | 186 | 11.16 | 2.82 | 13.98 | 11 | 52.18 | 49.68 | -38.2 | 0 | 0 | 0 | Battery-supported
2025-03-25 09:00 | 84 | 3 | Autumn | 9 | 11.58 | -11.4 | 5.33 | 71.5 | 209 | 12.54 | 0.86 | 13.4 | 11.4 | 56.45 | 32.46 | -43.05 | 0 | 0 | 0 | Battery-supported
2025-03-25 10:00 | 84 | 3 | Autumn | 10 | 11.58 | -8.9 | 6.83 | 23.2 | 464.1 | 27.85 | 5.17 | 33.02 | 8.9 | 48.1 | 26.43 | -15.08 | 0 | 0 | 0 | Battery-supported
2025-03-25 11:00 | 84 | 3 | Autumn | 11 | 11.58 | -9 | 4.13 | 43 | 428 | 25.68 | 0.03 | 25.71 | 9 | 48.77 | 17.21 | -23.06 | 0 | 0 | 0 | Battery-supported
2025-03-25 12:00 | 84 | 3 | Autumn | 12 | 11.58 | -12.4 | 16.61 | 25.3 | 531.4 | 31.88 | 120 | 151.88 | 12.4 | 55.56 | 52.65 | 96.32 | 0 | 0 | 0 | Normal
2025-03-25 13:00 | 84 | 3 | Autumn | 13 | 11.58 | -6.4 | 11.74 | 83.5 | 236.1 | 14.17 | 78.31 | 92.48 | 6.4 | 45 | 70.13 | 47.48 | 0 | 0 | 0 | Normal
2025-03-25 14:00 | 84 | 3 | Autumn | 14 | 11.58 | -8.7 | 9.01 | 44.1 | 376 | 22.56 | 23.41 | 45.97 | 8.7 | 45 | 70.48 | 0.97 | 0 | 0 | 0 | Normal
2025-03-25 15:00 | 84 | 3 | Autumn | 15 | 11.58 | -10.6 | 6.22 | 24.8 | 366.7 | 22 | 2.82 | 24.82 | 10.6 | 53.14 | 59.16 | -28.32 | 0 | 0 | 0 | Battery-supported
2025-03-25 16:00 | 84 | 3 | Autumn | 16 | 11.58 | -5.2 | 5.55 | 38.5 | 217.7 | 13.06 | 1.21 | 14.27 | 5.2 | 58.82 | 41.34 | -44.55 | 0 | 0 | 0 | Battery-supported
2025-03-25 17:00 | 84 | 3 | Autumn | 17 | 11.58 | -6.1 | 10.17 | 14.3 | 124.3 | 7.46 | 41.53 | 48.99 | 6.1 | 49.55 | 41.11 | -0.56 | 0 | 0 | 0 | Battery-supported
2025-03-25 18:00 | 84 | 3 | Autumn | 18 | 11.58 | -10 | 9.18 | 31.3 | 0 | 0 | 25.65 | 25.65 | 10 | 51.49 | 30.78 | -25.84 | 0 | 0 | 0 | Battery-supported
2025-03-25 19:00 | 84 | 3 | Autumn | 19 | 11.58 | -3.2 | 14.74 | 73.6 | 0 | 0 | 120 | 120 | 3.2 | 47.93 | 57.3 | 72.07 | 0 | 0 | 0 | Normal
2025-03-25 20:00 | 84 | 3 | Autumn | 20 | 11.58 | -5.6 | 5.61 | 48.6 | 0 | 0 | 1.31 | 1.31 | 5.6 | 50.91 | 37.46 | -49.6 | 0 | 0 | 0 | Battery-supported
2025-03-25 21:00 | 84 | 3 | Autumn | 21 | 11.58 | -7.1 | 5.28 | 21.6 | 0 | 0 | 0.79 | 0.79 | 7.1 | 45 | 19.77 | -44.21 | 0 | 0 | 0 | Battery-supported
2025-03-25 22:00 | 84 | 3 | Autumn | 22 | 11.58 | -3.7 | 11.47 | 63.3 | 0 | 0 | 70.86 | 70.86 | 3.7 | 45 | 29.29 | 25.86 | 0 | 0 | 0 | Normal
2025-03-25 23:00 | 84 | 3 | Autumn | 23 | 11.58 | -7.1 | 12.87 | 77.8 | 0 | 0 | 115.14 | 115.14 | 7.1 | 45 | 55.1 | 70.14 | 0 | 0 | 0 | Normal
2025-03-26 | 85 | 3 | Autumn | 0 | 11.42 | -8 | 26.72 | 33.7 | 0 | 0 | 120 | 120 | 8 | 46.6 | 82.11 | 73.4 | 0 | 0 | 0 | Normal
2025-03-26 01:00 | 85 | 3 | Autumn | 1 | 11.42 | -9.8 | 2.37 | 88.1 | 0 | 0 | 0 | 0 | 9.8 | 45 | 64.11 | -45 | 0 | 0 | 0 | Battery-supported
2025-03-26 02:00 | 85 | 3 | Autumn | 2 | 11.42 | -7.4 | 17.19 | 29.8 | 0 | 0 | 120 | 120 | 7.4 | 45 | 91.71 | 75 | 0 | 0 | 0 | Normal
2025-03-26 03:00 | 85 | 3 | Autumn | 3 | 11.42 | -8 | 8.59 | 30.1 | 0 | 0 | 18.46 | 18.46 | 8 | 47.23 | 80.2 | -28.77 | 0 | 0 | 0 | Battery-supported
2025-03-26 04:00 | 85 | 3 | Autumn | 4 | 11.42 | -9.4 | 5.84 | 56.5 | 0 | 0 | 1.79 | 1.79 | 9.4 | 45 | 62.92 | -43.21 | 0 | 0 | 0 | Battery-supported
2025-03-26 05:00 | 85 | 3 | Autumn | 5 | 11.42 | -11.5 | 10.29 | 79.3 | 0 | 0 | 43.81 | 43.81 | 11.5 | 45 | 62.44 | -1.19 | 0 | 0 | 0 | Battery-supported
2025-03-26 06:00 | 85 | 3 | Autumn | 6 | 11.42 | -9.7 | 10.08 | 19.1 | 0 | 0 | 39.87 | 39.87 | 9.7 | 45 | 60.39 | -5.13 | 0 | 0 | 0 | Battery-supported
2025-03-26 07:00 | 85 | 3 | Autumn | 7 | 11.42 | -10.3 | 5.94 | 40.8 | 88.5 | 5.31 | 2.03 | 7.34 | 10.3 | 45 | 45.33 | -37.66 | 0 | 0 | 0 | Battery-supported
2025-03-26 08:00 | 85 | 3 | Autumn | 8 | 11.42 | -13.1 | 2.5 | 50.1 | 185.6 | 11.14 | 0 | 11.14 | 13.1 | 58.08 | 26.55 | -46.94 | 0 | 0 | 0 | Battery-supported
2025-03-26 09:00 | 85 | 3 | Autumn | 9 | 11.42 | -13.4 | 17.22 | 31.8 | 339 | 20.34 | 120 | 140.34 | 13.4 | 54.11 | 58.28 | 86.23 | 0 | 0 | 0 | Normal
2025-03-26 10:00 | 85 | 3 | Autumn | 10 | 11.42 | -8.8 | 5.01 | 90.1 | 181.3 | 10.88 | 0.48 | 11.36 | 8.8 | 49.31 | 43.1 | -37.95 | 0 | 0 | 0 | Battery-supported
2025-03-26 11:00 | 85 | 3 | Autumn | 11 | 11.42 | -15.5 | 4.52 | 47.9 | 404.5 | 24.27 | 0.15 | 24.42 | 15.5 | 56.96 | 30.09 | -32.54 | 0 | 0 | 0 | Battery-supported
2025-03-26 12:00 | 85 | 3 | Autumn | 12 | 11.42 | -9 | 5.32 | 18.3 | 566.1 | 33.97 | 0.84 | 34.81 | 9 | 53.49 | 22.62 | -18.68 | 0 | 0 | 0 | Battery-supported
2025-03-26 13:00 | 85 | 3 | Autumn | 13 | 11.42 | -10.1 | 12.56 | 58.3 | 355.4 | 21.32 | 104.09 | 125.41 | 10.1 | 56.7 | 47.9 | 68.71 | 0 | 0 | 0 | Normal
2025-03-26 14:00 | 85 | 3 | Autumn | 14 | 11.42 | -5.8 | 6.4 | 84.5 | 204.6 | 12.28 | 3.41 | 15.69 | 5.8 | 58.13 | 30.93 | -42.44 | 0 | 0 | 0 | Battery-supported
2025-03-26 15:00 | 85 | 3 | Autumn | 15 | 11.42 | -9.4 | 5.38 | 50.3 | 277.1 | 16.63 | 0.93 | 17.56 | 9.4 | 60.12 | 15 | -39.82 | 2.74 | 1.027 | 0 | Diesel-backup
2025-03-26 16:00 | 85 | 3 | Autumn | 16 | 11.42 | -6.5 | 9.89 | 58.7 | 166.5 | 9.99 | 36.52 | 46.51 | 6.5 | 48.97 | 15 | 0 | 2.46 | 0.921 | 0 | Diesel-backup
2025-03-26 17:00 | 85 | 3 | Autumn | 17 | 11.42 | -8.5 | 9.09 | 38.1 | 91.1 | 5.47 | 24.45 | 29.92 | 8.5 | 48.62 | 15 | 0 | 18.7 | 6.614 | 0 | Diesel-backup
2025-03-26 18:00 | 85 | 3 | Autumn | 18 | 11.42 | -7.2 | 5.46 | 87 | 0 | 0 | 1.05 | 1.05 | 7.2 | 47.71 | 15 | 0 | 46.66 | 14.931 | 0 | Diesel-backup
2025-03-26 19:00 | 85 | 3 | Autumn | 19 | 11.42 | -5.6 | 2.47 | 49.5 | 0 | 0 | 0 | 0 | 5.6 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-03-26 20:00 | 85 | 3 | Autumn | 20 | 11.42 | -8.2 | 12.4 | 25.2 | 0 | 0 | 98.67 | 98.67 | 8.2 | 51.7 | 32.28 | 46.97 | 0 | 0 | 0 | Normal
2025-03-26 21:00 | 85 | 3 | Autumn | 21 | 11.42 | -5.1 | 9.19 | 62.5 | 0 | 0 | 25.78 | 25.78 | 5.1 | 45 | 24.6 | -19.22 | 0 | 0 | 0 | Battery-supported
2025-03-26 22:00 | 85 | 3 | Autumn | 22 | 11.42 | -9.6 | 1.91 | 6.9 | 0 | 0 | 0 | 0 | 9.6 | 45 | 15 | -23.99 | 21.01 | 7.368 | 0 | Diesel-backup
2025-03-26 23:00 | 85 | 3 | Autumn | 23 | 11.42 | -7 | 18.62 | 82.8 | 0 | 0 | 120 | 120 | 7 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-03-27 | 86 | 3 | Autumn | 0 | 11.27 | -6.1 | 1.85 | 48.9 | 0 | 0 | 0 | 0 | 6.1 | 45 | 24.6 | -45 | 0 | 0 | 0 | Battery-supported
2025-03-27 01:00 | 86 | 3 | Autumn | 1 | 11.27 | -7.1 | 4.77 | 29.3 | 0 | 0 | 0.29 | 0.29 | 7.1 | 45 | 15 | -24 | 20.71 | 7.271 | 0 | Diesel-backup
2025-03-27 02:00 | 86 | 3 | Autumn | 2 | 11.27 | -4.7 | 4.97 | 75.8 | 0 | 0 | 0.44 | 0.44 | 4.7 | 45 | 15 | 0 | 44.56 | 14.284 | 0 | Diesel-backup
2025-03-27 03:00 | 86 | 3 | Autumn | 3 | 11.27 | -11 | 5.53 | 60.8 | 0 | 0 | 1.17 | 1.17 | 11 | 49.52 | 15 | 0 | 48.35 | 15.472 | 0 | Diesel-backup
2025-03-27 04:00 | 86 | 3 | Autumn | 4 | 11.27 | -12.7 | 5.42 | 25.7 | 0 | 0 | 0.99 | 0.99 | 12.7 | 52.46 | 15 | 0 | 51.47 | 16.47 | 0 | Diesel-backup
2025-03-27 05:00 | 86 | 3 | Autumn | 5 | 11.27 | -12.1 | 3.44 | 61.6 | 0 | 0 | 0 | 0 | 12.1 | 45.26 | 15 | 0 | 45.26 | 14.483 | 0 | Diesel-backup
2025-03-27 06:00 | 86 | 3 | Autumn | 6 | 11.27 | -8.7 | 8.71 | 32.4 | 0 | 0 | 19.79 | 19.79 | 8.7 | 45 | 15 | 0 | 25.21 | 8.706 | 0 | Diesel-backup
2025-03-27 07:00 | 86 | 3 | Autumn | 7 | 11.27 | -9.3 | 13.63 | 35 | 85 | 5.1 | 120 | 125.1 | 9.3 | 45 | 44.48 | 80.1 | 0 | 0 | 0 | Normal
2025-03-27 08:00 | 86 | 3 | Autumn | 8 | 11.27 | -10.2 | 8.64 | 34.7 | 213.4 | 12.8 | 19.01 | 31.81 | 10.2 | 54.26 | 35.5 | -22.45 | 0 | 0 | 0 | Battery-supported
2025-03-27 09:00 | 86 | 3 | Autumn | 9 | 11.27 | -12.8 | 9.52 | 70.6 | 206.8 | 12.41 | 30.54 | 42.95 | 12.8 | 59.45 | 28.9 | -16.5 | 0 | 0 | 0 | Battery-supported
2025-03-27 10:00 | 86 | 3 | Autumn | 10 | 11.27 | -8.5 | 6.51 | 93.9 | 164.7 | 9.88 | 3.82 | 13.7 | 8.5 | 52.17 | 15 | -34.74 | 3.73 | 1.39 | 0 | Diesel-backup
2025-03-27 11:00 | 86 | 3 | Autumn | 11 | 11.27 | -12.7 | 8.44 | 89.6 | 206.6 | 12.4 | 16.87 | 29.27 | 12.7 | 50.32 | 15 | 0 | 21.05 | 7.381 | 0 | Diesel-backup
2025-03-27 12:00 | 86 | 3 | Autumn | 12 | 11.27 | -7.1 | 9.94 | 83.9 | 243 | 14.58 | 37.38 | 51.96 | 7.1 | 54.36 | 15 | 0 | 2.4 | 0.899 | 0 | Diesel-backup
2025-03-27 13:00 | 86 | 3 | Autumn | 13 | 11.27 | -3 | 11.83 | 19.8 | 537.1 | 32.23 | 80.9 | 113.13 | 3 | 45.78 | 39.78 | 67.35 | 0 | 0 | 0 | Normal
2025-03-27 14:00 | 86 | 3 | Autumn | 14 | 11.27 | -8.1 | 5.14 | 14.3 | 496.9 | 29.81 | 0.62 | 30.43 | 8.1 | 50.3 | 31.84 | -19.87 | 0 | 0 | 0 | Battery-supported
2025-03-27 15:00 | 86 | 3 | Autumn | 15 | 11.27 | -7.2 | 4.73 | 31.4 | 336.1 | 20.17 | 0.26 | 20.43 | 7.2 | 51.92 | 19.24 | -31.49 | 0 | 0 | 0 | Battery-supported
2025-03-27 16:00 | 86 | 3 | Autumn | 16 | 11.27 | -9.2 | 1.42 | 57.3 | 164.6 | 9.88 | 0 | 9.88 | 9.2 | 56.37 | 15 | -10.6 | 35.89 | 11.903 | 0 | Diesel-backup
2025-03-27 17:00 | 86 | 3 | Autumn | 17 | 11.27 | -11.8 | 21.75 | 87.2 | 39.9 | 2.39 | 120 | 122.39 | 11.8 | 50.25 | 41.55 | 72.14 | 0 | 0 | 0 | Normal
2025-03-27 18:00 | 86 | 3 | Autumn | 18 | 11.27 | -8.9 | 20.98 | 23.3 | 0 | 0 | 120 | 120 | 8.9 | 46.53 | 68.58 | 73.47 | 0 | 0 | 0 | Normal
2025-03-27 19:00 | 86 | 3 | Autumn | 19 | 11.27 | -9.9 | 7.6 | 42.4 | 0 | 0 | 9.65 | 9.65 | 9.9 | 52.71 | 51.36 | -43.06 | 0 | 0 | 0 | Battery-supported
2025-03-27 20:00 | 86 | 3 | Autumn | 20 | 11.27 | -10.6 | 7.86 | 71 | 0 | 0 | 11.6 | 11.6 | 10.6 | 53.46 | 34.62 | -41.86 | 0 | 0 | 0 | Battery-supported
2025-03-27 21:00 | 86 | 3 | Autumn | 21 | 11.27 | -3.7 | 17.94 | 40.2 | 0 | 0 | 120 | 120 | 3.7 | 45 | 62.22 | 75 | 0 | 0 | 0 | Normal
2025-03-27 22:00 | 86 | 3 | Autumn | 22 | 11.27 | -7 | 3.52 | 31.2 | 0 | 0 | 0 | 0 | 7 | 47.07 | 43.39 | -47.07 | 0 | 0 | 0 | Battery-supported
2025-03-27 23:00 | 86 | 3 | Autumn | 23 | 11.27 | -7 | 4.42 | 27.9 | 0 | 0 | 0.11 | 0.11 | 7 | 45 | 25.43 | -44.89 | 0 | 0 | 0 | Battery-supported
2025-03-28 | 87 | 3 | Autumn | 0 | 11.11 | -9 | 18.63 | 52.6 | 0 | 0 | 120 | 120 | 9 | 45.31 | 52.92 | 74.69 | 0 | 0 | 0 | Normal
2025-03-28 01:00 | 87 | 3 | Autumn | 1 | 11.11 | -9.1 | 6.49 | 85.4 | 0 | 0 | 3.74 | 3.74 | 9.1 | 45.94 | 36.04 | -42.2 | 0 | 0 | 0 | Battery-supported
2025-03-28 02:00 | 87 | 3 | Autumn | 2 | 11.11 | -7 | 4.03 | 33.7 | 0 | 0 | 0.02 | 0.02 | 7 | 45 | 18.05 | -44.98 | 0 | 0 | 0 | Battery-supported
2025-03-28 03:00 | 87 | 3 | Autumn | 3 | 11.11 | -9.6 | 10.31 | 68.7 | 0 | 0 | 44.2 | 44.2 | 9.6 | 45 | 17.73 | -0.8 | 0 | 0 | 0 | Battery-supported
2025-03-28 04:00 | 87 | 3 | Autumn | 4 | 11.11 | -8.7 | 5.18 | 62.3 | 0 | 0 | 0.66 | 0.66 | 8.7 | 45.79 | 15 | -6.82 | 38.31 | 12.588 | 0 | Diesel-backup
2025-03-28 05:00 | 87 | 3 | Autumn | 5 | 11.11 | -10.6 | 16.85 | 20.8 | 0 | 0 | 120 | 120 | 10.6 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-03-28 06:00 | 87 | 3 | Autumn | 6 | 11.11 | -11.1 | 8.43 | 30.2 | 0 | 0 | 16.77 | 16.77 | 11.1 | 48.39 | 29.95 | -31.62 | 0 | 0 | 0 | Battery-supported
2025-03-28 07:00 | 87 | 3 | Autumn | 7 | 11.11 | -13.6 | 5.32 | 19.9 | 87.4 | 5.24 | 0.84 | 6.08 | 13.6 | 45 | 15 | -37.38 | 1.54 | 0.578 | 0 | Diesel-backup
2025-03-28 08:00 | 87 | 3 | Autumn | 8 | 11.11 | -14.9 | 5.5 | 4.7 | 269.5 | 16.17 | 1.12 | 17.29 | 14.9 | 58.13 | 15 | 0 | 40.84 | 13.286 | 0 | Diesel-backup
2025-03-28 09:00 | 87 | 3 | Autumn | 9 | 11.11 | -11.1 | 10.03 | 43.1 | 293.6 | 17.62 | 38.97 | 56.59 | 11.1 | 52.86 | 16.37 | 3.73 | 0 | 0 | 0 | Normal
2025-03-28 10:00 | 87 | 3 | Autumn | 10 | 11.11 | -10.3 | 6.99 | 54.1 | 329.1 | 19.75 | 5.95 | 25.7 | 10.3 | 61.82 | 15 | -3.43 | 32.69 | 10.975 | 0 | Diesel-backup
2025-03-28 11:00 | 87 | 3 | Autumn | 11 | 11.11 | -13 | 6.43 | 81.2 | 246.5 | 14.79 | 3.52 | 18.31 | 13 | 52.41 | 15 | 0 | 34.1 | 11.388 | 0 | Diesel-backup
2025-03-28 12:00 | 87 | 3 | Autumn | 12 | 11.11 | -9.9 | 12.14 | 18.3 | 565.9 | 33.95 | 90.27 | 124.22 | 9.9 | 49.01 | 42.68 | 75.21 | 0 | 0 | 0 | Normal
2025-03-28 13:00 | 87 | 3 | Autumn | 13 | 11.11 | -9.4 | 18.15 | 32.3 | 477.3 | 28.64 | 120 | 148.64 | 9.4 | 58.26 | 75.94 | 90.38 | 0 | 0 | 0 | Normal
2025-03-28 14:00 | 87 | 3 | Autumn | 14 | 11.11 | -13.8 | 11.19 | 54.8 | 326.3 | 19.58 | 63.65 | 83.23 | 13.8 | 60.19 | 84.42 | 23.04 | 0 | 0 | 0 | Normal
2025-03-28 15:00 | 87 | 3 | Autumn | 15 | 11.11 | -10.7 | 4.92 | 55.5 | 253.4 | 15.2 | 0.4 | 15.6 | 10.7 | 54.65 | 68.8 | -39.05 | 0 | 0 | 0 | Battery-supported
2025-03-28 16:00 | 87 | 3 | Autumn | 16 | 11.11 | -7.4 | 3.87 | 78.2 | 115.5 | 6.93 | 0.01 | 6.94 | 7.4 | 48.32 | 52.24 | -41.38 | 0 | 0 | 0 | Battery-supported
2025-03-28 17:00 | 87 | 3 | Autumn | 17 | 11.11 | -7.2 | 11.74 | 66.6 | 51.5 | 3.09 | 78.31 | 81.4 | 7.2 | 45.43 | 65.48 | 35.97 | 0 | 0 | 0 | Normal
2025-03-28 18:00 | 87 | 3 | Autumn | 18 | 11.11 | -10.3 | 11.17 | 65.2 | 0 | 0 | 63.15 | 63.15 | 10.3 | 51.4 | 69.8 | 11.75 | 0 | 0 | 0 | Normal
2025-03-28 19:00 | 87 | 3 | Autumn | 19 | 11.11 | -7.3 | 6.15 | 39.4 | 0 | 0 | 2.6 | 2.6 | 7.3 | 47.98 | 51.65 | -45.38 | 0 | 0 | 0 | Battery-supported
2025-03-28 20:00 | 87 | 3 | Autumn | 20 | 11.11 | -5.3 | 7.07 | 90.2 | 0 | 0 | 6.37 | 6.37 | 5.3 | 45.32 | 36.07 | -38.95 | 0 | 0 | 0 | Battery-supported
2025-03-28 21:00 | 87 | 3 | Autumn | 21 | 11.11 | -5.9 | 5.11 | 81.2 | 0 | 0 | 0.58 | 0.58 | 5.9 | 45 | 18.3 | -44.42 | 0 | 0 | 0 | Battery-supported
2025-03-28 22:00 | 87 | 3 | Autumn | 22 | 11.11 | -8 | 3.93 | 42.5 | 0 | 0 | 0.01 | 0.01 | 8 | 45 | 15 | -8.26 | 36.73 | 12.142 | 0 | Diesel-backup
2025-03-28 23:00 | 87 | 3 | Autumn | 23 | 11.11 | -9.1 | 5.38 | 50.8 | 0 | 0 | 0.93 | 0.93 | 9.1 | 47.78 | 15 | 0 | 46.85 | 14.992 | 0 | Diesel-backup
2025-03-29 | 88 | 3 | Autumn | 0 | 10.96 | -9.9 | 1.14 | 90.9 | 0 | 0 | 0 | 0 | 9.9 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-03-29 01:00 | 88 | 3 | Autumn | 1 | 10.96 | -7.9 | 15.16 | 65.3 | 0 | 0 | 120 | 120 | 7.9 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-03-29 02:00 | 88 | 3 | Autumn | 2 | 10.96 | -8.9 | 3.14 | 54.5 | 0 | 0 | 0 | 0 | 8.9 | 45 | 24.6 | -45 | 0 | 0 | 0 | Battery-supported
2025-03-29 03:00 | 88 | 3 | Autumn | 3 | 10.96 | -8.3 | 7.75 | 55.9 | 0 | 0 | 10.74 | 10.74 | 8.3 | 45 | 15 | -24 | 10.26 | 3.739 | 0 | Diesel-backup
2025-03-29 04:00 | 88 | 3 | Autumn | 4 | 10.96 | -9.8 | 1.63 | 100 | 0 | 0 | 0 | 0 | 9.8 | 47.3 | 15 | 0 | 47.3 | 15.136 | 0 | Diesel-backup
2025-03-29 05:00 | 88 | 3 | Autumn | 5 | 10.96 | -8.6 | 11 | 66.1 | 0 | 0 | 59.05 | 59.05 | 8.6 | 45.15 | 20.12 | 13.9 | 0 | 0 | 0 | Normal
2025-03-29 06:00 | 88 | 3 | Autumn | 6 | 10.96 | -10.4 | 12.93 | 63.1 | 0 | 0 | 117.37 | 117.37 | 10.4 | 45.64 | 46.51 | 71.73 | 0 | 0 | 0 | Normal
2025-03-29 07:00 | 88 | 3 | Autumn | 7 | 10.96 | -9 | 8.18 | 26.1 | 72.2 | 4.33 | 14.35 | 18.68 | 9 | 48.25 | 34.68 | -29.57 | 0 | 0 | 0 | Battery-supported
2025-03-29 08:00 | 88 | 3 | Autumn | 8 | 10.96 | -8.9 | 7.48 | 65.6 | 137 | 8.22 | 8.82 | 17.04 | 8.9 | 45 | 23.5 | -27.96 | 0 | 0 | 0 | Battery-supported
2025-03-29 09:00 | 88 | 3 | Autumn | 9 | 10.96 | -12.5 | 5.11 | 85.8 | 152.5 | 9.15 | 0.58 | 9.73 | 12.5 | 64.1 | 15 | -21.25 | 33.12 | 11.102 | 0 | Diesel-backup
2025-03-29 10:00 | 88 | 3 | Autumn | 10 | 10.96 | -14.6 | 14.95 | 79.7 | 221.8 | 13.31 | 120 | 133.31 | 14.6 | 62.14 | 41.19 | 71.17 | 0 | 0 | 0 | Normal
2025-03-29 11:00 | 88 | 3 | Autumn | 11 | 10.96 | -7 | 2.67 | 67.6 | 310.2 | 18.61 | 0 | 18.61 | 7 | 56.75 | 25.93 | -38.14 | 0 | 0 | 0 | Battery-supported
2025-03-29 12:00 | 88 | 3 | Autumn | 12 | 10.96 | -9.5 | 5.92 | 52.2 | 399 | 23.94 | 1.98 | 25.92 | 9.5 | 48.86 | 16.76 | -22.94 | 0 | 0 | 0 | Battery-supported
2025-03-29 13:00 | 88 | 3 | Autumn | 13 | 10.96 | -13.5 | 4.73 | 83.5 | 235 | 14.1 | 0.26 | 14.36 | 13.5 | 56.65 | 15 | -4.4 | 37.89 | 12.471 | 0 | Diesel-backup
2025-03-29 14:00 | 88 | 3 | Autumn | 14 | 10.96 | -10.9 | 4.63 | 46.3 | 359.6 | 21.58 | 0.2 | 21.78 | 10.9 | 55.02 | 15 | 0 | 33.24 | 11.137 | 0 | Diesel-backup
2025-03-29 15:00 | 88 | 3 | Autumn | 15 | 10.96 | -7.2 | 14.73 | 12.8 | 386.7 | 23.2 | 120 | 143.2 | 7.2 | 48.59 | 49.82 | 94.61 | 0 | 0 | 0 | Normal
2025-03-29 16:00 | 88 | 3 | Autumn | 16 | 10.96 | -9.2 | 7.2 | 80.3 | 107.3 | 6.44 | 7.09 | 13.53 | 9.2 | 52.8 | 34.11 | -39.27 | 0 | 0 | 0 | Battery-supported
2025-03-29 17:00 | 88 | 3 | Autumn | 17 | 10.96 | -9.4 | 5.09 | 42.2 | 61.4 | 3.68 | 0.56 | 4.24 | 9.4 | 53.34 | 15 | -47.77 | 1.33 | 0.499 | 0 | Diesel-backup
2025-03-29 18:00 | 88 | 3 | Autumn | 18 | 10.96 | -4.9 | 9.47 | 53.8 | 0 | 0 | 29.78 | 29.78 | 4.9 | 45 | 15 | 0 | 15.22 | 5.451 | 0 | Diesel-backup
2025-03-29 19:00 | 88 | 3 | Autumn | 19 | 10.96 | -10.1 | 9.01 | 7.5 | 0 | 0 | 23.41 | 23.41 | 10.1 | 55.96 | 15 | 0 | 32.55 | 10.935 | 0 | Diesel-backup
2025-03-29 20:00 | 88 | 3 | Autumn | 20 | 10.96 | -9.5 | 12.8 | 48.9 | 0 | 0 | 112.58 | 112.58 | 9.5 | 55.03 | 36.18 | 57.55 | 0 | 0 | 0 | Normal
2025-03-29 21:00 | 88 | 3 | Autumn | 21 | 10.96 | -7.4 | 10.07 | 47.8 | 0 | 0 | 39.69 | 39.69 | 7.4 | 45 | 34.05 | -5.31 | 0 | 0 | 0 | Battery-supported
2025-03-29 22:00 | 88 | 3 | Autumn | 22 | 10.96 | -7.1 | 7.41 | 51.4 | 0 | 0 | 8.37 | 8.37 | 7.1 | 45 | 19.4 | -36.63 | 0 | 0 | 0 | Battery-supported
2025-03-29 23:00 | 88 | 3 | Autumn | 23 | 10.96 | -7.1 | 7.72 | 29.8 | 0 | 0 | 10.52 | 10.52 | 7.1 | 45 | 15 | -11.01 | 23.47 | 8.158 | 0 | Diesel-backup
2025-03-30 | 89 | 3 | Autumn | 0 | 10.8 | -6.7 | 2.55 | 65.9 | 0 | 0 | 0 | 0 | 6.7 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-03-30 01:00 | 89 | 3 | Autumn | 1 | 10.8 | -8.7 | 9.85 | 16.4 | 0 | 0 | 35.84 | 35.84 | 8.7 | 45 | 15 | 0 | 9.16 | 3.351 | 0 | Diesel-backup
2025-03-30 02:00 | 89 | 3 | Autumn | 2 | 10.8 | -8.4 | 4.28 | 52.8 | 0 | 0 | 0.07 | 0.07 | 8.4 | 45 | 15 | 0 | 44.93 | 14.382 | 0 | Diesel-backup
2025-03-30 03:00 | 89 | 3 | Autumn | 3 | 10.8 | -10.4 | 8.94 | 34.1 | 0 | 0 | 22.53 | 22.53 | 10.4 | 51.39 | 15 | 0 | 28.86 | 9.831 | 0 | Diesel-backup
2025-03-30 04:00 | 89 | 3 | Autumn | 4 | 10.8 | -10.1 | 18.05 | 75.7 | 0 | 0 | 120 | 120 | 10.1 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-03-30 05:00 | 89 | 3 | Autumn | 5 | 10.8 | -10.3 | 8.21 | 40.9 | 0 | 0 | 14.62 | 14.62 | 10.3 | 45 | 30.45 | -30.38 | 0 | 0 | 0 | Battery-supported
2025-03-30 06:00 | 89 | 3 | Autumn | 6 | 10.8 | -10.3 | 6.3 | 46.8 | 0 | 0 | 3.07 | 3.07 | 10.3 | 45.4 | 15 | -38.62 | 3.71 | 1.383 | 0 | Diesel-backup
2025-03-30 07:00 | 89 | 3 | Autumn | 7 | 10.8 | -9.2 | 6.25 | 61.1 | 41.4 | 2.48 | 2.91 | 5.39 | 9.2 | 45 | 15 | 0 | 39.61 | 12.948 | 0 | Diesel-backup
2025-03-30 08:00 | 89 | 3 | Autumn | 8 | 10.8 | -9.8 | 9.62 | 61.4 | 140.4 | 8.42 | 32.08 | 40.5 | 9.8 | 49.34 | 15 | 0 | 8.84 | 3.238 | 0 | Diesel-backup
2025-03-30 09:00 | 89 | 3 | Autumn | 9 | 10.8 | -10.8 | 8.65 | 70.3 | 199.4 | 11.96 | 19.12 | 31.08 | 10.8 | 47.18 | 15 | 0 | 16.1 | 5.748 | 0 | Diesel-backup
2025-03-30 10:00 | 89 | 3 | Autumn | 10 | 10.8 | -12.6 | 11.34 | 60.4 | 299.9 | 17.99 | 67.45 | 85.44 | 12.6 | 56.45 | 25.67 | 28.99 | 0 | 0 | 0 | Normal
2025-03-30 11:00 | 89 | 3 | Autumn | 11 | 10.8 | -10.4 | 5.32 | 77.1 | 265.1 | 15.91 | 0.84 | 16.75 | 10.4 | 57.11 | 15 | -26.67 | 13.69 | 4.929 | 0 | Diesel-backup
2025-03-30 12:00 | 89 | 3 | Autumn | 12 | 10.8 | -10.3 | 6.98 | 46.1 | 429.2 | 25.75 | 5.9 | 31.65 | 10.3 | 51.58 | 15 | 0 | 19.93 | 7.017 | 0 | Diesel-backup
2025-03-30 13:00 | 89 | 3 | Autumn | 13 | 10.8 | -9.5 | 12.43 | 26.8 | 502.1 | 30.13 | 99.67 | 129.8 | 9.5 | 57.52 | 41.6 | 72.28 | 0 | 0 | 0 | Normal
2025-03-30 14:00 | 89 | 3 | Autumn | 14 | 10.8 | -4.6 | 12.99 | 86.6 | 192.2 | 11.53 | 119.62 | 131.15 | 4.6 | 45 | 73.3 | 86.15 | 0 | 0 | 0 | Normal
2025-03-30 15:00 | 89 | 3 | Autumn | 15 | 10.8 | -10.3 | 13.04 | 65.3 | 215.2 | 12.91 | 120 | 132.91 | 10.3 | 51.43 | 95 | 58.96 | 0 | 0 | 0 | Normal
2025-03-30 16:00 | 89 | 3 | Autumn | 16 | 10.8 | -7.8 | 11.69 | 73.9 | 115.9 | 6.95 | 76.89 | 83.84 | 7.8 | 54.38 | 95 | 0 | 0 | 0 | 0 | Normal
2025-03-30 17:00 | 89 | 3 | Autumn | 17 | 10.8 | -6.1 | 11.91 | 59.2 | 42.5 | 2.55 | 83.25 | 85.8 | 6.1 | 51.96 | 95 | 0 | 0 | 0 | 0 | Normal
2025-03-30 18:00 | 89 | 3 | Autumn | 18 | 10.8 | -8 | 8.93 | 32.8 | 0 | 0 | 22.41 | 22.41 | 8 | 52.83 | 82.83 | -30.42 | 0 | 0 | 0 | Battery-supported
2025-03-30 19:00 | 89 | 3 | Autumn | 19 | 10.8 | -2.9 | 3.07 | 15.8 | 0 | 0 | 0 | 0 | 2.9 | 50.34 | 62.7 | -50.34 | 0 | 0 | 0 | Battery-supported
2025-03-30 20:00 | 89 | 3 | Autumn | 20 | 10.8 | -8.8 | 3.28 | 78 | 0 | 0 | 0 | 0 | 8.8 | 51.59 | 42.06 | -51.59 | 0 | 0 | 0 | Battery-supported
2025-03-30 21:00 | 89 | 3 | Autumn | 21 | 10.8 | -7.3 | 8.12 | 90.5 | 0 | 0 | 13.8 | 13.8 | 7.3 | 45 | 29.58 | -31.2 | 0 | 0 | 0 | Battery-supported
2025-03-30 22:00 | 89 | 3 | Autumn | 22 | 10.8 | -9.9 | 8.33 | 26.2 | 0 | 0 | 15.77 | 15.77 | 9.9 | 45 | 17.89 | -29.23 | 0 | 0 | 0 | Battery-supported
2025-03-30 23:00 | 89 | 3 | Autumn | 23 | 10.8 | -9.2 | 4.57 | 73.8 | 0 | 0 | 0.17 | 0.17 | 9.2 | 51.9 | 15 | -7.22 | 44.51 | 14.271 | 0 | Diesel-backup
2025-03-31 | 90 | 3 | Autumn | 0 | 10.65 | -8.4 | 4.78 | 63.4 | 0 | 0 | 0.29 | 0.29 | 8.4 | 45 | 15 | 0 | 44.71 | 14.324 | 0 | Diesel-backup
2025-03-31 01:00 | 90 | 3 | Autumn | 1 | 10.65 | -7.4 | 7.43 | 19.6 | 0 | 0 | 8.5 | 8.5 | 7.4 | 45 | 15 | 0 | 36.5 | 12.077 | 0 | Diesel-backup
2025-03-31 02:00 | 90 | 3 | Autumn | 2 | 10.65 | -9 | 23.9 | 47.4 | 0 | 0 | 120 | 120 | 9 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-03-31 03:00 | 90 | 3 | Autumn | 3 | 10.65 | -7.3 | 4.06 | 43.1 | 0 | 0 | 0.02 | 0.02 | 7.3 | 45 | 24.61 | -44.98 | 0 | 0 | 0 | Battery-supported
2025-03-31 04:00 | 90 | 3 | Autumn | 4 | 10.65 | -10.6 | 6.12 | 42.1 | 0 | 0 | 2.52 | 2.52 | 10.6 | 48.23 | 15 | -24.02 | 21.69 | 7.588 | 0 | Diesel-backup
2025-03-31 05:00 | 90 | 3 | Autumn | 5 | 10.65 | -11.5 | 12.88 | 51 | 0 | 0 | 115.51 | 115.51 | 11.5 | 45 | 40.95 | 70.51 | 0 | 0 | 0 | Normal
2025-03-31 06:00 | 90 | 3 | Autumn | 6 | 10.65 | -5 | 11.58 | 35.5 | 0 | 0 | 73.83 | 73.83 | 5 | 47.07 | 50.8 | 26.76 | 0 | 0 | 0 | Normal
2025-03-31 07:00 | 90 | 3 | Autumn | 7 | 10.65 | -10.3 | 9.37 | 33.8 | 46.8 | 2.81 | 28.31 | 31.12 | 10.3 | 51.74 | 42.55 | -20.62 | 0 | 0 | 0 | Battery-supported
2025-03-31 08:00 | 90 | 3 | Autumn | 8 | 10.65 | -12.8 | 2.16 | 52.6 | 151.2 | 9.07 | 0 | 9.07 | 12.8 | 60.81 | 21.85 | -51.74 | 0 | 0 | 0 | Battery-supported
2025-03-31 09:00 | 90 | 3 | Autumn | 9 | 10.65 | -12.7 | 6.77 | 34.7 | 307.2 | 18.43 | 4.89 | 23.32 | 12.7 | 56.29 | 15 | -17.13 | 15.84 | 5.661 | 0 | Diesel-backup
2025-03-31 10:00 | 90 | 3 | Autumn | 10 | 10.65 | -13.1 | 20.32 | 86.6 | 191.1 | 11.47 | 120 | 131.47 | 13.1 | 61.09 | 40.9 | 70.38 | 0 | 0 | 0 | Normal
2025-03-31 11:00 | 90 | 3 | Autumn | 11 | 10.65 | -8.7 | 4.68 | 58.2 | 353.8 | 21.23 | 0.23 | 21.46 | 8.7 | 52.75 | 28.38 | -31.29 | 0 | 0 | 0 | Battery-supported
2025-03-31 12:00 | 90 | 3 | Autumn | 12 | 10.65 | -11.2 | 4.56 | 75.9 | 282.6 | 16.96 | 0.17 | 17.13 | 11.2 | 55.2 | 15 | -33.46 | 4.61 | 1.714 | 0 | Diesel-backup
2025-03-31 13:00 | 90 | 3 | Autumn | 13 | 10.65 | -9.8 | 17.66 | 25.9 | 505.7 | 30.34 | 120 | 150.34 | 9.8 | 55.59 | 49.87 | 94.75 | 0 | 0 | 0 | Normal
2025-03-31 14:00 | 90 | 3 | Autumn | 14 | 10.65 | -9.8 | 7.42 | 27.7 | 431.7 | 25.9 | 8.43 | 34.33 | 9.8 | 54.97 | 41.61 | -20.64 | 0 | 0 | 0 | Battery-supported
2025-03-31 15:00 | 90 | 3 | Autumn | 15 | 10.65 | -7.7 | 2.29 | 38.9 | 294.2 | 17.65 | 0 | 17.65 | 7.7 | 54.8 | 26.75 | -37.15 | 0 | 0 | 0 | Battery-supported
2025-03-31 16:00 | 90 | 3 | Autumn | 16 | 10.65 | -10.8 | 3.72 | 90.3 | 80.7 | 4.84 | 0 | 4.84 | 10.8 | 45.19 | 15 | -29.38 | 10.97 | 3.988 | 0 | Diesel-backup
2025-03-31 17:00 | 90 | 3 | Autumn | 17 | 10.65 | -11 | 5.43 | 54.9 | 36.9 | 2.21 | 1.01 | 3.22 | 11 | 53.64 | 15 | 0 | 50.42 | 16.134 | 0 | Diesel-backup
2025-03-31 18:00 | 90 | 3 | Autumn | 18 | 10.65 | -7.9 | 9.1 | 82.4 | 0 | 0 | 24.58 | 24.58 | 7.9 | 46.02 | 15 | 0 | 21.44 | 7.507 | 0 | Diesel-backup
2025-03-31 19:00 | 90 | 3 | Autumn | 19 | 10.65 | -6.9 | 6.93 | 3.2 | 0 | 0 | 5.65 | 5.65 | 6.9 | 53.62 | 15 | 0 | 47.97 | 15.35 | 0 | Diesel-backup
2025-03-31 20:00 | 90 | 3 | Autumn | 20 | 10.65 | -7.5 | 4.43 | 48.5 | 0 | 0 | 0.11 | 0.11 | 7.5 | 46.85 | 15 | 0 | 46.74 | 14.957 | 0 | Diesel-backup
2025-03-31 21:00 | 90 | 3 | Autumn | 21 | 10.65 | -10 | 6.99 | 100 | 0 | 0 | 5.95 | 5.95 | 10 | 45 | 15 | 0 | 39.05 | 12.793 | 0 | Diesel-backup
2025-03-31 22:00 | 90 | 3 | Autumn | 22 | 10.65 | -6.9 | 4.68 | 30.5 | 0 | 0 | 0.23 | 0.23 | 6.9 | 45.65 | 15 | 0 | 45.42 | 14.534 | 0 | Diesel-backup
2025-03-31 23:00 | 90 | 3 | Autumn | 23 | 10.65 | -10.3 | 20.99 | 42 | 0 | 0 | 120 | 120 | 10.3 | 50.53 | 40.56 | 69.47 | 0 | 0 | 0 | Normal
2025-04-01 | 91 | 4 | Autumn | 0 | 10.49 | -10.3 | 3.59 | 35.7 | 0 | 0 | 0 | 0 | 10.3 | 48.83 | 21.03 | -48.83 | 0 | 0 | 0 | Battery-supported
2025-04-01 01:00 | 91 | 4 | Autumn | 1 | 10.49 | -11.6 | 5.89 | 56.9 | 0 | 0 | 1.91 | 1.91 | 11.6 | 49.61 | 15 | -15.08 | 32.62 | 10.955 | 0 | Diesel-backup
2025-04-01 02:00 | 91 | 4 | Autumn | 2 | 10.49 | -7 | 5.37 | 6.9 | 0 | 0 | 0.92 | 0.92 | 7 | 45 | 15 | 0 | 44.08 | 14.158 | 0 | Diesel-backup
2025-04-01 03:00 | 91 | 4 | Autumn | 3 | 10.49 | -8.9 | 5.43 | 90.2 | 0 | 0 | 1.01 | 1.01 | 8.9 | 45 | 15 | 0 | 43.99 | 14.134 | 0 | Diesel-backup
2025-04-01 04:00 | 91 | 4 | Autumn | 4 | 10.49 | -9.3 | 3.87 | 37.7 | 0 | 0 | 0.01 | 0.01 | 9.3 | 45 | 15 | 0 | 44.99 | 14.397 | 0 | Diesel-backup
2025-04-01 05:00 | 91 | 4 | Autumn | 5 | 10.49 | -8.2 | 16.97 | 19.7 | 0 | 0 | 120 | 120 | 8.2 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-04-01 06:00 | 91 | 4 | Autumn | 6 | 10.49 | -5 | 25.03 | 31.3 | 0 | 0 | 120 | 120 | 5 | 45 | 70.2 | 75 | 0 | 0 | 0 | Normal
2025-04-01 07:00 | 91 | 4 | Autumn | 7 | 10.49 | -15.1 | 9.8 | 23.8 | 39.7 | 2.38 | 35 | 37.38 | 15.1 | 54.12 | 63.5 | -16.74 | 0 | 0 | 0 | Battery-supported
2025-04-01 08:00 | 91 | 4 | Autumn | 8 | 10.49 | -13 | 9.31 | 26.6 | 191.4 | 11.48 | 27.45 | 38.93 | 13 | 60.01 | 55.07 | -21.08 | 0 | 0 | 0 | Battery-supported
2025-04-01 09:00 | 91 | 4 | Autumn | 9 | 10.49 | -12.7 | 2.63 | 50.3 | 254.4 | 15.26 | 0 | 15.26 | 12.7 | 48.29 | 41.86 | -33.03 | 0 | 0 | 0 | Battery-supported
2025-04-01 10:00 | 91 | 4 | Autumn | 10 | 10.49 | -13.1 | 16.74 | 64.7 | 279.1 | 16.75 | 120 | 136.75 | 13.1 | 55.95 | 71.59 | 80.8 | 0 | 0 | 0 | Normal
2025-04-01 11:00 | 91 | 4 | Autumn | 11 | 10.49 | -13.3 | 4.69 | 70.4 | 295.8 | 17.75 | 0.24 | 17.99 | 13.3 | 55.2 | 56.71 | -37.21 | 0 | 0 | 0 | Battery-supported
2025-04-01 12:00 | 91 | 4 | Autumn | 12 | 10.49 | -11.3 | 2.42 | 40.1 | 458.4 | 27.5 | 0 | 27.5 | 11.3 | 45.03 | 49.7 | -17.53 | 0 | 0 | 0 | Battery-supported
2025-04-01 13:00 | 91 | 4 | Autumn | 13 | 10.49 | -13 | 10.84 | 57.5 | 356.5 | 21.39 | 55.35 | 76.74 | 13 | 59.32 | 56.11 | 17.42 | 0 | 0 | 0 | Normal
2025-04-01 14:00 | 91 | 4 | Autumn | 14 | 10.49 | -9.1 | 14.26 | 39.4 | 381.8 | 22.91 | 120 | 142.91 | 9.1 | 55.31 | 88.35 | 87.6 | 0 | 0 | 0 | Normal
2025-04-01 15:00 | 91 | 4 | Autumn | 15 | 10.49 | -9.4 | 16.64 | 34.6 | 302.5 | 18.15 | 120 | 138.15 | 9.4 | 49.97 | 95 | 18.08 | 0 | 0 | 0 | Normal
2025-04-01 16:00 | 91 | 4 | Autumn | 16 | 10.49 | -8.1 | 5.94 | 13.1 | 215.7 | 12.94 | 2.03 | 14.97 | 8.1 | 49.86 | 81.04 | -34.89 | 0 | 0 | 0 | Battery-supported
2025-04-01 17:00 | 91 | 4 | Autumn | 17 | 10.49 | -7.7 | 5.51 | 28.5 | 38 | 2.28 | 1.14 | 3.42 | 7.7 | 51.28 | 61.9 | -47.86 | 0 | 0 | 0 | Battery-supported
2025-04-01 18:00 | 91 | 4 | Autumn | 18 | 10.49 | -7.3 | 8.87 | 65.5 | 0 | 0 | 21.67 | 21.67 | 7.3 | 51.96 | 49.78 | -30.29 | 0 | 0 | 0 | Battery-supported
2025-04-01 19:00 | 91 | 4 | Autumn | 19 | 10.49 | -9.3 | 6.96 | 60.5 | 0 | 0 | 5.8 | 5.8 | 9.3 | 49.71 | 32.22 | -43.91 | 0 | 0 | 0 | Battery-supported
2025-04-01 20:00 | 91 | 4 | Autumn | 20 | 10.49 | -3.7 | 10.97 | 86.9 | 0 | 0 | 58.34 | 58.34 | 3.7 | 45 | 37.13 | 13.34 | 0 | 0 | 0 | Normal
2025-04-01 21:00 | 91 | 4 | Autumn | 21 | 10.49 | -7.9 | 8.93 | 81 | 0 | 0 | 22.41 | 22.41 | 7.9 | 45 | 28.09 | -22.59 | 0 | 0 | 0 | Battery-supported
2025-04-01 22:00 | 91 | 4 | Autumn | 22 | 10.49 | -12.7 | 4.44 | 66.3 | 0 | 0 | 0.12 | 0.12 | 12.7 | 53.66 | 15 | -32.73 | 20.81 | 7.303 | 0 | Diesel-backup
2025-04-01 23:00 | 91 | 4 | Autumn | 23 | 10.49 | -11 | 16.95 | 68.2 | 0 | 0 | 120 | 120 | 11 | 50.88 | 40.44 | 69.12 | 0 | 0 | 0 | Normal
2025-04-02 | 92 | 4 | Autumn | 0 | 10.34 | -13.2 | 11.05 | 60.1 | 0 | 0 | 60.24 | 60.24 | 13.2 | 45 | 46.04 | 15.24 | 0 | 0 | 0 | Normal
2025-04-02 01:00 | 92 | 4 | Autumn | 1 | 10.34 | -9.7 | 14.13 | 92.1 | 0 | 0 | 120 | 120 | 9.7 | 45 | 73.64 | 75 | 0 | 0 | 0 | Normal
2025-04-02 02:00 | 92 | 4 | Autumn | 2 | 10.34 | -10.4 | 4.51 | 74.2 | 0 | 0 | 0.14 | 0.14 | 10.4 | 45 | 55.7 | -44.86 | 0 | 0 | 0 | Battery-supported
2025-04-02 03:00 | 92 | 4 | Autumn | 3 | 10.34 | -11.5 | 10.87 | 32 | 0 | 0 | 56.03 | 56.03 | 11.5 | 45 | 59.76 | 11.03 | 0 | 0 | 0 | Normal
2025-04-02 04:00 | 92 | 4 | Autumn | 4 | 10.34 | -6.4 | 12.62 | 42.1 | 0 | 0 | 106.17 | 106.17 | 6.4 | 49.2 | 80.72 | 56.97 | 0 | 0 | 0 | Normal
2025-04-02 05:00 | 92 | 4 | Autumn | 5 | 10.34 | -9.9 | 8.75 | 77.9 | 0 | 0 | 20.25 | 20.25 | 9.9 | 45 | 70.82 | -24.75 | 0 | 0 | 0 | Battery-supported
2025-04-02 06:00 | 92 | 4 | Autumn | 6 | 10.34 | -9.8 | 3.86 | 31.3 | 0 | 0 | 0.01 | 0.01 | 9.8 | 47.84 | 51.69 | -47.83 | 0 | 0 | 0 | Battery-supported
2025-04-02 07:00 | 92 | 4 | Autumn | 7 | 10.34 | -13.6 | 8.27 | 53.6 | 20.1 | 1.21 | 15.19 | 16.4 | 13.6 | 47.25 | 39.35 | -30.85 | 0 | 0 | 0 | Battery-supported
2025-04-02 08:00 | 92 | 4 | Autumn | 8 | 10.34 | -13.8 | 11.94 | 52 | 139.1 | 8.35 | 84.15 | 92.5 | 13.8 | 55.92 | 52.81 | 36.58 | 0 | 0 | 0 | Normal
2025-04-02 09:00 | 92 | 4 | Autumn | 9 | 10.34 | -11.5 | 14.68 | 91.3 | 126.7 | 7.6 | 120 | 127.6 | 11.5 | 53.34 | 80.14 | 74.26 | 0 | 0 | 0 | Normal
2025-04-02 10:00 | 92 | 4 | Autumn | 10 | 10.34 | -11 | 2.81 | 92.6 | 164.4 | 9.86 | 0 | 9.86 | 11 | 55.47 | 61.9 | -45.61 | 0 | 0 | 0 | Battery-supported
2025-04-02 11:00 | 92 | 4 | Autumn | 11 | 10.34 | -15.2 | 8.65 | 42.8 | 425.2 | 25.51 | 19.12 | 44.63 | 15.2 | 57.46 | 56.77 | -12.83 | 0 | 0 | 0 | Battery-supported
2025-04-02 12:00 | 92 | 4 | Autumn | 12 | 10.34 | -11.2 | 3.27 | 4.4 | 634.4 | 38.06 | 0 | 38.06 | 11.2 | 57.18 | 49.12 | -19.12 | 0 | 0 | 0 | Battery-supported
2025-04-02 13:00 | 92 | 4 | Autumn | 13 | 10.34 | -10.4 | 12.03 | 69.5 | 299.7 | 17.98 | 86.87 | 104.85 | 10.4 | 58.02 | 66.35 | 46.83 | 0 | 0 | 0 | Normal
2025-04-02 14:00 | 92 | 4 | Autumn | 14 | 10.34 | -10.6 | 13.85 | 6.5 | 512 | 30.72 | 120 | 150.72 | 10.6 | 51.12 | 95 | 77.85 | 0 | 0 | 0 | Normal
2025-04-02 15:00 | 92 | 4 | Autumn | 15 | 10.34 | -11.5 | 4.24 | 4.1 | 389.4 | 23.36 | 0.06 | 23.42 | 11.5 | 55.32 | 82.24 | -31.9 | 0 | 0 | 0 | Battery-supported
2025-04-02 16:00 | 92 | 4 | Autumn | 16 | 10.34 | -10.5 | 3.73 | 47.1 | 147.5 | 8.85 | 0 | 8.85 | 10.5 | 46.97 | 66.99 | -38.12 | 0 | 0 | 0 | Battery-supported
2025-04-02 17:00 | 92 | 4 | Autumn | 17 | 10.34 | -9.4 | 5.36 | 15.3 | 29.7 | 1.78 | 0.9 | 2.68 | 9.4 | 50.31 | 47.94 | -47.63 | 0 | 0 | 0 | Battery-supported
2025-04-02 18:00 | 92 | 4 | Autumn | 18 | 10.34 | -8.6 | 7.14 | 31.4 | 0 | 0 | 6.75 | 6.75 | 8.6 | 51.67 | 29.97 | -44.92 | 0 | 0 | 0 | Battery-supported
2025-04-02 19:00 | 92 | 4 | Autumn | 19 | 10.34 | -7.3 | 4.92 | 68.1 | 0 | 0 | 0.4 | 0.4 | 7.3 | 49.5 | 15 | -37.43 | 11.67 | 4.232 | 0 | Diesel-backup
2025-04-02 20:00 | 92 | 4 | Autumn | 20 | 10.34 | -6.2 | 12.65 | 33.5 | 0 | 0 | 107.22 | 107.22 | 6.2 | 48.76 | 36.51 | 58.46 | 0 | 0 | 0 | Normal
2025-04-02 21:00 | 92 | 4 | Autumn | 21 | 10.34 | -9.3 | 14.72 | 57.8 | 0 | 0 | 120 | 120 | 9.3 | 46.37 | 63.61 | 73.63 | 0 | 0 | 0 | Normal
2025-04-02 22:00 | 92 | 4 | Autumn | 22 | 10.34 | -9.8 | 8.44 | 39.9 | 0 | 0 | 16.87 | 16.87 | 9.8 | 47.7 | 51.28 | -30.83 | 0 | 0 | 0 | Battery-supported
2025-04-02 23:00 | 92 | 4 | Autumn | 23 | 10.34 | -8.1 | 5.03 | 82.1 | 0 | 0 | 0.5 | 0.5 | 8.1 | 45 | 33.48 | -44.5 | 0 | 0 | 0 | Battery-supported
2025-04-03 | 93 | 4 | Autumn | 0 | 10.18 | -8.2 | 7.01 | 77.1 | 0 | 0 | 6.05 | 6.05 | 8.2 | 45 | 17.9 | -38.95 | 0 | 0 | 0 | Battery-supported
2025-04-03 01:00 | 93 | 4 | Autumn | 1 | 10.18 | -10.9 | 8.47 | 11.2 | 0 | 0 | 17.18 | 17.18 | 10.9 | 45 | 15 | -7.24 | 20.58 | 7.228 | 0 | Diesel-backup
2025-04-03 02:00 | 93 | 4 | Autumn | 2 | 10.18 | -8.5 | 6.83 | 47.2 | 0 | 0 | 5.17 | 5.17 | 8.5 | 45 | 15 | 0 | 39.83 | 13.009 | 0 | Diesel-backup
2025-04-03 03:00 | 93 | 4 | Autumn | 3 | 10.18 | -8.5 | 7.55 | 67.8 | 0 | 0 | 9.3 | 9.3 | 8.5 | 49.08 | 15 | 0 | 39.78 | 12.995 | 0 | Diesel-backup
2025-04-03 04:00 | 93 | 4 | Autumn | 4 | 10.18 | -8.2 | 14.11 | 17.8 | 0 | 0 | 120 | 120 | 8.2 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-04-03 05:00 | 93 | 4 | Autumn | 5 | 10.18 | -7.4 | 4.84 | 21.1 | 0 | 0 | 0.34 | 0.34 | 7.4 | 45 | 24.74 | -44.66 | 0 | 0 | 0 | Battery-supported
2025-04-03 06:00 | 93 | 4 | Autumn | 6 | 10.18 | -13.5 | 22.21 | 24.1 | 0 | 0 | 120 | 120 | 13.5 | 54.26 | 48.93 | 65.74 | 0 | 0 | 0 | Normal
2025-04-03 07:00 | 93 | 4 | Autumn | 7 | 10.18 | -11.7 | 8.62 | 90.1 | 5.9 | 0.35 | 18.79 | 19.14 | 11.7 | 46.99 | 37.79 | -27.85 | 0 | 0 | 0 | Battery-supported
2025-04-03 08:00 | 93 | 4 | Autumn | 8 | 10.18 | -11.8 | 6.6 | 24.2 | 177.2 | 10.63 | 4.17 | 14.8 | 11.8 | 51 | 23.31 | -36.2 | 0 | 0 | 0 | Battery-supported
2025-04-03 09:00 | 93 | 4 | Autumn | 9 | 10.18 | -12 | 4.76 | 19.3 | 337.4 | 20.24 | 0.28 | 20.52 | 12 | 54.13 | 15 | -20.77 | 12.84 | 4.637 | 0 | Diesel-backup
2025-04-03 10:00 | 93 | 4 | Autumn | 10 | 10.18 | -13 | 5.03 | 9.8 | 495.5 | 29.73 | 0.5 | 30.23 | 13 | 63.08 | 15 | 0 | 32.85 | 11.023 | 0 | Diesel-backup
2025-04-03 11:00 | 93 | 4 | Autumn | 11 | 10.18 | -14.6 | 8 | 26.7 | 499.9 | 29.99 | 12.75 | 42.74 | 14.6 | 62.29 | 15 | 0 | 19.55 | 6.893 | 0 | Diesel-backup
2025-04-03 12:00 | 93 | 4 | Autumn | 12 | 10.18 | -10.8 | 8.58 | 41.3 | 452.8 | 27.17 | 18.35 | 45.52 | 10.8 | 51.73 | 15 | 0 | 6.21 | 2.296 | 0 | Diesel-backup
2025-04-03 13:00 | 93 | 4 | Autumn | 13 | 10.18 | -12.4 | 6.46 | 10.7 | 574.9 | 34.49 | 3.63 | 38.12 | 12.4 | 61.54 | 15 | 0 | 23.42 | 8.141 | 0 | Diesel-backup
2025-04-03 14:00 | 93 | 4 | Autumn | 14 | 10.18 | -10.1 | 3.27 | 93 | 161.8 | 9.71 | 0 | 9.71 | 10.1 | 55.65 | 15 | 0 | 45.94 | 14.701 | 0 | Diesel-backup
2025-04-03 15:00 | 93 | 4 | Autumn | 15 | 10.18 | -11.6 | 8 | 21.2 | 331.7 | 19.9 | 12.75 | 32.65 | 11.6 | 45 | 15 | 0 | 12.35 | 4.468 | 0 | Diesel-backup
2025-04-03 16:00 | 93 | 4 | Autumn | 16 | 10.18 | -12 | 5.09 | 46.6 | 141 | 8.46 | 0.56 | 9.02 | 12 | 54.58 | 15 | 0 | 45.56 | 14.579 | 0 | Diesel-backup
2025-04-03 17:00 | 93 | 4 | Autumn | 17 | 10.18 | -8.7 | 2.31 | 16.3 | 16.1 | 0.97 | 0 | 0.97 | 8.7 | 59 | 15 | 0 | 58.03 | 18.57 | 0 | Diesel-backup
2025-04-03 18:00 | 93 | 4 | Autumn | 18 | 10.18 | -8.7 | 11.3 | 25.3 | 0 | 0 | 66.42 | 66.42 | 8.7 | 51.07 | 20.65 | 15.35 | 0 | 0 | 0 | Normal
2025-04-03 19:00 | 93 | 4 | Autumn | 19 | 10.18 | -7.6 | 2.57 | 31.4 | 0 | 0 | 0 | 0 | 7.6 | 56.68 | 15 | -14.12 | 42.56 | 13.752 | 0 | Diesel-backup
2025-04-03 20:00 | 93 | 4 | Autumn | 20 | 10.18 | -4 | 6.29 | 99.6 | 0 | 0 | 3.04 | 3.04 | 4 | 45 | 15 | 0 | 41.96 | 13.59 | 0 | Diesel-backup
2025-04-03 21:00 | 93 | 4 | Autumn | 21 | 10.18 | -8.2 | 7.42 | 37.1 | 0 | 0 | 8.43 | 8.43 | 8.2 | 45 | 15 | 0 | 36.57 | 12.097 | 0 | Diesel-backup
2025-04-03 22:00 | 93 | 4 | Autumn | 22 | 10.18 | -7.9 | 15.9 | 31 | 0 | 0 | 120 | 120 | 7.9 | 47.43 | 41.71 | 72.57 | 0 | 0 | 0 | Normal
2025-04-03 23:00 | 93 | 4 | Autumn | 23 | 10.18 | -11.6 | 2.4 | 56.4 | 0 | 0 | 0 | 0 | 11.6 | 50.01 | 21.7 | -50.01 | 0 | 0 | 0 | Battery-supported
2025-04-04 | 94 | 4 | Autumn | 0 | 10.02 | -12.6 | 12.04 | 75.3 | 0 | 0 | 87.17 | 87.17 | 12.6 | 47.5 | 36.3 | 39.67 | 0 | 0 | 0 | Normal
2025-04-04 01:00 | 94 | 4 | Autumn | 1 | 10.02 | -6.6 | 13.12 | 70.4 | 0 | 0 | 120 | 120 | 6.6 | 45.08 | 63.87 | 74.92 | 0 | 0 | 0 | Normal
2025-04-04 02:00 | 94 | 4 | Autumn | 2 | 10.02 | -12.5 | 18.67 | 26.4 | 0 | 0 | 120 | 120 | 12.5 | 45.13 | 91.42 | 74.87 | 0 | 0 | 0 | Normal
2025-04-04 03:00 | 94 | 4 | Autumn | 3 | 10.02 | -13.2 | 14.54 | 4.5 | 0 | 0 | 120 | 120 | 13.2 | 45 | 95 | 9.72 | 0 | 0 | 0 | Normal
2025-04-04 04:00 | 94 | 4 | Autumn | 4 | 10.02 | -11.3 | 7.6 | 65.7 | 0 | 0 | 9.65 | 9.65 | 11.3 | 47.85 | 79.72 | -38.2 | 0 | 0 | 0 | Battery-supported
2025-04-04 05:00 | 94 | 4 | Autumn | 5 | 10.02 | -11.7 | 12.35 | 63.9 | 0 | 0 | 97.02 | 97.02 | 11.7 | 45.55 | 95 | 41.52 | 0 | 0 | 0 | Normal
2025-04-04 06:00 | 94 | 4 | Autumn | 6 | 10.02 | -13.8 | 16.39 | 10.5 | 0 | 0 | 120 | 120 | 13.8 | 50.47 | 95 | 0 | 0 | 0 | 0 | Normal
2025-04-04 07:00 | 94 | 4 | Autumn | 7 | 10.02 | -12.6 | 1.97 | 5.6 | 2.4 | 0.14 | 0 | 0.14 | 12.6 | 48.43 | 75.68 | -48.29 | 0 | 0 | 0 | Battery-supported
2025-04-04 08:00 | 94 | 4 | Autumn | 8 | 10.02 | -9.3 | 3.26 | 48.7 | 129.9 | 7.79 | 0 | 7.79 | 9.3 | 50.96 | 58.42 | -43.17 | 0 | 0 | 0 | Battery-supported
2025-04-04 09:00 | 94 | 4 | Autumn | 9 | 10.02 | -13.7 | 9.13 | 23 | 320.1 | 19.21 | 24.98 | 44.19 | 13.7 | 64.24 | 50.4 | -20.05 | 0 | 0 | 0 | Battery-supported
2025-04-04 10:00 | 94 | 4 | Autumn | 10 | 10.02 | -14.9 | 13.03 | 47.7 | 341.3 | 20.48 | 120 | 140.48 | 14.9 | 53.75 | 82.31 | 86.73 | 0 | 0 | 0 | Normal
2025-04-04 11:00 | 94 | 4 | Autumn | 11 | 10.02 | -9.5 | 11.11 | 64.1 | 324.1 | 19.45 | 61.68 | 81.13 | 9.5 | 53.11 | 92.62 | 28.02 | 0 | 0 | 0 | Normal
2025-04-04 12:00 | 94 | 4 | Autumn | 12 | 10.02 | -10.2 | 9.62 | 64.2 | 339.9 | 20.39 | 32.08 | 52.47 | 10.2 | 52.83 | 92.48 | -0.36 | 0 | 0 | 0 | Battery-supported
2025-04-04 13:00 | 94 | 4 | Autumn | 13 | 10.02 | -12.2 | 18.52 | 41.4 | 430.3 | 25.82 | 120 | 145.82 | 12.2 | 56.43 | 95 | 6.85 | 0 | 0 | 0 | Normal
2025-04-04 14:00 | 94 | 4 | Autumn | 14 | 10.02 | -14 | 6.48 | 86.9 | 185.2 | 11.11 | 3.7 | 14.81 | 14 | 57.19 | 78.05 | -42.38 | 0 | 0 | 0 | Battery-supported
2025-04-04 15:00 | 94 | 4 | Autumn | 15 | 10.02 | -11.7 | 4.97 | 53.2 | 232.6 | 13.96 | 0.44 | 14.4 | 11.7 | 59.02 | 60.2 | -44.62 | 0 | 0 | 0 | Battery-supported
2025-04-04 16:00 | 94 | 4 | Autumn | 16 | 10.02 | -9.9 | 5.73 | 63 | 107.9 | 6.47 | 1.55 | 8.02 | 9.9 | 54.15 | 41.75 | -46.13 | 0 | 0 | 0 | Battery-supported
2025-04-04 17:00 | 94 | 4 | Autumn | 17 | 10.02 | -6.9 | 9.25 | 39.6 | 1.8 | 0.11 | 26.61 | 26.72 | 6.9 | 47.3 | 33.52 | -20.58 | 0 | 0 | 0 | Battery-supported
2025-04-04 18:00 | 94 | 4 | Autumn | 18 | 10.02 | -11.5 | 7.43 | 19.1 | 0 | 0 | 8.5 | 8.5 | 11.5 | 50.39 | 16.76 | -41.89 | 0 | 0 | 0 | Battery-supported
2025-04-04 19:00 | 94 | 4 | Autumn | 19 | 10.02 | -9.2 | 13.45 | 57.8 | 0 | 0 | 120 | 120 | 9.2 | 49.12 | 42.84 | 70.88 | 0 | 0 | 0 | Normal
2025-04-04 20:00 | 94 | 4 | Autumn | 20 | 10.02 | -7.5 | 5.15 | 87.9 | 0 | 0 | 0.63 | 0.63 | 7.5 | 47.25 | 24.2 | -46.62 | 0 | 0 | 0 | Battery-supported
2025-04-04 21:00 | 94 | 4 | Autumn | 21 | 10.02 | -14.3 | 9.95 | 56.3 | 0 | 0 | 37.56 | 37.56 | 14.3 | 52.01 | 18.42 | -14.45 | 0 | 0 | 0 | Battery-supported
2025-04-04 22:00 | 94 | 4 | Autumn | 22 | 10.02 | -6.9 | 12.37 | 69.5 | 0 | 0 | 97.67 | 97.67 | 6.9 | 45 | 37.8 | 52.67 | 0 | 0 | 0 | Normal
2025-04-04 23:00 | 94 | 4 | Autumn | 23 | 10.02 | -12 | 16.39 | 61.2 | 0 | 0 | 120 | 120 | 12 | 48.58 | 64.08 | 71.42 | 0 | 0 | 0 | Normal
2025-04-05 | 95 | 4 | Autumn | 0 | 9.87 | -9.2 | 3.68 | 69.3 | 0 | 0 | 0 | 0 | 9.2 | 45 | 46.08 | -45 | 0 | 0 | 0 | Battery-supported
2025-04-05 01:00 | 95 | 4 | Autumn | 1 | 9.87 | -9.8 | 5.68 | 86.4 | 0 | 0 | 1.45 | 1.45 | 9.8 | 45 | 28.66 | -43.55 | 0 | 0 | 0 | Battery-supported
2025-04-05 02:00 | 95 | 4 | Autumn | 2 | 9.87 | -8.3 | 7.13 | 34 | 0 | 0 | 6.69 | 6.69 | 8.3 | 45.23 | 15 | -34.15 | 4.39 | 1.632 | 0 | Diesel-backup
2025-04-05 03:00 | 95 | 4 | Autumn | 3 | 9.87 | -9.9 | 2.97 | 61.4 | 0 | 0 | 0 | 0 | 9.9 | 49.06 | 15 | 0 | 49.06 | 15.699 | 0 | Diesel-backup
2025-04-05 04:00 | 95 | 4 | Autumn | 4 | 9.87 | -16.7 | 9.61 | 73.3 | 0 | 0 | 31.93 | 31.93 | 16.7 | 45.76 | 15 | 0 | 13.83 | 4.977 | 0 | Diesel-backup
2025-04-05 05:00 | 95 | 4 | Autumn | 5 | 9.87 | -13.5 | 9.52 | 32.8 | 0 | 0 | 30.54 | 30.54 | 13.5 | 54.77 | 15 | 0 | 24.23 | 8.398 | 0 | Diesel-backup
2025-04-05 06:00 | 95 | 4 | Autumn | 6 | 9.87 | -11.7 | 9.05 | 81.2 | 0 | 0 | 23.93 | 23.93 | 11.7 | 52.46 | 15 | 0 | 28.53 | 9.731 | 0 | Diesel-backup
2025-04-05 07:00 | 95 | 4 | Autumn | 7 | 9.87 | -12.6 | 6.87 | 67.1 | 0 | 0 | 5.36 | 5.36 | 12.6 | 51.67 | 15 | 0 | 46.31 | 14.819 | 0 | Diesel-backup
2025-04-05 08:00 | 95 | 4 | Autumn | 8 | 9.87 | -11.1 | 15.44 | 35.5 | 141 | 8.46 | 120 | 128.46 | 11.1 | 59.16 | 40.5 | 69.3 | 0 | 0 | 0 | Normal
2025-04-05 09:00 | 95 | 4 | Autumn | 9 | 9.87 | -10.4 | 5.77 | 31.8 | 288.3 | 17.3 | 1.64 | 18.94 | 10.4 | 51.89 | 27.32 | -32.95 | 0 | 0 | 0 | Battery-supported
2025-04-05 10:00 | 95 | 4 | Autumn | 10 | 9.87 | -10.7 | 14.65 | 37.6 | 378.7 | 22.72 | 120 | 142.72 | 10.7 | 50.51 | 61.26 | 92.21 | 0 | 0 | 0 | Normal
2025-04-05 11:00 | 95 | 4 | Autumn | 11 | 9.87 | -12.2 | 5.69 | 23.8 | 511.7 | 30.7 | 1.47 | 32.17 | 12.2 | 55.54 | 51.91 | -23.37 | 0 | 0 | 0 | Battery-supported
2025-04-05 12:00 | 95 | 4 | Autumn | 12 | 9.87 | -15.5 | 3.62 | 56.8 | 376.4 | 22.58 | 0 | 22.58 | 15.5 | 59.7 | 37.06 | -37.12 | 0 | 0 | 0 | Battery-supported
2025-04-05 13:00 | 95 | 4 | Autumn | 13 | 9.87 | -12.1 | 7.67 | 16.8 | 544.3 | 32.66 | 10.15 | 42.81 | 12.1 | 52.6 | 33.14 | -9.79 | 0 | 0 | 0 | Battery-supported
2025-04-05 14:00 | 95 | 4 | Autumn | 14 | 9.87 | -9.8 | 8.54 | 35.9 | 385.5 | 23.13 | 17.92 | 41.05 | 9.8 | 55.16 | 27.5 | -14.11 | 0 | 0 | 0 | Battery-supported
2025-04-05 15:00 | 95 | 4 | Autumn | 15 | 9.87 | -12.7 | 10.08 | 13.6 | 340.1 | 20.41 | 39.87 | 60.28 | 12.7 | 61.34 | 27.08 | -1.06 | 0 | 0 | 0 | Battery-supported
2025-04-05 16:00 | 95 | 4 | Autumn | 16 | 9.87 | -8.6 | 1.53 | 12.7 | 173.9 | 10.43 | 0 | 10.43 | 8.6 | 55.18 | 15 | -30.19 | 14.56 | 5.227 | 0 | Diesel-backup
2025-04-05 17:00 | 95 | 4 | Autumn | 17 | 9.87 | -7.6 | 6.43 | 48.9 | 0 | 0 | 3.52 | 3.52 | 7.6 | 50.79 | 15 | 0 | 47.27 | 15.126 | 0 | Diesel-backup
2025-04-05 18:00 | 95 | 4 | Autumn | 18 | 9.87 | -9.1 | 21.47 | 7 | 0 | 0 | 120 | 120 | 9.1 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-04-05 19:00 | 95 | 4 | Autumn | 19 | 9.87 | -16 | 5.43 | 94.7 | 0 | 0 | 1.01 | 1.01 | 16 | 52.86 | 21.86 | -51.85 | 0 | 0 | 0 | Battery-supported
2025-04-05 20:00 | 95 | 4 | Autumn | 20 | 9.87 | -12 | 13.19 | 60 | 0 | 0 | 120 | 120 | 12 | 54.62 | 45.92 | 65.38 | 0 | 0 | 0 | Normal
2025-04-05 21:00 | 95 | 4 | Autumn | 21 | 9.87 | -5.1 | 33.43 | 74.5 | 0 | 0 | 0 | 0 | 5.1 | 45 | 27.92 | -45 | 0 | 0 | 0 | Battery-supported
2025-04-05 22:00 | 95 | 4 | Autumn | 22 | 9.87 | -10.6 | 23.68 | 68.4 | 0 | 0 | 120 | 120 | 10.6 | 45 | 55.52 | 75 | 0 | 0 | 0 | Normal
2025-04-05 23:00 | 95 | 4 | Autumn | 23 | 9.87 | -14 | 4 | 48.9 | 0 | 0 | 0.02 | 0.02 | 14 | 49.38 | 35.78 | -49.36 | 0 | 0 | 0 | Battery-supported
2025-04-06 | 96 | 4 | Autumn | 0 | 9.71 | -7.4 | 12.61 | 0 | 0 | 0 | 105.82 | 105.82 | 7.4 | 45.25 | 58.07 | 60.57 | 0 | 0 | 0 | Normal
2025-04-06 01:00 | 96 | 4 | Autumn | 1 | 9.71 | -10.5 | 13.06 | 47.2 | 0 | 0 | 120 | 120 | 10.5 | 45.24 | 85.58 | 74.76 | 0 | 0 | 0 | Normal
2025-04-06 02:00 | 96 | 4 | Autumn | 2 | 9.71 | -8.5 | 11.48 | 55.9 | 0 | 0 | 71.12 | 71.12 | 8.5 | 45 | 95 | 25.61 | 0 | 0 | 0 | Normal
2025-04-06 03:00 | 96 | 4 | Autumn | 3 | 9.71 | -10.7 | 3.57 | 59.5 | 0 | 0 | 0 | 0 | 10.7 | 45 | 77 | -45 | 0 | 0 | 0 | Battery-supported
2025-04-06 04:00 | 96 | 4 | Autumn | 4 | 9.71 | -10.6 | 9.04 | 86.6 | 0 | 0 | 23.8 | 23.8 | 10.6 | 48.69 | 67.04 | -24.89 | 0 | 0 | 0 | Battery-supported
2025-04-06 05:00 | 96 | 4 | Autumn | 5 | 9.71 | -11.2 | 9 | 45.5 | 0 | 0 | 23.29 | 23.29 | 11.2 | 45 | 58.36 | -21.71 | 0 | 0 | 0 | Battery-supported
2025-04-06 06:00 | 96 | 4 | Autumn | 6 | 9.71 | -10.7 | 3.23 | 70.8 | 0 | 0 | 0 | 0 | 10.7 | 52.29 | 37.44 | -52.29 | 0 | 0 | 0 | Battery-supported
2025-04-06 07:00 | 96 | 4 | Autumn | 7 | 9.71 | -7.3 | 6.68 | 40.2 | 0 | 0 | 4.5 | 4.5 | 7.3 | 45 | 21.24 | -40.5 | 0 | 0 | 0 | Battery-supported
2025-04-06 08:00 | 96 | 4 | Autumn | 8 | 9.71 | -10.3 | 9.28 | 45.4 | 118.1 | 7.09 | 27.03 | 34.12 | 10.3 | 54.78 | 15 | -15.61 | 5.05 | 1.874 | 0 | Diesel-backup
2025-04-06 09:00 | 96 | 4 | Autumn | 9 | 9.71 | -15.8 | 7.56 | 61.5 | 199.7 | 11.98 | 9.37 | 21.35 | 15.8 | 62.13 | 15 | 0 | 40.78 | 13.27 | 0 | Diesel-backup
2025-04-06 10:00 | 96 | 4 | Autumn | 10 | 9.71 | -11.2 | 11.96 | 49.4 | 329.3 | 19.76 | 84.75 | 104.51 | 11.2 | 52.74 | 34.05 | 51.77 | 0 | 0 | 0 | Normal
2025-04-06 11:00 | 96 | 4 | Autumn | 11 | 9.71 | -9.4 | 6.57 | 54.7 | 366.6 | 22 | 4.05 | 26.05 | 9.4 | 54.28 | 22.76 | -28.23 | 0 | 0 | 0 | Battery-supported
2025-04-06 12:00 | 96 | 4 | Autumn | 12 | 9.71 | -9 | 8.5 | 64.1 | 340.6 | 20.44 | 17.5 | 37.94 | 9 | 49.42 | 18.17 | -11.48 | 0 | 0 | 0 | Battery-supported
2025-04-06 13:00 | 96 | 4 | Autumn | 13 | 9.71 | -12.2 | 13.72 | 65.6 | 315.9 | 18.95 | 120 | 138.95 | 12.2 | 52 | 50.16 | 86.95 | 0 | 0 | 0 | Normal
2025-04-06 14:00 | 96 | 4 | Autumn | 14 | 9.71 | -8.3 | 20.13 | 40.4 | 364.9 | 21.89 | 120 | 141.89 | 8.3 | 47.65 | 84.85 | 94.24 | 0 | 0 | 0 | Normal
2025-04-06 15:00 | 96 | 4 | Autumn | 15 | 9.71 | -8.5 | 3.52 | 19.1 | 317.4 | 19.04 | 0 | 19.04 | 8.5 | 49.54 | 72.65 | -30.5 | 0 | 0 | 0 | Battery-supported
2025-04-06 16:00 | 96 | 4 | Autumn | 16 | 9.71 | -4.5 | 11.7 | 8.8 | 167.3 | 10.04 | 77.17 | 87.21 | 4.5 | 55.73 | 84.23 | 31.48 | 0 | 0 | 0 | Normal
2025-04-06 17:00 | 96 | 4 | Autumn | 17 | 9.71 | -11.5 | 5.93 | 49.8 | 0 | 0 | 2.01 | 2.01 | 11.5 | 50.88 | 64.68 | -48.87 | 0 | 0 | 0 | Battery-supported
2025-04-06 18:00 | 96 | 4 | Autumn | 18 | 9.71 | -10.7 | 10.19 | 70.9 | 0 | 0 | 41.91 | 41.91 | 10.7 | 56.16 | 58.98 | -14.25 | 0 | 0 | 0 | Battery-supported
2025-04-06 19:00 | 96 | 4 | Autumn | 19 | 9.71 | -10.1 | 3.34 | 10.4 | 0 | 0 | 0 | 0 | 10.1 | 52.19 | 38.11 | -52.19 | 0 | 0 | 0 | Battery-supported
2025-04-06 20:00 | 96 | 4 | Autumn | 20 | 9.71 | -10.5 | 15.68 | 66.6 | 0 | 0 | 120 | 120 | 10.5 | 48.96 | 64.25 | 71.04 | 0 | 0 | 0 | Normal
2025-04-06 21:00 | 96 | 4 | Autumn | 21 | 9.71 | -11.4 | 4.79 | 63.8 | 0 | 0 | 0.3 | 0.3 | 11.4 | 49.57 | 44.54 | -49.27 | 0 | 0 | 0 | Battery-supported
2025-04-06 22:00 | 96 | 4 | Autumn | 22 | 9.71 | -15.7 | 13.86 | 56.6 | 0 | 0 | 120 | 120 | 15.7 | 48.69 | 70.78 | 71.31 | 0 | 0 | 0 | Normal
2025-04-06 23:00 | 96 | 4 | Autumn | 23 | 9.71 | -10.8 | 3.65 | 50.1 | 0 | 0 | 0 | 0 | 10.8 | 45 | 52.78 | -45 | 0 | 0 | 0 | Battery-supported
2025-04-07 | 97 | 4 | Autumn | 0 | 9.55 | -9.5 | 2.88 | 73.1 | 0 | 0 | 0 | 0 | 9.5 | 48.83 | 33.25 | -48.83 | 0 | 0 | 0 | Battery-supported
2025-04-07 01:00 | 97 | 4 | Autumn | 1 | 9.55 | -11.8 | 7.03 | 19.5 | 0 | 0 | 6.16 | 6.16 | 11.8 | 45.75 | 17.41 | -39.59 | 0 | 0 | 0 | Battery-supported
2025-04-07 02:00 | 97 | 4 | Autumn | 2 | 9.55 | -6.8 | 9.13 | 75.7 | 0 | 0 | 24.98 | 24.98 | 6.8 | 45 | 15 | -6.04 | 13.98 | 5.03 | 0 | Diesel-backup
2025-04-07 03:00 | 97 | 4 | Autumn | 3 | 9.55 | -11.5 | 25.07 | 16.1 | 0 | 0 | 120 | 120 | 11.5 | 46.39 | 42.09 | 73.61 | 0 | 0 | 0 | Normal
2025-04-07 04:00 | 97 | 4 | Autumn | 4 | 9.55 | -9 | 9 | 25.1 | 0 | 0 | 23.29 | 23.29 | 9 | 45 | 33.4 | -21.71 | 0 | 0 | 0 | Battery-supported
2025-04-07 05:00 | 97 | 4 | Autumn | 5 | 9.55 | -11.6 | 4.02 | 54.2 | 0 | 0 | 0.02 | 0.02 | 11.6 | 45 | 15.41 | -44.98 | 0 | 0 | 0 | Battery-supported
2025-04-07 06:00 | 97 | 4 | Autumn | 6 | 9.55 | -10.6 | 12.65 | 13.9 | 0 | 0 | 107.22 | 107.22 | 10.6 | 49.03 | 36.83 | 58.19 | 0 | 0 | 0 | Normal
2025-04-07 07:00 | 97 | 4 | Autumn | 7 | 9.55 | -11.9 | 17.22 | 29.5 | 0 | 0 | 120 | 120 | 11.9 | 47.79 | 63.4 | 72.21 | 0 | 0 | 0 | Normal
2025-04-07 08:00 | 97 | 4 | Autumn | 8 | 9.55 | -9.6 | 4.63 | 58.3 | 93.2 | 5.59 | 0.2 | 5.79 | 9.6 | 55.86 | 43.37 | -50.07 | 0 | 0 | 0 | Battery-supported
2025-04-07 09:00 | 97 | 4 | Autumn | 9 | 9.55 | -12.4 | 13.62 | 12.9 | 326.8 | 19.61 | 120 | 139.61 | 12.4 | 55.86 | 74.19 | 83.75 | 0 | 0 | 0 | Normal
2025-04-07 10:00 | 97 | 4 | Autumn | 10 | 9.55 | -11.3 | 16.01 | 65.6 | 263.5 | 15.81 | 120 | 135.81 | 11.3 | 58.52 | 95 | 56.54 | 0 | 0 | 0 | Normal
2025-04-07 11:00 | 97 | 4 | Autumn | 11 | 9.55 | -11.4 | 12.82 | 13 | 560.4 | 33.62 | 113.31 | 146.93 | 11.4 | 55.01 | 95 | 0 | 0 | 0 | 0 | Normal
2025-04-07 12:00 | 97 | 4 | Autumn | 12 | 9.55 | -12.5 | 5.29 | 47.6 | 421.8 | 25.31 | 0.8 | 26.11 | 12.5 | 60.99 | 81.05 | -34.88 | 0 | 0 | 0 | Battery-supported
2025-04-07 13:00 | 97 | 4 | Autumn | 13 | 9.55 | -10.6 | 9.18 | 53.8 | 370.5 | 22.23 | 25.65 | 47.88 | 10.6 | 49.98 | 80.21 | -2.1 | 0 | 0 | 0 | Battery-supported
2025-04-07 14:00 | 97 | 4 | Autumn | 14 | 9.55 | -6.2 | 10.22 | 59.4 | 287.9 | 17.27 | 42.47 | 59.74 | 6.2 | 46.04 | 85.25 | 13.7 | 0 | 0 | 0 | Normal
2025-04-07 15:00 | 97 | 4 | Autumn | 15 | 9.55 | -11.3 | 15.48 | 71.7 | 167.2 | 10.03 | 120 | 130.03 | 11.3 | 61.45 | 95 | 26.5 | 0 | 0 | 0 | Normal
2025-04-07 16:00 | 97 | 4 | Autumn | 16 | 9.55 | -9.4 | 5.52 | 59.8 | 91.3 | 5.48 | 1.15 | 6.63 | 9.4 | 55.71 | 75.37 | -49.08 | 0 | 0 | 0 | Battery-supported
2025-04-07 17:00 | 97 | 4 | Autumn | 17 | 9.55 | -7.3 | 13.82 | 69.9 | 0 | 0 | 120 | 120 | 7.3 | 57.76 | 95 | 53.35 | 0 | 0 | 0 | Normal
2025-04-07 18:00 | 97 | 4 | Autumn | 18 | 9.55 | -7.3 | 7.43 | 55.8 | 0 | 0 | 8.5 | 8.5 | 7.3 | 52.75 | 77.3 | -44.25 | 0 | 0 | 0 | Battery-supported
2025-04-07 19:00 | 97 | 4 | Autumn | 19 | 9.55 | -9.6 | 6.47 | 83.1 | 0 | 0 | 3.67 | 3.67 | 9.6 | 51.49 | 58.17 | -47.82 | 0 | 0 | 0 | Battery-supported
2025-04-07 20:00 | 97 | 4 | Autumn | 20 | 9.55 | -14.8 | 8.35 | 65.8 | 0 | 0 | 15.97 | 15.97 | 14.8 | 65.27 | 38.45 | -49.3 | 0 | 0 | 0 | Battery-supported
2025-04-07 21:00 | 97 | 4 | Autumn | 21 | 9.55 | -8.5 | 1.32 | 61 | 0 | 0 | 0 | 0 | 8.5 | 45 | 20.45 | -45 | 0 | 0 | 0 | Battery-supported
2025-04-07 22:00 | 97 | 4 | Autumn | 22 | 9.55 | -14.7 | 1.71 | 53.6 | 0 | 0 | 0 | 0 | 14.7 | 52.9 | 15 | -13.63 | 39.27 | 12.854 | 0 | Diesel-backup
2025-04-07 23:00 | 97 | 4 | Autumn | 23 | 9.55 | -6.8 | 2.12 | 56.5 | 0 | 0 | 0 | 0 | 6.8 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-04-08 | 98 | 4 | Autumn | 0 | 9.39 | -10.2 | 10.52 | 39.1 | 0 | 0 | 48.42 | 48.42 | 10.2 | 51.22 | 15 | 0 | 2.8 | 1.047 | 0 | Diesel-backup
2025-04-08 01:00 | 98 | 4 | Autumn | 1 | 9.39 | -8.7 | 6.96 | 2.5 | 0 | 0 | 5.8 | 5.8 | 8.7 | 45 | 15 | 0 | 39.2 | 12.835 | 0 | Diesel-backup
2025-04-08 02:00 | 98 | 4 | Autumn | 2 | 9.39 | -13.3 | 5.32 | 78.3 | 0 | 0 | 0.84 | 0.84 | 13.3 | 47.08 | 15 | 0 | 46.24 | 14.797 | 0 | Diesel-backup
2025-04-08 03:00 | 98 | 4 | Autumn | 3 | 9.39 | -15.1 | 7.93 | 33 | 0 | 0 | 12.17 | 12.17 | 15.1 | 46.23 | 15 | 0 | 34.06 | 11.376 | 0 | Diesel-backup
2025-04-08 04:00 | 98 | 4 | Autumn | 4 | 9.39 | -11.5 | 14.05 | 50.6 | 0 | 0 | 120 | 120 | 11.5 | 48.87 | 41.18 | 71.13 | 0 | 0 | 0 | Normal
2025-04-08 05:00 | 98 | 4 | Autumn | 5 | 9.39 | -12.4 | 7.71 | 69.2 | 0 | 0 | 10.44 | 10.44 | 12.4 | 46.66 | 26.69 | -36.22 | 0 | 0 | 0 | Battery-supported
2025-04-08 06:00 | 98 | 4 | Autumn | 6 | 9.39 | -13.7 | 3.96 | 43.1 | 0 | 0 | 0.01 | 0.01 | 13.7 | 54.23 | 15 | -29.22 | 25 | 8.64 | 0 | Diesel-backup
2025-04-08 07:00 | 98 | 4 | Autumn | 7 | 9.39 | -12.6 | 27.43 | 28.8 | 0 | 0 | 120 | 120 | 12.6 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-04-08 08:00 | 98 | 4 | Autumn | 8 | 9.39 | -6.7 | 8.18 | 32 | 115.1 | 6.91 | 14.35 | 21.26 | 6.7 | 45 | 33.1 | -23.74 | 0 | 0 | 0 | Battery-supported
2025-04-08 09:00 | 98 | 4 | Autumn | 9 | 9.39 | -10.9 | 16.15 | 33.2 | 264.8 | 15.89 | 120 | 135.89 | 10.9 | 52.02 | 63.97 | 83.87 | 0 | 0 | 0 | Normal
2025-04-08 10:00 | 98 | 4 | Autumn | 10 | 9.39 | -10.3 | 12.94 | 29 | 402.5 | 24.15 | 117.74 | 141.89 | 10.3 | 59.85 | 94.16 | 82.04 | 0 | 0 | 0 | Normal
2025-04-08 11:00 | 98 | 4 | Autumn | 11 | 9.39 | -10.5 | 6.23 | 81.4 | 241.2 | 14.47 | 2.85 | 17.32 | 10.5 | 57.67 | 78.02 | -40.35 | 0 | 0 | 0 | Battery-supported
2025-04-08 12:00 | 98 | 4 | Autumn | 12 | 9.39 | -8.8 | 20.11 | 70.9 | 307 | 18.42 | 120 | 138.42 | 8.8 | 56.43 | 95 | 46.14 | 0 | 0 | 0 | Normal
2025-04-08 13:00 | 98 | 4 | Autumn | 13 | 9.39 | -12.1 | 5.61 | 71.4 | 288 | 17.28 | 1.31 | 18.59 | 12.1 | 52.9 | 81.28 | -34.31 | 0 | 0 | 0 | Battery-supported
2025-04-08 14:00 | 98 | 4 | Autumn | 14 | 9.39 | -15.8 | 10.42 | 79.8 | 206.5 | 12.39 | 46.38 | 58.77 | 15.8 | 53.52 | 83.21 | 5.25 | 0 | 0 | 0 | Normal
2025-04-08 15:00 | 98 | 4 | Autumn | 15 | 9.39 | -11.3 | 9.62 | 55.7 | 205.3 | 12.32 | 32.08 | 44.4 | 11.3 | 59.99 | 76.97 | -15.59 | 0 | 0 | 0 | Battery-supported
2025-04-08 16:00 | 98 | 4 | Autumn | 16 | 9.39 | -8.8 | 10.15 | 28.3 | 119.3 | 7.16 | 41.16 | 48.32 | 8.8 | 46.29 | 77.72 | 2.03 | 0 | 0 | 0 | Normal
2025-04-08 17:00 | 98 | 4 | Autumn | 17 | 9.39 | -12.4 | 18.22 | 74.6 | 0 | 0 | 120 | 120 | 12.4 | 55.42 | 95 | 46.96 | 0 | 0 | 0 | Normal
2025-04-08 18:00 | 98 | 4 | Autumn | 18 | 9.39 | -10.4 | 8.31 | 69.2 | 0 | 0 | 15.58 | 15.58 | 10.4 | 50.74 | 80.94 | -35.16 | 0 | 0 | 0 | Battery-supported
2025-04-08 19:00 | 98 | 4 | Autumn | 19 | 9.39 | -11.4 | 9.27 | 21.5 | 0 | 0 | 26.89 | 26.89 | 11.4 | 54.7 | 69.81 | -27.81 | 0 | 0 | 0 | Battery-supported
2025-04-08 20:00 | 98 | 4 | Autumn | 20 | 9.39 | -6.5 | 9.55 | 26.5 | 0 | 0 | 30.99 | 30.99 | 6.5 | 45 | 64.21 | -14.01 | 0 | 0 | 0 | Battery-supported
2025-04-08 21:00 | 98 | 4 | Autumn | 21 | 9.39 | -8.2 | 24.56 | 21.5 | 0 | 0 | 120 | 120 | 8.2 | 46.6 | 91.22 | 73.4 | 0 | 0 | 0 | Normal
2025-04-08 22:00 | 98 | 4 | Autumn | 22 | 9.39 | -8.6 | 15.46 | 55.1 | 0 | 0 | 120 | 120 | 8.6 | 49.08 | 95 | 10.27 | 0 | 0 | 0 | Normal
2025-04-08 23:00 | 98 | 4 | Autumn | 23 | 9.39 | -8.9 | 2.78 | 84.9 | 0 | 0 | 0 | 0 | 8.9 | 48.08 | 75.77 | -48.08 | 0 | 0 | 0 | Battery-supported
2025-04-09 | 99 | 4 | Autumn | 0 | 9.23 | -10.8 | 5.77 | 59.5 | 0 | 0 | 1.64 | 1.64 | 10.8 | 45 | 58.42 | -43.36 | 0 | 0 | 0 | Battery-supported
2025-04-09 01:00 | 99 | 4 | Autumn | 1 | 9.23 | -10.7 | 8.69 | 48.5 | 0 | 0 | 19.57 | 19.57 | 10.7 | 47.44 | 47.28 | -27.87 | 0 | 0 | 0 | Battery-supported
2025-04-09 02:00 | 99 | 4 | Autumn | 2 | 9.23 | -14.1 | 18.08 | 18.4 | 0 | 0 | 120 | 120 | 14.1 | 48.41 | 73.62 | 71.59 | 0 | 0 | 0 | Normal
2025-04-09 03:00 | 99 | 4 | Autumn | 3 | 9.23 | -16.7 | 19.07 | 26.2 | 0 | 0 | 120 | 120 | 16.7 | 51.7 | 95 | 58.09 | 0 | 0 | 0 | Normal
2025-04-09 04:00 | 99 | 4 | Autumn | 4 | 9.23 | -11.9 | 8.04 | 52.1 | 0 | 0 | 13.1 | 13.1 | 11.9 | 53.54 | 78.82 | -40.44 | 0 | 0 | 0 | Battery-supported
2025-04-09 05:00 | 99 | 4 | Autumn | 5 | 9.23 | -11.9 | 5.64 | 73.8 | 0 | 0 | 1.37 | 1.37 | 11.9 | 45.16 | 61.31 | -43.79 | 0 | 0 | 0 | Battery-supported
2025-04-09 06:00 | 99 | 4 | Autumn | 6 | 9.23 | -10.1 | 7.37 | 81.7 | 0 | 0 | 8.11 | 8.11 | 10.1 | 47.82 | 45.42 | -39.71 | 0 | 0 | 0 | Battery-supported
2025-04-09 07:00 | 99 | 4 | Autumn | 7 | 9.23 | -9.5 | 8.88 | 54.2 | 0 | 0 | 21.8 | 21.8 | 9.5 | 45 | 36.14 | -23.2 | 0 | 0 | 0 | Battery-supported
2025-04-09 08:00 | 99 | 4 | Autumn | 8 | 9.23 | -9.6 | 7.06 | 60 | 75.2 | 4.51 | 6.31 | 10.82 | 9.6 | 52.89 | 19.32 | -42.07 | 0 | 0 | 0 | Battery-supported
2025-04-09 09:00 | 99 | 4 | Autumn | 9 | 9.23 | -15.2 | 16.44 | 17.4 | 298.3 | 17.9 | 120 | 137.9 | 15.2 | 61.92 | 47.28 | 75.98 | 0 | 0 | 0 | Normal
2025-04-09 10:00 | 99 | 4 | Autumn | 10 | 9.23 | -13.6 | 6.64 | 25.9 | 410.7 | 24.64 | 4.33 | 28.97 | 13.6 | 56 | 36.46 | -27.03 | 0 | 0 | 0 | Battery-supported
2025-04-09 11:00 | 99 | 4 | Autumn | 11 | 9.23 | -11.5 | 4.71 | 52.7 | 374.1 | 22.45 | 0.25 | 22.7 | 11.5 | 56.96 | 22.76 | -34.26 | 0 | 0 | 0 | Battery-supported
2025-04-09 12:00 | 99 | 4 | Autumn | 12 | 9.23 | -6.7 | 7.27 | 82.2 | 251.5 | 15.09 | 7.5 | 22.59 | 6.7 | 46.46 | 15 | -19.4 | 4.47 | 1.662 | 0 | Diesel-backup
2025-04-09 13:00 | 99 | 4 | Autumn | 13 | 9.23 | -8.6 | 9.94 | 100 | 154.6 | 9.28 | 37.38 | 46.66 | 8.6 | 49.74 | 15 | 0 | 3.08 | 1.151 | 0 | Diesel-backup
2025-04-09 14:00 | 99 | 4 | Autumn | 14 | 9.23 | -9 | 16.61 | 69.7 | 243.4 | 14.6 | 120 | 134.6 | 9 | 51.46 | 45.6 | 83.14 | 0 | 0 | 0 | Normal
2025-04-09 15:00 | 99 | 4 | Autumn | 15 | 9.23 | -12 | 4.47 | 7.8 | 323 | 19.38 | 0.13 | 19.51 | 12 | 52.83 | 32.27 | -33.32 | 0 | 0 | 0 | Battery-supported
2025-04-09 16:00 | 99 | 4 | Autumn | 16 | 9.23 | -12.7 | 9.98 | 27.2 | 108.8 | 6.53 | 38.08 | 44.61 | 12.7 | 59.29 | 26.4 | -14.68 | 0 | 0 | 0 | Battery-supported
2025-04-09 17:00 | 99 | 4 | Autumn | 17 | 9.23 | -8.7 | 10.16 | 38.1 | 0 | 0 | 41.35 | 41.35 | 8.7 | 56.07 | 20.51 | -14.72 | 0 | 0 | 0 | Battery-supported
2025-04-09 18:00 | 99 | 4 | Autumn | 18 | 9.23 | -12.6 | 11.28 | 84.8 | 0 | 0 | 65.91 | 65.91 | 12.6 | 58.19 | 23.35 | 7.72 | 0 | 0 | 0 | Normal
2025-04-09 19:00 | 99 | 4 | Autumn | 19 | 9.23 | -10.6 | 6.64 | 49 | 0 | 0 | 4.33 | 4.33 | 10.6 | 45 | 15 | -20.87 | 19.8 | 6.974 | 0 | Diesel-backup
2025-04-09 20:00 | 99 | 4 | Autumn | 20 | 9.23 | -10.3 | 11.17 | 60.3 | 0 | 0 | 63.15 | 63.15 | 10.3 | 52.03 | 19.09 | 11.12 | 0 | 0 | 0 | Normal
2025-04-09 21:00 | 99 | 4 | Autumn | 21 | 9.23 | -6.6 | 12.8 | 92.7 | 0 | 0 | 112.58 | 112.58 | 6.6 | 45 | 43.96 | 67.58 | 0 | 0 | 0 | Normal
2025-04-09 22:00 | 99 | 4 | Autumn | 22 | 9.23 | -11 | 6.59 | 86.5 | 0 | 0 | 4.13 | 4.13 | 11 | 45.35 | 27.47 | -41.22 | 0 | 0 | 0 | Battery-supported
2025-04-09 23:00 | 99 | 4 | Autumn | 23 | 9.23 | -15.8 | 9.3 | 60.4 | 0 | 0 | 27.31 | 27.31 | 15.8 | 49.91 | 18.43 | -22.6 | 0 | 0 | 0 | Battery-supported
2025-04-10 | 100 | 4 | Autumn | 0 | 9.07 | -9.9 | 7.57 | 49.3 | 0 | 0 | 9.44 | 9.44 | 9.9 | 48.64 | 15 | -8.58 | 30.62 | 10.361 | 0 | Diesel-backup
2025-04-10 01:00 | 100 | 4 | Autumn | 1 | 9.07 | -12.9 | 5.15 | 39 | 0 | 0 | 0.63 | 0.63 | 12.9 | 51.85 | 15 | 0 | 51.22 | 16.39 | 0 | Diesel-backup
2025-04-10 02:00 | 100 | 4 | Autumn | 2 | 9.07 | -11.6 | 3.45 | 66.5 | 0 | 0 | 0 | 0 | 11.6 | 48.99 | 15 | 0 | 48.99 | 15.677 | 0 | Diesel-backup
2025-04-10 03:00 | 100 | 4 | Autumn | 3 | 9.07 | -12.3 | 5.65 | 22 | 0 | 0 | 1.39 | 1.39 | 12.3 | 45 | 15 | 0 | 43.61 | 14.033 | 0 | Diesel-backup
2025-04-10 04:00 | 100 | 4 | Autumn | 4 | 9.07 | -13.1 | 5.91 | 59.4 | 0 | 0 | 1.96 | 1.96 | 13.1 | 45 | 15 | 0 | 43.04 | 13.881 | 0 | Diesel-backup
2025-04-10 05:00 | 100 | 4 | Autumn | 5 | 9.07 | -11 | 3.41 | 85.8 | 0 | 0 | 0 | 0 | 11 | 47.57 | 15 | 0 | 47.57 | 15.222 | 0 | Diesel-backup
2025-04-10 06:00 | 100 | 4 | Autumn | 6 | 9.07 | -16.4 | 10.79 | 8.1 | 0 | 0 | 54.22 | 54.22 | 16.4 | 45 | 18.39 | 9.22 | 0 | 0 | 0 | Normal
2025-04-10 07:00 | 100 | 4 | Autumn | 7 | 9.07 | -14.3 | 13.37 | 6.5 | 0 | 0 | 120 | 120 | 14.3 | 55.86 | 42 | 64.14 | 0 | 0 | 0 | Normal
2025-04-10 08:00 | 100 | 4 | Autumn | 8 | 9.07 | -11.7 | 7.45 | 62.2 | 64.7 | 3.88 | 8.63 | 12.51 | 11.7 | 55.24 | 24.9 | -42.73 | 0 | 0 | 0 | Battery-supported
2025-04-10 09:00 | 100 | 4 | Autumn | 9 | 9.07 | -14.5 | 8.13 | 29.9 | 258.1 | 15.49 | 13.89 | 29.38 | 14.5 | 54.68 | 15 | -24.76 | 0.54 | 0.203 | 0 | Diesel-backup
2025-04-10 10:00 | 100 | 4 | Autumn | 10 | 9.07 | -16.5 | 6.16 | 35 | 372.4 | 22.34 | 2.63 | 24.97 | 16.5 | 57.37 | 15 | 0 | 32.4 | 10.891 | 0 | Diesel-backup
2025-04-10 11:00 | 100 | 4 | Autumn | 11 | 9.07 | -11.3 | 7.86 | 89.2 | 204.4 | 12.26 | 11.6 | 23.86 | 11.3 | 59.13 | 15 | 0 | 35.27 | 11.726 | 0 | Diesel-backup
2025-04-10 12:00 | 100 | 4 | Autumn | 12 | 9.07 | -10 | 11.26 | 52.2 | 399.4 | 23.96 | 65.4 | 89.36 | 10 | 47.96 | 30.24 | 41.4 | 0 | 0 | 0 | Normal
2025-04-10 13:00 | 100 | 4 | Autumn | 13 | 9.07 | -12.2 | 10.03 | 73.8 | 275.5 | 16.53 | 38.97 | 55.5 | 12.2 | 47.51 | 33.18 | 7.99 | 0 | 0 | 0 | Normal
2025-04-10 14:00 | 100 | 4 | Autumn | 14 | 9.07 | -16 | 7.83 | 28.8 | 396 | 23.76 | 11.36 | 35.12 | 16 | 55.03 | 25.21 | -19.91 | 0 | 0 | 0 | Battery-supported
2025-04-10 15:00 | 100 | 4 | Autumn | 15 | 9.07 | -9.8 | 5.9 | 65.1 | 170.3 | 10.22 | 1.93 | 12.15 | 9.8 | 53.98 | 15 | -25.53 | 16.3 | 5.815 | 0 | Diesel-backup
2025-04-10 16:00 | 100 | 4 | Autumn | 16 | 9.07 | -14.6 | 12.73 | 38.3 | 86.4 | 5.18 | 110.06 | 115.24 | 14.6 | 64.01 | 33.85 | 51.23 | 0 | 0 | 0 | Normal
2025-04-10 17:00 | 100 | 4 | Autumn | 17 | 9.07 | -10 | 6.29 | 73.6 | 0 | 0 | 3.04 | 3.04 | 10 | 57.87 | 15 | -47.13 | 7.7 | 2.831 | 0 | Diesel-backup
2025-04-10 18:00 | 100 | 4 | Autumn | 18 | 9.07 | -12.4 | 3.6 | 16 | 0 | 0 | 0 | 0 | 12.4 | 53.65 | 15 | 0 | 53.65 | 17.168 | 0 | Diesel-backup
2025-04-10 19:00 | 100 | 4 | Autumn | 19 | 9.07 | -12.8 | 9.01 | 69.8 | 0 | 0 | 23.41 | 23.41 | 12.8 | 56.93 | 15 | 0 | 33.52 | 11.219 | 0 | Diesel-backup
2025-04-10 20:00 | 100 | 4 | Autumn | 20 | 9.07 | -11.2 | 2.44 | 5.6 | 0 | 0 | 0 | 0 | 11.2 | 55.59 | 15 | 0 | 55.59 | 17.789 | 0 | Diesel-backup
2025-04-10 21:00 | 100 | 4 | Autumn | 21 | 9.07 | -10.7 | 9.79 | 41.7 | 0 | 0 | 34.83 | 34.83 | 10.7 | 46.59 | 15 | 0 | 11.76 | 4.264 | 0 | Diesel-backup
2025-04-10 22:00 | 100 | 4 | Autumn | 22 | 9.07 | -11.8 | 10.22 | 40.7 | 0 | 0 | 42.47 | 42.47 | 11.8 | 45 | 15 | 0 | 2.53 | 0.947 | 0 | Diesel-backup
2025-04-10 23:00 | 100 | 4 | Autumn | 23 | 9.07 | -9.4 | 5.61 | 97.8 | 0 | 0 | 1.31 | 1.31 | 9.4 | 45 | 15 | 0 | 43.69 | 14.054 | 0 | Diesel-backup
2025-04-11 | 101 | 4 | Autumn | 0 | 8.91 | -12.1 | 6.15 | 80.2 | 0 | 0 | 2.6 | 2.6 | 12.1 | 50.26 | 15 | 0 | 47.66 | 15.251 | 0 | Diesel-backup
2025-04-11 01:00 | 101 | 4 | Autumn | 1 | 8.91 | -9.4 | 13.82 | 16.2 | 0 | 0 | 120 | 120 | 9.4 | 51.86 | 40.08 | 68.14 | 0 | 0 | 0 | Normal
2025-04-11 02:00 | 101 | 4 | Autumn | 2 | 8.91 | -11.3 | 23.5 | 63.1 | 0 | 0 | 120 | 120 | 11.3 | 47.89 | 66.61 | 72.11 | 0 | 0 | 0 | Normal
2025-04-11 03:00 | 101 | 4 | Autumn | 3 | 8.91 | -13.8 | 8.43 | 73.3 | 0 | 0 | 16.77 | 16.77 | 13.8 | 53.17 | 52.05 | -36.4 | 0 | 0 | 0 | Battery-supported
2025-04-11 04:00 | 101 | 4 | Autumn | 4 | 8.91 | -14.6 | 1.77 | 50.1 | 0 | 0 | 0 | 0 | 14.6 | 53.13 | 30.8 | -53.13 | 0 | 0 | 0 | Battery-supported
2025-04-11 05:00 | 101 | 4 | Autumn | 5 | 8.91 | -16.6 | 5.7 | 65.3 | 0 | 0 | 1.49 | 1.49 | 16.6 | 50.08 | 15 | -39.5 | 9.09 | 3.327 | 0 | Diesel-backup
2025-04-11 06:00 | 101 | 4 | Autumn | 6 | 8.91 | -12.6 | 10.31 | 37.1 | 0 | 0 | 44.2 | 44.2 | 12.6 | 45 | 15 | 0 | 0.8 | 0.301 | 0 | Diesel-backup
2025-04-11 07:00 | 101 | 4 | Autumn | 7 | 8.91 | -14.1 | 7.67 | 66.6 | 0 | 0 | 10.15 | 10.15 | 14.1 | 53.63 | 15 | 0 | 43.48 | 13.998 | 0 | Diesel-backup
2025-04-11 08:00 | 101 | 4 | Autumn | 8 | 8.91 | -18.6 | 9.91 | 57.5 | 59.8 | 3.05 | 36.86 | 39.91 | 18.6 | 69.01 | 15 | 0 | 29.1 | 9.904 | 0 | Diesel-backup
2025-04-11 09:00 | 101 | 4 | Autumn | 9 | 8.91 | -14.5 | 9.06 | 94.4 | 94.2 | 5.65 | 24.06 | 29.71 | 14.5 | 55.81 | 15 | 0 | 26.1 | 8.983 | 0 | Diesel-backup
2025-04-11 10:00 | 101 | 4 | Autumn | 10 | 8.91 | -15.2 | 9.19 | 41.7 | 343.4 | 20.6 | 25.78 | 46.38 | 15.2 | 62.97 | 15 | 0 | 16.59 | 5.912 | 0 | Diesel-backup
2025-04-11 11:00 | 101 | 4 | Autumn | 11 | 8.91 | -9.5 | 1.88 | 80.5 | 243.8 | 14.63 | 0 | 14.63 | 9.5 | 53.1 | 15 | 0 | 38.47 | 12.632 | 0 | Diesel-backup
2025-04-11 12:00 | 101 | 4 | Autumn | 12 | 8.91 | -16.4 | 6.13 | 34.5 | 486.4 | 29.18 | 2.55 | 31.73 | 16.4 | 53.88 | 15 | 0 | 22.15 | 7.736 | 0 | Diesel-backup
2025-04-11 13:00 | 101 | 4 | Autumn | 13 | 8.91 | -15.5 | 5.77 | 42.5 | 419.4 | 25.16 | 1.64 | 26.8 | 15.5 | 58.69 | 15 | 0 | 31.89 | 10.74 | 0 | Diesel-backup
2025-04-11 14:00 | 101 | 4 | Autumn | 14 | 8.91 | -9.5 | 5.72 | 19.8 | 425.4 | 25.52 | 1.53 | 27.05 | 9.5 | 50.23 | 15 | 0 | 23.18 | 8.065 | 0 | Diesel-backup
2025-04-11 15:00 | 101 | 4 | Autumn | 15 | 8.91 | -8.5 | 11.8 | 69.7 | 153.8 | 9.23 | 80.03 | 89.26 | 8.5 | 53.27 | 28.24 | 35.99 | 0 | 0 | 0 | Normal
2025-04-11 16:00 | 101 | 4 | Autumn | 16 | 8.91 | -12.8 | 3.84 | 79.4 | 42.6 | 2.56 | 0.01 | 2.57 | 12.8 | 57.4 | 15 | -33.11 | 21.72 | 7.597 | 0 | Diesel-backup
2025-04-11 17:00 | 101 | 4 | Autumn | 17 | 8.91 | -12.2 | 1.89 | 59.9 | 0 | 0 | 0 | 0 | 12.2 | 52.62 | 15 | 0 | 52.62 | 16.838 | 0 | Diesel-backup
2025-04-11 18:00 | 101 | 4 | Autumn | 18 | 8.91 | -9.3 | 5.64 | 34.7 | 0 | 0 | 1.37 | 1.37 | 9.3 | 47.07 | 15 | 0 | 45.7 | 14.624 | 0 | Diesel-backup
2025-04-11 19:00 | 101 | 4 | Autumn | 19 | 8.91 | -15.6 | 4.93 | 18.3 | 0 | 0 | 0.41 | 0.41 | 15.6 | 56.77 | 15 | 0 | 56.36 | 18.035 | 0 | Diesel-backup
2025-04-11 20:00 | 101 | 4 | Autumn | 20 | 8.91 | -14.5 | 8.47 | 90.7 | 0 | 0 | 17.18 | 17.18 | 14.5 | 63.7 | 15 | 0 | 46.52 | 14.886 | 0 | Diesel-backup
2025-04-11 21:00 | 101 | 4 | Autumn | 21 | 8.91 | -11.1 | 4.91 | 21.6 | 0 | 0 | 0.39 | 0.39 | 11.1 | 45 | 15 | 0 | 44.61 | 14.297 | 0 | Diesel-backup
2025-04-11 22:00 | 101 | 4 | Autumn | 22 | 8.91 | -7.2 | 7.01 | 38 | 0 | 0 | 6.05 | 6.05 | 7.2 | 45.1 | 15 | 0 | 39.05 | 12.793 | 0 | Diesel-backup
2025-04-11 23:00 | 101 | 4 | Autumn | 23 | 8.91 | -11.8 | 6.41 | 74.4 | 0 | 0 | 3.45 | 3.45 | 11.8 | 49.19 | 15 | 0 | 45.74 | 14.637 | 0 | Diesel-backup
2025-04-12 | 102 | 4 | Autumn | 0 | 8.75 | -11.2 | 16.32 | 28 | 0 | 0 | 120 | 120 | 11.2 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-04-12 01:00 | 102 | 4 | Autumn | 1 | 8.75 | -9.2 | 5.01 | 24.3 | 0 | 0 | 0.48 | 0.48 | 9.2 | 45 | 24.79 | -44.52 | 0 | 0 | 0 | Battery-supported
2025-04-12 02:00 | 102 | 4 | Autumn | 2 | 8.75 | -7.5 | 11.44 | 44.7 | 0 | 0 | 70.06 | 70.06 | 7.5 | 45 | 34.01 | 25.06 | 0 | 0 | 0 | Normal
2025-04-12 03:00 | 102 | 4 | Autumn | 3 | 8.75 | -13.8 | 7.86 | 55.9 | 0 | 0 | 11.6 | 11.6 | 13.8 | 48.69 | 19.18 | -37.09 | 0 | 0 | 0 | Battery-supported
2025-04-12 04:00 | 102 | 4 | Autumn | 4 | 8.75 | -12.9 | 14.05 | 39.9 | 0 | 0 | 120 | 120 | 12.9 | 45.89 | 46.45 | 74.11 | 0 | 0 | 0 | Normal
2025-04-12 05:00 | 102 | 4 | Autumn | 5 | 8.75 | -9.2 | 19.11 | 84.9 | 0 | 0 | 120 | 120 | 9.2 | 46.09 | 73.65 | 73.91 | 0 | 0 | 0 | Normal
2025-04-12 06:00 | 102 | 4 | Autumn | 6 | 8.75 | -16.8 | 7.78 | 48.9 | 0 | 0 | 10.97 | 10.97 | 16.8 | 58.3 | 54.72 | -47.33 | 0 | 0 | 0 | Battery-supported
2025-04-12 07:00 | 102 | 4 | Autumn | 7 | 8.75 | -11.3 | 2.51 | 54.7 | 0 | 0 | 0 | 0 | 11.3 | 51.26 | 34.21 | -51.26 | 0 | 0 | 0 | Battery-supported
2025-04-12 08:00 | 102 | 4 | Autumn | 8 | 8.75 | -15.9 | 3.87 | 29.9 | 68.5 | 4.11 | 0.01 | 4.12 | 15.9 | 59.41 | 15 | -48.03 | 7.26 | 2.673 | 0 | Diesel-backup
2025-04-12 09:00 | 102 | 4 | Autumn | 9 | 8.75 | -13.3 | 3.27 | 51.7 | 190.4 | 11.42 | 0 | 11.42 | 13.3 | 45 | 15 | 0 | 33.58 | 11.236 | 0 | Diesel-backup
2025-04-12 10:00 | 102 | 4 | Autumn | 10 | 8.75 | -14 | 6.18 | 48.2 | 315.5 | 18.93 | 2.69 | 21.62 | 14 | 56.04 | 15 | 0 | 34.42 | 11.481 | 0 | Diesel-backup
2025-04-12 11:00 | 102 | 4 | Autumn | 11 | 8.75 | -15.3 | 5.59 | 40.1 | 429.2 | 25.75 | 1.28 | 27.03 | 15.3 | 54.29 | 15 | 0 | 27.26 | 9.342 | 0 | Diesel-backup
2025-04-12 12:00 | 102 | 4 | Autumn | 12 | 8.75 | -15 | 9.35 | 55.2 | 384.2 | 23.05 | 28.02 | 51.07 | 15 | 57.19 | 15 | 0 | 6.12 | 2.263 | 0 | Diesel-backup
2025-04-12 13:00 | 102 | 4 | Autumn | 13 | 8.75 | -11.9 | 13.44 | 85.1 | 222 | 13.32 | 120 | 133.32 | 11.9 | 53.5 | 44.37 | 79.82 | 0 | 0 | 0 | Normal
2025-04-12 14:00 | 102 | 4 | Autumn | 14 | 8.75 | -9.9 | 2.32 | 28 | 390.2 | 23.41 | 0 | 23.41 | 9.9 | 51.64 | 33.08 | -28.23 | 0 | 0 | 0 | Battery-supported
2025-04-12 15:00 | 102 | 4 | Autumn | 15 | 8.75 | -12 | 8.21 | 59.7 | 171.7 | 10.3 | 14.62 | 24.92 | 12 | 59.31 | 19.33 | -34.39 | 0 | 0 | 0 | Battery-supported
2025-04-12 16:00 | 102 | 4 | Autumn | 16 | 8.75 | -11.2 | 5.1 | 65.4 | 45 | 2.7 | 0.57 | 3.27 | 11.2 | 53.29 | 15 | -10.81 | 39.21 | 12.837 | 0 | Diesel-backup
2025-04-12 17:00 | 102 | 4 | Autumn | 17 | 8.75 | -9.8 | 8.38 | 70.3 | 0 | 0 | 16.27 | 16.27 | 9.8 | 51.72 | 15 | 0 | 35.45 | 11.777 | 0 | Diesel-backup
2025-04-12 18:00 | 102 | 4 | Autumn | 18 | 8.75 | -13 | 6.19 | 26.6 | 0 | 0 | 2.72 | 2.72 | 13 | 57.91 | 15 | 0 | 55.19 | 17.661 | 0 | Diesel-backup
2025-04-12 19:00 | 102 | 4 | Autumn | 19 | 8.75 | -9 | 12.18 | 15.4 | 0 | 0 | 91.53 | 91.53 | 9 | 47.77 | 31.1 | 43.76 | 0 | 0 | 0 | Normal
2025-04-12 20:00 | 102 | 4 | Autumn | 20 | 8.75 | -8.8 | 4.06 | 42.4 | 0 | 0 | 0.02 | 0.02 | 8.8 | 50.45 | 15 | -40.26 | 10.17 | 3.708 | 0 | Diesel-backup
2025-04-12 21:00 | 102 | 4 | Autumn | 21 | 8.75 | -4.9 | 5.31 | 69.2 | 0 | 0 | 0.83 | 0.83 | 4.9 | 45 | 15 | 0 | 44.17 | 14.181 | 0 | Diesel-backup
2025-04-12 22:00 | 102 | 4 | Autumn | 22 | 8.75 | -11.7 | 7.46 | 86.1 | 0 | 0 | 8.69 | 8.69 | 11.7 | 49.19 | 15 | 0 | 40.5 | 13.193 | 0 | Diesel-backup
2025-04-12 23:00 | 102 | 4 | Autumn | 23 | 8.75 | -12.1 | 6.6 | 21.2 | 0 | 0 | 4.17 | 4.17 | 12.1 | 48.03 | 15 | 0 | 43.86 | 14.099 | 0 | Diesel-backup
2025-04-13 | 103 | 4 | Autumn | 0 | 8.59 | -9.9 | 7.46 | 64 | 0 | 0 | 8.69 | 8.69 | 9.9 | 53.17 | 15 | 0 | 44.48 | 14.263 | 0 | Diesel-backup
2025-04-13 01:00 | 103 | 4 | Autumn | 1 | 8.59 | -10.1 | 2.75 | 21.7 | 0 | 0 | 0 | 0 | 10.1 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-04-13 02:00 | 103 | 4 | Autumn | 2 | 8.59 | -13.5 | 17.57 | 82.5 | 0 | 0 | 120 | 120 | 13.5 | 52.38 | 39.88 | 67.62 | 0 | 0 | 0 | Normal
2025-04-13 03:00 | 103 | 4 | Autumn | 3 | 8.59 | -13.6 | 5.92 | 37.1 | 0 | 0 | 1.98 | 1.98 | 13.6 | 45 | 22.68 | -43.02 | 0 | 0 | 0 | Battery-supported
2025-04-13 04:00 | 103 | 4 | Autumn | 4 | 8.59 | -11.9 | 4.26 | 66.5 | 0 | 0 | 0.06 | 0.06 | 11.9 | 45 | 15 | -19.19 | 25.75 | 8.874 | 0 | Diesel-backup
2025-04-13 05:00 | 103 | 4 | Autumn | 5 | 8.59 | -15.2 | 7.59 | 37.7 | 0 | 0 | 9.58 | 9.58 | 15.2 | 45 | 15 | 0 | 35.42 | 11.769 | 0 | Diesel-backup
2025-04-13 06:00 | 103 | 4 | Autumn | 6 | 8.59 | -14.5 | 8.29 | 90 | 0 | 0 | 15.38 | 15.38 | 14.5 | 49.78 | 15 | 0 | 34.4 | 11.475 | 0 | Diesel-backup
2025-04-13 07:00 | 103 | 4 | Autumn | 7 | 8.59 | -13.6 | 21.86 | 67.6 | 0 | 0 | 120 | 120 | 13.6 | 49.69 | 40.87 | 70.31 | 0 | 0 | 0 | Normal
2025-04-13 08:00 | 103 | 4 | Autumn | 8 | 8.59 | -11.6 | 14.71 | 42.5 | 48.1 | 2.89 | 120 | 122.89 | 11.6 | 53.31 | 66.48 | 69.58 | 0 | 0 | 0 | Normal
2025-04-13 09:00 | 103 | 4 | Autumn | 9 | 8.59 | -15.1 | 6.54 | 0 | 299.2 | 17.95 | 3.93 | 21.88 | 15.1 | 49.36 | 55.49 | -27.48 | 0 | 0 | 0 | Battery-supported
2025-04-13 10:00 | 103 | 4 | Autumn | 10 | 8.59 | -17.7 | 19.72 | 39.3 | 344.1 | 20.65 | 120 | 140.65 | 17.7 | 58.57 | 85.69 | 82.08 | 0 | 0 | 0 | Normal
2025-04-13 11:00 | 103 | 4 | Autumn | 11 | 8.59 | -17.6 | 17.59 | 70.2 | 289.9 | 17.39 | 120 | 137.39 | 17.6 | 61.12 | 95 | 25.29 | 0 | 0 | 0 | Normal
2025-04-13 12:00 | 103 | 4 | Autumn | 12 | 8.59 | -15.8 | 4.29 | 38.1 | 468.3 | 28.1 | 0.07 | 28.17 | 15.8 | 55.14 | 84.21 | -26.97 | 0 | 0 | 0 | Battery-supported
2025-04-13 13:00 | 103 | 4 | Autumn | 13 | 8.59 | -15.6 | 24.68 | 65.8 | 310.4 | 18.62 | 120 | 138.62 | 15.6 | 58.49 | 95 | 29.32 | 0 | 0 | 0 | Normal
2025-04-13 14:00 | 103 | 4 | Autumn | 14 | 8.59 | -12.7 | 5.99 | 46 | 319.6 | 19.18 | 2.16 | 21.34 | 12.7 | 60.02 | 79.53 | -38.68 | 0 | 0 | 0 | Battery-supported
2025-04-13 15:00 | 103 | 4 | Autumn | 15 | 8.59 | -14.6 | 8.87 | 27.3 | 237.9 | 14.27 | 21.67 | 35.94 | 14.6 | 55.3 | 71.78 | -19.36 | 0 | 0 | 0 | Battery-supported
2025-04-13 16:00 | 103 | 4 | Autumn | 16 | 8.59 | -13.1 | 16.1 | 18 | 61.1 | 3.67 | 120 | 123.67 | 13.1 | 51.75 | 95 | 63.09 | 0 | 0 | 0 | Normal
2025-04-13 17:00 | 103 | 4 | Autumn | 17 | 8.59 | -13 | 2.34 | 44.1 | 0 | 0 | 0 | 0 | 13 | 55.68 | 72.73 | -55.68 | 0 | 0 | 0 | Battery-supported
2025-04-13 18:00 | 103 | 4 | Autumn | 18 | 8.59 | -12 | 7.46 | 86 | 0 | 0 | 8.69 | 8.69 | 12 | 62.26 | 51.3 | -53.57 | 0 | 0 | 0 | Battery-supported
2025-04-13 19:00 | 103 | 4 | Autumn | 19 | 8.59 | -8 | 9.68 | 14.3 | 0 | 0 | 33.04 | 33.04 | 8 | 53.02 | 43.31 | -19.98 | 0 | 0 | 0 | Battery-supported
2025-04-13 20:00 | 103 | 4 | Autumn | 20 | 8.59 | -9.4 | 14.41 | 41.9 | 0 | 0 | 120 | 120 | 9.4 | 46.36 | 70.41 | 73.64 | 0 | 0 | 0 | Normal
2025-04-13 21:00 | 103 | 4 | Autumn | 21 | 8.59 | -10.8 | 8.05 | 86.9 | 0 | 0 | 13.18 | 13.18 | 10.8 | 51.22 | 55.19 | -38.04 | 0 | 0 | 0 | Battery-supported
2025-04-13 22:00 | 103 | 4 | Autumn | 22 | 8.59 | -12 | 2.36 | 79.6 | 0 | 0 | 0 | 0 | 12 | 45.34 | 37.06 | -45.34 | 0 | 0 | 0 | Battery-supported
2025-04-13 23:00 | 103 | 4 | Autumn | 23 | 8.59 | -12.2 | 21.77 | 48.9 | 0 | 0 | 120 | 120 | 12.2 | 46.27 | 64.19 | 73.73 | 0 | 0 | 0 | Normal
2025-04-14 | 104 | 4 | Autumn | 0 | 8.43 | -11.1 | 8.25 | 94.2 | 0 | 0 | 15 | 15 | 11.1 | 45 | 52.19 | -30 | 0 | 0 | 0 | Battery-supported
2025-04-14 01:00 | 104 | 4 | Autumn | 1 | 8.43 | -10.9 | 9.94 | 64.7 | 0 | 0 | 37.38 | 37.38 | 10.9 | 46.49 | 48.54 | -9.11 | 0 | 0 | 0 | Battery-supported
2025-04-14 02:00 | 104 | 4 | Autumn | 2 | 8.43 | -14.5 | 2.99 | 60.6 | 0 | 0 | 0 | 0 | 14.5 | 45 | 30.54 | -45 | 0 | 0 | 0 | Battery-supported
2025-04-14 03:00 | 104 | 4 | Autumn | 3 | 8.43 | -12.8 | 17.22 | 72.6 | 0 | 0 | 120 | 120 | 12.8 | 45 | 58.14 | 75 | 0 | 0 | 0 | Normal
2025-04-14 04:00 | 104 | 4 | Autumn | 4 | 8.43 | -17.8 | 6.07 | 29 | 0 | 0 | 2.38 | 2.38 | 17.8 | 55.23 | 37 | -52.85 | 0 | 0 | 0 | Battery-supported
2025-04-14 05:00 | 104 | 4 | Autumn | 5 | 8.43 | -13.1 | 5.15 | 49.9 | 0 | 0 | 0.63 | 0.63 | 13.1 | 48.61 | 17.81 | -47.98 | 0 | 0 | 0 | Battery-supported
2025-04-14 06:00 | 104 | 4 | Autumn | 6 | 8.43 | -12.2 | 15.1 | 59.1 | 0 | 0 | 120 | 120 | 12.2 | 45 | 45.41 | 75 | 0 | 0 | 0 | Normal
2025-04-14 07:00 | 104 | 4 | Autumn | 7 | 8.43 | -14.6 | 3.23 | 54.7 | 0 | 0 | 0 | 0 | 14.6 | 48.82 | 25.88 | -48.82 | 0 | 0 | 0 | Battery-supported
2025-04-14 08:00 | 104 | 4 | Autumn | 8 | 8.43 | -10 | 10.02 | 42.2 | 35.7 | 2.14 | 38.79 | 40.93 | 10 | 55.79 | 19.94 | -14.86 | 0 | 0 | 0 | Battery-supported
2025-04-14 09:00 | 104 | 4 | Autumn | 9 | 8.43 | -15.9 | 5.05 | 27.4 | 227.9 | 13.67 | 0.52 | 14.19 | 15.9 | 60.43 | 15 | -12.35 | 33.89 | 11.327 | 0 | Diesel-backup
2025-04-14 10:00 | 104 | 4 | Autumn | 10 | 8.43 | -13.4 | 10.72 | 42.2 | 329.6 | 19.78 | 52.68 | 72.46 | 13.4 | 59.05 | 19.93 | 13.41 | 0 | 0 | 0 | Normal
2025-04-14 11:00 | 104 | 4 | Autumn | 11 | 8.43 | -13.7 | 12.37 | 88.3 | 206.2 | 12.37 | 97.67 | 110.04 | 13.7 | 51.95 | 41.31 | 58.09 | 0 | 0 | 0 | Normal
2025-04-14 12:00 | 104 | 4 | Autumn | 12 | 8.43 | -13.5 | 5.93 | 62 | 350.8 | 21.05 | 2.01 | 23.06 | 13.5 | 53.67 | 29.07 | -30.61 | 0 | 0 | 0 | Battery-supported
2025-04-14 13:00 | 104 | 4 | Autumn | 13 | 8.43 | -13.2 | 16.66 | 21.1 | 514.1 | 30.85 | 120 | 150.85 | 13.2 | 63.94 | 61.05 | 86.91 | 0 | 0 | 0 | Normal
2025-04-14 14:00 | 104 | 4 | Autumn | 14 | 8.43 | -12.3 | 8.26 | 54.7 | 284.1 | 17.05 | 15.09 | 32.14 | 12.3 | 53.71 | 52.42 | -21.57 | 0 | 0 | 0 | Battery-supported
2025-04-14 15:00 | 104 | 4 | Autumn | 15 | 8.43 | -10.3 | 22.03 | 37.3 | 206.6 | 12.4 | 120 | 132.4 | 10.3 | 51.46 | 82.21 | 80.94 | 0 | 0 | 0 | Normal
2025-04-14 16:00 | 104 | 4 | Autumn | 16 | 8.43 | -8.8 | 15.21 | 68.7 | 25.3 | 1.52 | 120 | 121.52 | 8.8 | 52.29 | 95 | 34.76 | 0 | 0 | 0 | Normal
2025-04-14 17:00 | 104 | 4 | Autumn | 17 | 8.43 | -11.5 | 8.82 | 41.9 | 0 | 0 | 21.07 | 21.07 | 11.5 | 55.38 | 81.28 | -34.31 | 0 | 0 | 0 | Battery-supported
2025-04-14 18:00 | 104 | 4 | Autumn | 18 | 8.43 | -9.4 | 8.78 | 39.4 | 0 | 0 | 20.6 | 20.6 | 9.4 | 48.41 | 70.15 | -27.81 | 0 | 0 | 0 | Battery-supported
2025-04-14 19:00 | 104 | 4 | Autumn | 19 | 8.43 | -12.6 | 3.46 | 73.8 | 0 | 0 | 0 | 0 | 12.6 | 45.64 | 51.9 | -45.64 | 0 | 0 | 0 | Battery-supported
2025-04-14 20:00 | 104 | 4 | Autumn | 20 | 8.43 | -9.4 | 15.09 | 28.9 | 0 | 0 | 120 | 120 | 9.4 | 51.11 | 77.25 | 68.89 | 0 | 0 | 0 | Normal
2025-04-14 21:00 | 104 | 4 | Autumn | 21 | 8.43 | -12.8 | 5.58 | 5.4 | 0 | 0 | 1.26 | 1.26 | 12.8 | 47.72 | 58.66 | -46.46 | 0 | 0 | 0 | Battery-supported
2025-04-14 22:00 | 104 | 4 | Autumn | 22 | 8.43 | -8.8 | 9.39 | 44.7 | 0 | 0 | 28.6 | 28.6 | 8.8 | 45 | 52.1 | -16.4 | 0 | 0 | 0 | Battery-supported
2025-04-14 23:00 | 104 | 4 | Autumn | 23 | 8.43 | -6.6 | 21.92 | 51.9 | 0 | 0 | 120 | 120 | 6.6 | 45 | 79.7 | 75 | 0 | 0 | 0 | Normal
2025-04-15 | 105 | 4 | Autumn | 0 | 8.26 | -12.3 | 16.55 | 41 | 0 | 0 | 120 | 120 | 12.3 | 48.64 | 95 | 41.57 | 0 | 0 | 0 | Normal
2025-04-15 01:00 | 105 | 4 | Autumn | 1 | 8.26 | -17.2 | 4.5 | 38.9 | 0 | 0 | 0.14 | 0.14 | 17.2 | 56.09 | 72.62 | -55.95 | 0 | 0 | 0 | Battery-supported
2025-04-15 02:00 | 105 | 4 | Autumn | 2 | 8.26 | -13.9 | 8.32 | 84.6 | 0 | 0 | 15.67 | 15.67 | 13.9 | 45 | 60.89 | -29.33 | 0 | 0 | 0 | Battery-supported
2025-04-15 03:00 | 105 | 4 | Autumn | 3 | 8.26 | -10.4 | 9.99 | 51.6 | 0 | 0 | 38.26 | 38.26 | 10.4 | 46.87 | 57.44 | -8.61 | 0 | 0 | 0 | Battery-supported
2025-04-15 04:00 | 105 | 4 | Autumn | 4 | 8.26 | -12.3 | 17.69 | 16.1 | 0 | 0 | 120 | 120 | 12.3 | 49.51 | 83.38 | 70.49 | 0 | 0 | 0 | Normal
2025-04-15 05:00 | 105 | 4 | Autumn | 5 | 8.26 | -13.3 | 16.24 | 58.7 | 0 | 0 | 120 | 120 | 13.3 | 54.21 | 95 | 31.56 | 0 | 0 | 0 | Normal
2025-04-15 06:00 | 105 | 4 | Autumn | 6 | 8.26 | -11.8 | 11.5 | 59 | 0 | 0 | 71.66 | 71.66 | 11.8 | 50.21 | 95 | 0 | 0 | 0 | 0 | Normal
2025-04-15 07:00 | 105 | 4 | Autumn | 7 | 8.26 | -13.1 | 10.88 | 67.7 | 0 | 0 | 56.26 | 56.26 | 13.1 | 52.32 | 95 | 0 | 0 | 0 | 0 | Normal
2025-04-15 08:00 | 105 | 4 | Autumn | 8 | 8.26 | -11.6 | 8.23 | 37.9 | 23.5 | 1.41 | 14.81 | 16.22 | 11.6 | 55.21 | 79.4 | -38.99 | 0 | 0 | 0 | Battery-supported
2025-04-15 09:00 | 105 | 4 | Autumn | 9 | 8.26 | -12.2 | 9.82 | 48.7 | 173.6 | 10.42 | 35.33 | 45.75 | 12.2 | 53.39 | 76.35 | -7.64 | 0 | 0 | 0 | Battery-supported
2025-04-15 10:00 | 105 | 4 | Autumn | 10 | 8.26 | -10.7 | 7.1 | 28.2 | 374.9 | 22.49 | 6.53 | 29.02 | 10.7 | 58.78 | 64.44 | -29.76 | 0 | 0 | 0 | Battery-supported
2025-04-15 11:00 | 105 | 4 | Autumn | 11 | 8.26 | -13 | 13.09 | 83.2 | 229.1 | 13.75 | 120 | 133.75 | 13 | 50.92 | 94.93 | 82.83 | 0 | 0 | 0 | Normal
2025-04-15 12:00 | 105 | 4 | Autumn | 12 | 8.26 | -11.5 | 11.21 | 80.8 | 258.6 | 15.52 | 64.15 | 79.67 | 11.5 | 60.6 | 95 | 0.2 | 0 | 0 | 0 | Normal
2025-04-15 13:00 | 105 | 4 | Autumn | 13 | 8.26 | -13.8 | 14.84 | 67.5 | 300.7 | 18.04 | 120 | 138.04 | 13.8 | 59.97 | 95 | 0 | 0 | 0 | 0 | Normal
2025-04-15 14:00 | 105 | 4 | Autumn | 14 | 8.26 | -14.1 | 14.6 | 49.2 | 299.9 | 17.99 | 120 | 137.99 | 14.1 | 55.75 | 95 | 0 | 0 | 0 | 0 | Normal
2025-04-15 15:00 | 105 | 4 | Autumn | 15 | 8.26 | -8.6 | 5.58 | 3.4 | 266.5 | 15.99 | 1.26 | 17.25 | 8.6 | 45.24 | 83.8 | -27.99 | 0 | 0 | 0 | Battery-supported
2025-04-15 16:00 | 105 | 4 | Autumn | 16 | 8.26 | -11.5 | 1.56 | 60.3 | 18 | 1.08 | 0 | 1.08 | 11.5 | 54.22 | 62.55 | -53.14 | 0 | 0 | 0 | Battery-supported
2025-04-15 17:00 | 105 | 4 | Autumn | 17 | 8.26 | -9.9 | 5.31 | 68.8 | 0 | 0 | 0.83 | 0.83 | 9.9 | 50.36 | 42.74 | -49.53 | 0 | 0 | 0 | Battery-supported
2025-04-15 18:00 | 105 | 4 | Autumn | 18 | 8.26 | -11.2 | 9.78 | 61.9 | 0 | 0 | 34.66 | 34.66 | 11.2 | 47.87 | 37.45 | -13.21 | 0 | 0 | 0 | Battery-supported
2025-04-15 19:00 | 105 | 4 | Autumn | 19 | 8.26 | -12.6 | 7.11 | 69.1 | 0 | 0 | 6.58 | 6.58 | 12.6 | 53.31 | 18.76 | -46.73 | 0 | 0 | 0 | Battery-supported
2025-04-15 20:00 | 105 | 4 | Autumn | 20 | 8.26 | -11.2 | 6.93 | 40 | 0 | 0 | 5.65 | 5.65 | 11.2 | 57.81 | 15 | -9.4 | 42.76 | 13.806 | 0 | Diesel-backup
2025-04-15 21:00 | 105 | 4 | Autumn | 21 | 8.26 | -8.1 | 5.1 | 88.6 | 0 | 0 | 0.57 | 0.57 | 8.1 | 45 | 15 | 0 | 44.43 | 14.25 | 0 | Diesel-backup
2025-04-15 22:00 | 105 | 4 | Autumn | 22 | 8.26 | -10.2 | 10.59 | 66.9 | 0 | 0 | 49.88 | 49.88 | 10.2 | 45 | 16.8 | 4.88 | 0 | 0 | 0 | Normal
2025-04-15 23:00 | 105 | 4 | Autumn | 23 | 8.26 | -15.4 | 2.43 | 70.5 | 0 | 0 | 0 | 0 | 15.4 | 45 | 15 | -4.49 | 40.51 | 13.196 | 0 | Diesel-backup
2025-04-16 | 106 | 4 | Autumn | 0 | 8.1 | -12.7 | 11.49 | 56.2 | 0 | 0 | 71.39 | 71.39 | 12.7 | 46.97 | 23.99 | 24.42 | 0 | 0 | 0 | Normal
2025-04-16 01:00 | 106 | 4 | Autumn | 1 | 8.1 | -8.6 | 11.62 | 79.5 | 0 | 0 | 74.93 | 74.93 | 8.6 | 49.89 | 33.2 | 25.04 | 0 | 0 | 0 | Normal
2025-04-16 02:00 | 106 | 4 | Autumn | 2 | 8.1 | -13.4 | 14.71 | 12.2 | 0 | 0 | 120 | 120 | 13.4 | 48.55 | 59.49 | 71.45 | 0 | 0 | 0 | Normal
2025-04-16 03:00 | 106 | 4 | Autumn | 3 | 8.1 | -17.3 | 36.73 | 53 | 0 | 0 | 0 | 0 | 17.3 | 50.85 | 39.15 | -50.85 | 0 | 0 | 0 | Battery-supported
2025-04-16 04:00 | 106 | 4 | Autumn | 4 | 8.1 | -9.5 | 1.42 | 71.7 | 0 | 0 | 0 | 0 | 9.5 | 47.49 | 20.16 | -47.49 | 0 | 0 | 0 | Battery-supported
2025-04-16 05:00 | 106 | 4 | Autumn | 5 | 8.1 | -12.5 | 11.32 | 0.3 | 0 | 0 | 66.93 | 66.93 | 12.5 | 52.56 | 25.45 | 14.37 | 0 | 0 | 0 | Normal
2025-04-16 06:00 | 106 | 4 | Autumn | 6 | 8.1 | -14.4 | 12.62 | 67.6 | 0 | 0 | 106.17 | 106.17 | 14.4 | 54.92 | 44.31 | 51.25 | 0 | 0 | 0 | Normal
2025-04-16 07:00 | 106 | 4 | Autumn | 7 | 8.1 | -15.2 | 5.34 | 59 | 0 | 0 | 0.87 | 0.87 | 15.2 | 51.58 | 24.02 | -50.71 | 0 | 0 | 0 | Battery-supported
2025-04-16 08:00 | 106 | 4 | Autumn | 8 | 8.1 | -12.1 | 7.44 | 45.2 | 8.3 | 0.5 | 8.56 | 9.06 | 12.1 | 48.53 | 15 | -22.56 | 16.91 | 6.02 | 0 | Diesel-backup
2025-04-16 09:00 | 106 | 4 | Autumn | 9 | 8.1 | -15.6 | 6.16 | 42.3 | 177.2 | 10.63 | 2.63 | 13.26 | 15.6 | 62.57 | 15 | 0 | 49.31 | 15.779 | 0 | Diesel-backup
2025-04-16 10:00 | 106 | 4 | Autumn | 10 | 8.1 | -11.7 | 11.74 | 7.9 | 440.6 | 26.44 | 78.31 | 104.75 | 11.7 | 53.13 | 34 | 51.62 | 0 | 0 | 0 | Normal
2025-04-16 11:00 | 106 | 4 | Autumn | 11 | 8.1 | -12.8 | 15.62 | 29.1 | 474.7 | 28.48 | 120 | 148.48 | 12.8 | 53.69 | 68.88 | 94.79 | 0 | 0 | 0 | Normal
2025-04-16 12:00 | 106 | 4 | Autumn | 12 | 8.1 | -13.2 | 3.82 | 30.1 | 508.1 | 30.49 | 0 | 30.49 | 13.2 | 52.3 | 60.15 | -21.81 | 0 | 0 | 0 | Battery-supported
2025-04-16 13:00 | 106 | 4 | Autumn | 13 | 8.1 | -13 | 10.7 | 62.7 | 321.8 | 19.31 | 52.24 | 71.55 | 13 | 58.17 | 65.08 | 13.38 | 0 | 0 | 0 | Normal
2025-04-16 14:00 | 106 | 4 | Autumn | 14 | 8.1 | -13.3 | 17.46 | 37.1 | 338.1 | 20.29 | 120 | 140.29 | 13.3 | 60.13 | 94.58 | 80.16 | 0 | 0 | 0 | Normal
2025-04-16 15:00 | 106 | 4 | Autumn | 15 | 8.1 | -10.3 | 5.59 | 51.2 | 160 | 9.6 | 1.28 | 10.88 | 10.3 | 50.63 | 78.68 | -39.75 | 0 | 0 | 0 | Battery-supported
2025-04-16 16:00 | 106 | 4 | Autumn | 16 | 8.1 | -14.1 | 1.14 | 63.7 | 6.5 | 0.39 | 0 | 0.39 | 14.1 | 59.67 | 54.97 | -59.28 | 0 | 0 | 0 | Battery-supported
2025-04-16 17:00 | 106 | 4 | Autumn | 17 | 8.1 | -15.5 | 4.74 | 51.1 | 0 | 0 | 0.27 | 0.27 | 15.5 | 62.9 | 29.91 | -62.63 | 0 | 0 | 0 | Battery-supported
2025-04-16 18:00 | 106 | 4 | Autumn | 18 | 8.1 | -10.3 | 4.38 | 23.8 | 0 | 0 | 0.1 | 0.1 | 10.3 | 54.76 | 15 | -37.28 | 17.38 | 6.175 | 0 | Diesel-backup
2025-04-16 19:00 | 106 | 4 | Autumn | 19 | 8.1 | -10.1 | 4.91 | 52.1 | 0 | 0 | 0.39 | 0.39 | 10.1 | 53.1 | 15 | 0 | 52.71 | 16.867 | 0 | Diesel-backup
2025-04-16 20:00 | 106 | 4 | Autumn | 20 | 8.1 | -10.4 | 21.86 | 35.7 | 0 | 0 | 120 | 120 | 10.4 | 52.79 | 39.73 | 67.21 | 0 | 0 | 0 | Normal
2025-04-16 21:00 | 106 | 4 | Autumn | 21 | 8.1 | -10.6 | 24.71 | 66.5 | 0 | 0 | 120 | 120 | 10.6 | 45 | 67.33 | 75 | 0 | 0 | 0 | Normal
2025-04-16 22:00 | 106 | 4 | Autumn | 22 | 8.1 | -12.4 | 18.73 | 76.2 | 0 | 0 | 120 | 120 | 12.4 | 50.44 | 92.93 | 69.56 | 0 | 0 | 0 | Normal
2025-04-16 23:00 | 106 | 4 | Autumn | 23 | 8.1 | -10.2 | 7.04 | 90.9 | 0 | 0 | 6.21 | 6.21 | 10.2 | 49.76 | 75.51 | -43.55 | 0 | 0 | 0 | Battery-supported
2025-04-17 | 107 | 4 | Autumn | 0 | 7.93 | -12.5 | 19.21 | 93.8 | 7.8 | 0.47 | 120 | 120.47 | 12.5 | 48.03 | 95 | 52.96 | 0 | 0 | 0 | Normal
2025-04-17 01:00 | 107 | 4 | Autumn | 1 | 7.93 | -13.8 | 1.6 | 34.9 | 0 | 0 | 0 | 0 | 13.8 | 47.02 | 76.19 | -47.02 | 0 | 0 | 0 | Battery-supported
2025-04-17 02:00 | 107 | 4 | Autumn | 2 | 7.93 | -13.8 | 4.23 | 19.2 | 0 | 0 | 0.05 | 0.05 | 13.8 | 50.77 | 55.9 | -50.72 | 0 | 0 | 0 | Battery-supported
2025-04-17 03:00 | 107 | 4 | Autumn | 3 | 7.93 | -9.1 | 13.36 | 93.7 | 0 | 0 | 120 | 120 | 9.1 | 45 | 83.5 | 75 | 0 | 0 | 0 | Normal
2025-04-17 04:00 | 107 | 4 | Autumn | 4 | 7.93 | -17.7 | 5.93 | 15.4 | 0 | 0 | 2.01 | 2.01 | 17.7 | 57.73 | 61.22 | -55.72 | 0 | 0 | 0 | Battery-supported
2025-04-17 05:00 | 107 | 4 | Autumn | 5 | 7.93 | -13.1 | 3.86 | 72.9 | 0 | 0 | 0.01 | 0.01 | 13.1 | 52.67 | 40.15 | -52.66 | 0 | 0 | 0 | Battery-supported
2025-04-17 06:00 | 107 | 4 | Autumn | 6 | 7.93 | -18.1 | 10.55 | 39.3 | 0 | 0 | 49.04 | 49.04 | 18.1 | 55.09 | 37.73 | -6.05 | 0 | 0 | 0 | Battery-supported
2025-04-17 07:00 | 107 | 4 | Autumn | 7 | 7.93 | -14.8 | 10.7 | 45.6 | 0 | 0 | 52.24 | 52.24 | 14.8 | 48.09 | 39.26 | 4.15 | 0 | 0 | 0 | Normal
2025-04-17 08:00 | 107 | 4 | Autumn | 8 | 7.93 | -15.6 | 11.32 | 8.2 | 0 | 0 | 66.93 | 66.93 | 15.6 | 57.83 | 42.61 | 9.1 | 0 | 0 | 0 | Normal
2025-04-17 09:00 | 107 | 4 | Autumn | 9 | 7.93 | -19.2 | 12.07 | 62.9 | 129.4 | 6.6 | 88.1 | 94.7 | 19.2 | 55.24 | 57.13 | 39.46 | 0 | 0 | 0 | Normal
2025-04-17 10:00 | 107 | 4 | Autumn | 10 | 7.93 | -13.6 | 10.24 | 9.4 | 428.3 | 25.7 | 42.85 | 68.55 | 13.6 | 53.54 | 62.65 | 15.01 | 0 | 0 | 0 | Normal
2025-04-17 11:00 | 107 | 4 | Autumn | 11 | 7.93 | -15.1 | 7.91 | 61.1 | 327.8 | 19.67 | 12 | 31.67 | 15.1 | 61.04 | 50.9 | -29.37 | 0 | 0 | 0 | Battery-supported
2025-04-17 12:00 | 107 | 4 | Autumn | 12 | 7.93 | -18.5 | 8.81 | 46.5 | 427.1 | 21.78 | 20.96 | 42.74 | 18.5 | 58.41 | 44.64 | -15.67 | 0 | 0 | 0 | Battery-supported
2025-04-17 13:00 | 107 | 4 | Autumn | 13 | 7.93 | -11.7 | 13.47 | 35.4 | 444.4 | 26.66 | 120 | 146.66 | 11.7 | 64.25 | 74.96 | 82.41 | 0 | 0 | 0 | Normal
2025-04-17 14:00 | 107 | 4 | Autumn | 14 | 7.93 | -10 | 10.02 | 44 | 308.7 | 18.52 | 38.79 | 57.31 | 10 | 51.01 | 77.28 | 6.3 | 0 | 0 | 0 | Normal
2025-04-17 15:00 | 107 | 4 | Autumn | 15 | 7.93 | -9.5 | 6.35 | 53.5 | 146.7 | 8.8 | 3.24 | 12.04 | 9.5 | 48.79 | 62.58 | -36.75 | 0 | 0 | 0 | Battery-supported
2025-04-17 16:00 | 107 | 4 | Autumn | 16 | 7.93 | -11.6 | 5.3 | 74.1 | 0 | 0 | 0.82 | 0.82 | 11.6 | 55.95 | 40.53 | -55.13 | 0 | 0 | 0 | Battery-supported
2025-04-17 17:00 | 107 | 4 | Autumn | 17 | 7.93 | -12 | 8.77 | 43.6 | 0 | 0 | 20.49 | 20.49 | 12 | 56.53 | 26.11 | -36.04 | 0 | 0 | 0 | Battery-supported
2025-04-17 18:00 | 107 | 4 | Autumn | 18 | 7.93 | -8.9 | 17.47 | 76.5 | 0 | 0 | 120 | 120 | 8.9 | 57.36 | 49.17 | 62.64 | 0 | 0 | 0 | Normal
2025-04-17 19:00 | 107 | 4 | Autumn | 19 | 7.93 | -8 | 12.18 | 53 | 0 | 0 | 91.53 | 91.53 | 8 | 49.97 | 64.46 | 41.56 | 0 | 0 | 0 | Normal
2025-04-17 20:00 | 107 | 4 | Autumn | 20 | 7.93 | -9.2 | 18 | 36.7 | 0 | 0 | 120 | 120 | 9.2 | 48.65 | 90.72 | 71.35 | 0 | 0 | 0 | Normal
2025-04-17 21:00 | 107 | 4 | Autumn | 21 | 7.93 | -13.8 | 6.99 | 57.7 | 0 | 0 | 5.95 | 5.95 | 13.8 | 46.47 | 74.51 | -40.52 | 0 | 0 | 0 | Battery-supported
2025-04-17 22:00 | 107 | 4 | Autumn | 22 | 7.93 | -11.4 | 9.58 | 17.9 | 0 | 0 | 31.46 | 31.46 | 11.4 | 51.21 | 66.61 | -19.75 | 0 | 0 | 0 | Battery-supported
2025-04-17 23:00 | 107 | 4 | Autumn | 23 | 7.93 | -11.1 | 10.44 | 36.8 | 0 | 0 | 46.78 | 46.78 | 11.1 | 52.66 | 64.26 | -5.88 | 0 | 0 | 0 | Battery-supported
2025-04-18 | 108 | 4 | Autumn | 0 | 7.76 | -16.6 | 13.88 | 50.6 | 57.9 | 3.47 | 120 | 123.47 | 16.6 | 49.21 | 91.58 | 74.26 | 0 | 0 | 0 | Normal
2025-04-18 01:00 | 108 | 4 | Autumn | 1 | 7.76 | -11.9 | 7.02 | 19.6 | 0 | 0 | 6.1 | 6.1 | 11.9 | 46.3 | 75.5 | -40.2 | 0 | 0 | 0 | Battery-supported
2025-04-18 02:00 | 108 | 4 | Autumn | 2 | 7.76 | -8.4 | 12.2 | 30.1 | 0 | 0 | 92.17 | 92.17 | 8.4 | 48.93 | 91.42 | 43.24 | 0 | 0 | 0 | Normal
2025-04-18 03:00 | 108 | 4 | Autumn | 3 | 7.76 | -12.3 | 16.98 | 81.2 | 0 | 0 | 120 | 120 | 12.3 | 50.24 | 95 | 9.74 | 0 | 0 | 0 | Normal
2025-04-18 04:00 | 108 | 4 | Autumn | 4 | 7.76 | -10.9 | 8.2 | 84.8 | 0 | 0 | 14.53 | 14.53 | 10.9 | 45 | 82.81 | -30.47 | 0 | 0 | 0 | Battery-supported
2025-04-18 05:00 | 108 | 4 | Autumn | 5 | 7.76 | -14 | 4.89 | 33.9 | 0 | 0 | 0.38 | 0.38 | 14 | 45 | 64.96 | -44.62 | 0 | 0 | 0 | Battery-supported
2025-04-18 06:00 | 108 | 4 | Autumn | 6 | 7.76 | -14.8 | 17.3 | 83.9 | 0 | 0 | 120 | 120 | 14.8 | 47.09 | 91.79 | 72.91 | 0 | 0 | 0 | Normal
2025-04-18 07:00 | 108 | 4 | Autumn | 7 | 7.76 | -14 | 12.85 | 68.8 | 0 | 0 | 114.41 | 114.41 | 14 | 52.29 | 95 | 8.71 | 0 | 0 | 0 | Normal
2025-04-18 08:00 | 108 | 4 | Autumn | 8 | 7.76 | -16.7 | 3.27 | 59.2 | 0 | 0 | 0 | 0 | 16.7 | 53.62 | 73.55 | -53.62 | 0 | 0 | 0 | Battery-supported
2025-04-18 09:00 | 108 | 4 | Autumn | 9 | 7.76 | -16.9 | 8.32 | 19.8 | 195.3 | 11.72 | 15.67 | 27.39 | 16.9 | 60.61 | 60.26 | -33.22 | 0 | 0 | 0 | Battery-supported
2025-04-18 10:00 | 108 | 4 | Autumn | 10 | 7.76 | -11.9 | 22.77 | 27.4 | 359.8 | 21.59 | 120 | 141.59 | 11.9 | 53.33 | 92.74 | 88.26 | 0 | 0 | 0 | Normal
2025-04-18 11:00 | 108 | 4 | Autumn | 11 | 7.76 | -11.4 | 11.64 | 48.8 | 382.5 | 22.95 | 75.49 | 98.44 | 11.4 | 51.36 | 95 | 6.13 | 0 | 0 | 0 | Normal
2025-04-18 12:00 | 108 | 4 | Autumn | 12 | 7.76 | -16.3 | 8.79 | 17.5 | 569.7 | 34.18 | 20.72 | 54.9 | 16.3 | 57.24 | 94.06 | -2.34 | 0 | 0 | 0 | Battery-supported
2025-04-18 13:00 | 108 | 4 | Autumn | 13 | 7.76 | -11.6 | 4.48 | 53 | 363.2 | 21.79 | 0.13 | 21.92 | 11.6 | 57.99 | 79.64 | -36.07 | 0 | 0 | 0 | Battery-supported
2025-04-18 14:00 | 108 | 4 | Autumn | 14 | 7.76 | -13.6 | 4.48 | 26.6 | 362.2 | 21.73 | 0.13 | 21.86 | 13.6 | 58.62 | 64.93 | -36.76 | 0 | 0 | 0 | Battery-supported
2025-04-18 15:00 | 108 | 4 | Autumn | 15 | 7.76 | -12.2 | 13.39 | 78.4 | 94.5 | 5.67 | 120 | 125.67 | 12.2 | 59.23 | 89.38 | 66.44 | 0 | 0 | 0 | Normal
2025-04-18 16:00 | 108 | 4 | Autumn | 16 | 7.76 | -11.6 | 4.75 | 61.3 | 0 | 0 | 0.27 | 0.27 | 11.6 | 51.24 | 68.99 | -50.97 | 0 | 0 | 0 | Battery-supported
2025-04-18 17:00 | 108 | 4 | Autumn | 17 | 7.76 | -10.1 | 10.52 | 72.6 | 0 | 0 | 48.42 | 48.42 | 10.1 | 46.28 | 69.78 | 2.14 | 0 | 0 | 0 | Normal
2025-04-18 18:00 | 108 | 4 | Autumn | 18 | 7.76 | -11.9 | 8.19 | 28.6 | 0 | 0 | 14.44 | 14.44 | 11.9 | 55.53 | 53.35 | -41.09 | 0 | 0 | 0 | Battery-supported
2025-04-18 19:00 | 108 | 4 | Autumn | 19 | 7.76 | -8.8 | 10.16 | 71.7 | 0 | 0 | 41.35 | 41.35 | 8.8 | 51.64 | 49.23 | -10.29 | 0 | 0 | 0 | Battery-supported
2025-04-18 20:00 | 108 | 4 | Autumn | 20 | 7.76 | -11.2 | 7.77 | 83 | 0 | 0 | 10.9 | 10.9 | 11.2 | 52.13 | 32.74 | -41.23 | 0 | 0 | 0 | Battery-supported
2025-04-18 21:00 | 108 | 4 | Autumn | 21 | 7.76 | -10.5 | 11.34 | 58.1 | 0 | 0 | 67.45 | 67.45 | 10.5 | 45 | 41 | 22.45 | 0 | 0 | 0 | Normal
2025-04-18 22:00 | 108 | 4 | Autumn | 22 | 7.76 | -13.9 | 14.76 | 55.6 | 0 | 0 | 120 | 120 | 13.9 | 52.24 | 65.93 | 67.76 | 0 | 0 | 0 | Normal
2025-04-18 23:00 | 108 | 4 | Autumn | 23 | 7.76 | -7.6 | 7.85 | 59.9 | 0 | 0 | 11.52 | 11.52 | 7.6 | 45 | 52.54 | -33.48 | 0 | 0 | 0 | Battery-supported
2025-04-19 | 109 | 4 | Autumn | 0 | 7.6 | -11.8 | 14.09 | 66.5 | 81.5 | 4.89 | 120 | 124.89 | 11.8 | 49.54 | 80.27 | 75.35 | 0 | 0 | 0 | Normal
2025-04-19 01:00 | 109 | 4 | Autumn | 1 | 7.6 | -11.6 | 18.58 | 56.3 | 0 | 0 | 120 | 120 | 11.6 | 49.15 | 95 | 40.02 | 0 | 0 | 0 | Normal
2025-04-19 02:00 | 109 | 4 | Autumn | 2 | 7.6 | -17.1 | 10.51 | 28 | 0 | 0 | 48.21 | 48.21 | 17.1 | 54.4 | 92.52 | -6.19 | 0 | 0 | 0 | Battery-supported
2025-04-19 03:00 | 109 | 4 | Autumn | 3 | 7.6 | -15.8 | 13.25 | 19.9 | 0 | 0 | 120 | 120 | 15.8 | 50.42 | 95 | 6.73 | 0 | 0 | 0 | Normal
2025-04-19 04:00 | 109 | 4 | Autumn | 4 | 7.6 | -11.6 | 3.89 | 32.7 | 0 | 0 | 0.01 | 0.01 | 11.6 | 45 | 77 | -44.99 | 0 | 0 | 0 | Battery-supported
2025-04-19 05:00 | 109 | 4 | Autumn | 5 | 7.6 | -14 | 7.98 | 5.4 | 0 | 0 | 12.58 | 12.58 | 14 | 45 | 64.04 | -32.42 | 0 | 0 | 0 | Battery-supported
2025-04-19 06:00 | 109 | 4 | Autumn | 6 | 7.6 | -19.1 | 3.01 | 79.6 | 0 | 0 | 0 | 0 | 19.1 | 50.64 | 43.78 | -50.64 | 0 | 0 | 0 | Battery-supported
2025-04-19 07:00 | 109 | 4 | Autumn | 7 | 7.6 | -12.7 | 6.31 | 8.5 | 0 | 0 | 3.11 | 3.11 | 12.7 | 54.98 | 23.03 | -51.87 | 0 | 0 | 0 | Battery-supported
2025-04-19 08:00 | 109 | 4 | Autumn | 8 | 7.6 | -16.3 | 8.04 | 66.4 | 0 | 0 | 13.1 | 13.1 | 16.3 | 63 | 15 | -20.08 | 29.82 | 10.122 | 0 | Diesel-backup
2025-04-19 09:00 | 109 | 4 | Autumn | 9 | 7.6 | -11.9 | 23.95 | 77.4 | 89.2 | 5.35 | 120 | 125.35 | 11.9 | 54.06 | 41.23 | 71.29 | 0 | 0 | 0 | Normal
2025-04-19 10:00 | 109 | 4 | Autumn | 10 | 7.6 | -15.1 | 5.38 | 77.3 | 186.5 | 11.19 | 0.93 | 12.12 | 15.1 | 55.53 | 23.87 | -43.41 | 0 | 0 | 0 | Battery-supported
2025-04-19 11:00 | 109 | 4 | Autumn | 11 | 7.6 | -14.2 | 8.58 | 41.3 | 414.8 | 24.89 | 18.35 | 43.24 | 14.2 | 57.61 | 18.12 | -14.37 | 0 | 0 | 0 | Battery-supported
2025-04-19 12:00 | 109 | 4 | Autumn | 12 | 7.6 | -11.7 | 4.77 | 22.9 | 543.2 | 32.59 | 0.29 | 32.88 | 11.7 | 57.97 | 15 | -7.81 | 17.28 | 6.144 | 0 | Diesel-backup
2025-04-19 13:00 | 109 | 4 | Autumn | 13 | 7.6 | -15.9 | 7.63 | 84.8 | 218.4 | 13.1 | 9.86 | 22.96 | 15.9 | 59.98 | 15 | 0 | 37.02 | 12.225 | 0 | Diesel-backup
2025-04-19 14:00 | 109 | 4 | Autumn | 14 | 7.6 | -15.8 | 11.49 | 62 | 237.6 | 14.26 | 71.39 | 85.65 | 15.8 | 53.12 | 26.97 | 32.53 | 0 | 0 | 0 | Normal
2025-04-19 15:00 | 109 | 4 | Autumn | 15 | 7.6 | -13.6 | 12.56 | 75 | 93 | 5.58 | 104.09 | 109.67 | 13.6 | 62.22 | 44.43 | 47.45 | 0 | 0 | 0 | Normal
2025-04-19 16:00 | 109 | 4 | Autumn | 16 | 7.6 | -11 | 7.03 | 10.8 | 0 | 0 | 6.16 | 6.16 | 11 | 55.81 | 24.57 | -49.65 | 0 | 0 | 0 | Battery-supported
2025-04-19 17:00 | 109 | 4 | Autumn | 17 | 7.6 | -15.4 | 5.89 | 26.6 | 0 | 0 | 1.91 | 1.91 | 15.4 | 56.26 | 15 | -23.93 | 30.42 | 10.302 | 0 | Diesel-backup
2025-04-19 18:00 | 109 | 4 | Autumn | 18 | 7.6 | -15.9 | 0.93 | 41.6 | 0 | 0 | 0 | 0 | 15.9 | 60.19 | 15 | 0 | 60.19 | 19.261 | 0 | Diesel-backup
2025-04-19 19:00 | 109 | 4 | Autumn | 19 | 7.6 | -10.3 | 19.93 | 31 | 0 | 0 | 120 | 120 | 10.3 | 58.04 | 37.8 | 61.96 | 0 | 0 | 0 | Normal
2025-04-19 20:00 | 109 | 4 | Autumn | 20 | 7.6 | -13.4 | 6.71 | 77.6 | 0 | 0 | 4.63 | 4.63 | 13.4 | 57.82 | 16.53 | -53.19 | 0 | 0 | 0 | Battery-supported
2025-04-19 21:00 | 109 | 4 | Autumn | 21 | 7.6 | -13 | 1.85 | 82.6 | 0 | 0 | 0 | 0 | 13 | 49.65 | 15 | -3.81 | 45.84 | 14.668 | 0 | Diesel-backup
2025-04-19 22:00 | 109 | 4 | Autumn | 22 | 7.6 | -16.4 | 17.09 | 40.9 | 0 | 0 | 120 | 120 | 16.4 | 57.42 | 38.03 | 62.58 | 0 | 0 | 0 | Normal
2025-04-19 23:00 | 109 | 4 | Autumn | 23 | 7.6 | -14 | 2.22 | 38.1 | 0 | 0 | 0 | 0 | 14 | 46.39 | 19.47 | -46.39 | 0 | 0 | 0 | Battery-supported
2025-04-20 | 110 | 4 | Autumn | 0 | 7.43 | -13 | 17.17 | 80.4 | 92.7 | 5.56 | 120 | 125.56 | 13 | 45 | 49.12 | 80.56 | 0 | 0 | 0 | Normal
2025-04-20 01:00 | 110 | 4 | Autumn | 1 | 7.43 | -11.3 | 3.07 | 29.4 | 0 | 0 | 0 | 0 | 11.3 | 45 | 31.12 | -45 | 0 | 0 | 0 | Battery-supported
2025-04-20 02:00 | 110 | 4 | Autumn | 2 | 7.43 | -15.5 | 3.53 | 83.2 | 0 | 0 | 0 | 0 | 15.5 | 53.87 | 15 | -40.3 | 13.57 | 4.889 | 0 | Diesel-backup
2025-04-20 03:00 | 110 | 4 | Autumn | 3 | 7.43 | -10.5 | 4.19 | 89 | 0 | 0 | 0.05 | 0.05 | 10.5 | 49.33 | 15 | 0 | 49.28 | 15.77 | 0 | Diesel-backup
2025-04-20 04:00 | 110 | 4 | Autumn | 4 | 7.43 | -16 | 6.4 | 27.3 | 0 | 0 | 3.41 | 3.41 | 16 | 51.65 | 15 | 0 | 48.24 | 15.437 | 0 | Diesel-backup
2025-04-20 05:00 | 110 | 4 | Autumn | 5 | 7.43 | -16.3 | 17.26 | 20.5 | 0 | 0 | 120 | 120 | 16.3 | 47.91 | 41.53 | 72.09 | 0 | 0 | 0 | Normal
2025-04-20 06:00 | 110 | 4 | Autumn | 6 | 7.43 | -11.7 | 4.28 | 1.3 | 0 | 0 | 0.07 | 0.07 | 11.7 | 53.82 | 20.03 | -53.75 | 0 | 0 | 0 | Battery-supported
2025-04-20 07:00 | 110 | 4 | Autumn | 7 | 7.43 | -14.8 | 11.51 | 88.7 | 0 | 0 | 71.93 | 71.93 | 14.8 | 45.15 | 29.88 | 26.78 | 0 | 0 | 0 | Normal
2025-04-20 08:00 | 110 | 4 | Autumn | 8 | 7.43 | -16.5 | 10.09 | 20.9 | 0 | 0 | 40.06 | 40.06 | 16.5 | 57.67 | 22.84 | -17.61 | 0 | 0 | 0 | Battery-supported
2025-04-20 09:00 | 110 | 4 | Autumn | 9 | 7.43 | -15.6 | 9.08 | 40.6 | 135.6 | 8.14 | 24.32 | 32.46 | 15.6 | 55.78 | 15 | -19.6 | 3.72 | 1.387 | 0 | Diesel-backup
2025-04-20 10:00 | 110 | 4 | Autumn | 10 | 7.43 | -12.1 | 15.48 | 59.2 | 241.9 | 14.51 | 120 | 134.51 | 12.1 | 59.34 | 42.66 | 75.17 | 0 | 0 | 0 | Normal
2025-04-20 11:00 | 110 | 4 | Autumn | 11 | 7.43 | -11.6 | 9.54 | 17.1 | 521.5 | 31.29 | 30.84 | 62.13 | 11.6 | 53.89 | 45.69 | 8.24 | 0 | 0 | 0 | Normal
2025-04-20 12:00 | 110 | 4 | Autumn | 12 | 7.43 | -16.3 | 9.97 | 79.1 | 266.8 | 16.01 | 37.91 | 53.92 | 16.3 | 65.88 | 40.91 | -11.96 | 0 | 0 | 0 | Battery-supported
2025-04-20 13:00 | 110 | 4 | Autumn | 13 | 7.43 | -14.3 | 13.23 | 54.9 | 352 | 21.12 | 120 | 141.12 | 14.3 | 60.5 | 70.58 | 80.62 | 0 | 0 | 0 | Normal
2025-04-20 14:00 | 110 | 4 | Autumn | 14 | 7.43 | -13.6 | 6.54 | 44.1 | 290.9 | 17.45 | 3.93 | 21.38 | 13.6 | 52.88 | 57.98 | -31.5 | 0 | 0 | 0 | Battery-supported
2025-04-20 15:00 | 110 | 4 | Autumn | 15 | 7.43 | -15.6 | 8.66 | 27.7 | 154.4 | 9.26 | 19.23 | 28.49 | 15.6 | 57.33 | 46.44 | -28.84 | 0 | 0 | 0 | Battery-supported
2025-04-20 16:00 | 110 | 4 | Autumn | 16 | 7.43 | -13.1 | 10.54 | 57.7 | 0 | 0 | 48.83 | 48.83 | 13.1 | 53.96 | 44.39 | -5.13 | 0 | 0 | 0 | Battery-supported
2025-04-20 17:00 | 110 | 4 | Autumn | 17 | 7.43 | -12.7 | 14.64 | 27.3 | 0 | 0 | 120 | 120 | 12.7 | 61.24 | 66.01 | 58.76 | 0 | 0 | 0 | Normal
2025-04-20 18:00 | 110 | 4 | Autumn | 18 | 7.43 | -10 | 8 | 96.6 | 0 | 0 | 12.75 | 12.75 | 10 | 56.38 | 48.56 | -43.63 | 0 | 0 | 0 | Battery-supported
2025-04-20 19:00 | 110 | 4 | Autumn | 19 | 7.43 | -9.7 | 8.57 | 45.1 | 0 | 0 | 18.24 | 18.24 | 9.7 | 46.36 | 37.31 | -28.12 | 0 | 0 | 0 | Battery-supported
2025-04-20 20:00 | 110 | 4 | Autumn | 20 | 7.43 | -13 | 11.35 | 40.3 | 0 | 0 | 67.7 | 67.7 | 13 | 58.1 | 40.85 | 9.6 | 0 | 0 | 0 | Normal
2025-04-20 21:00 | 110 | 4 | Autumn | 21 | 7.43 | -12.8 | 8.09 | 32.4 | 0 | 0 | 13.53 | 13.53 | 12.8 | 47.55 | 27.24 | -34.02 | 0 | 0 | 0 | Battery-supported
2025-04-20 22:00 | 110 | 4 | Autumn | 22 | 7.43 | -11 | 5.49 | 52.4 | 0 | 0 | 1.1 | 1.1 | 11 | 45 | 15 | -30.6 | 13.3 | 4.796 | 0 | Diesel-backup
2025-04-20 23:00 | 110 | 4 | Autumn | 23 | 7.43 | -14 | 13.21 | 39.8 | 0 | 0 | 120 | 120 | 14 | 45.69 | 42.35 | 74.31 | 0 | 0 | 0 | Normal
2025-04-21 | 111 | 4 | Autumn | 0 | 7.26 | -11.9 | 9.6 | 40.7 | 211.9 | 12.71 | 31.77 | 44.48 | 11.9 | 46.04 | 41.72 | -1.56 | 0 | 0 | 0 | Battery-supported
2025-04-21 01:00 | 111 | 4 | Autumn | 1 | 7.26 | -13.8 | 6.88 | 71.7 | 15.3 | 0.92 | 5.4 | 6.32 | 13.8 | 45 | 26.25 | -38.68 | 0 | 0 | 0 | Battery-supported
2025-04-21 02:00 | 111 | 4 | Autumn | 2 | 7.26 | -16.1 | 4.2 | 66.1 | 0 | 0 | 0.05 | 0.05 | 16.1 | 51.99 | 15 | -28.13 | 23.81 | 8.267 | 0 | Diesel-backup
2025-04-21 03:00 | 111 | 4 | Autumn | 3 | 7.26 | -16.5 | 2.27 | 6.4 | 0 | 0 | 0 | 0 | 16.5 | 51.84 | 15 | 0 | 51.84 | 16.589 | 0 | Diesel-backup
2025-04-21 04:00 | 111 | 4 | Autumn | 4 | 7.26 | -11.5 | 11.73 | 78.8 | 0 | 0 | 78.02 | 78.02 | 11.5 | 45.48 | 26.97 | 32.54 | 0 | 0 | 0 | Normal
2025-04-21 05:00 | 111 | 4 | Autumn | 5 | 7.26 | -15.4 | 5.42 | 71.7 | 0 | 0 | 0.99 | 0.99 | 15.4 | 50.54 | 15 | -29.94 | 19.61 | 6.914 | 0 | Diesel-backup
2025-04-21 06:00 | 111 | 4 | Autumn | 6 | 7.26 | -11.7 | 2.94 | 11.6 | 0 | 0 | 0 | 0 | 11.7 | 45.8 | 15 | 0 | 45.8 | 14.656 | 0 | Diesel-backup
2025-04-21 07:00 | 111 | 4 | Autumn | 7 | 7.26 | -16.6 | 5.01 | 48.8 | 0 | 0 | 0.48 | 0.48 | 16.6 | 47.1 | 15 | 0 | 46.62 | 14.918 | 0 | Diesel-backup
2025-04-21 08:00 | 111 | 4 | Autumn | 8 | 7.26 | -14.8 | 10.55 | 73.5 | 0 | 0 | 49.04 | 49.04 | 14.8 | 55.24 | 15 | 0 | 6.2 | 2.292 | 0 | Diesel-backup
2025-04-21 09:00 | 111 | 4 | Autumn | 9 | 7.26 | -10.2 | 5.39 | 70.1 | 83.5 | 5.01 | 0.94 | 5.95 | 10.2 | 50.09 | 15 | 0 | 44.14 | 14.173 | 0 | Diesel-backup
2025-04-21 10:00 | 111 | 4 | Autumn | 10 | 7.26 | -17.6 | 10.67 | 19.1 | 364 | 21.84 | 51.59 | 73.43 | 17.6 | 63.12 | 18.79 | 10.31 | 0 | 0 | 0 | Normal
2025-04-21 11:00 | 111 | 4 | Autumn | 11 | 7.26 | -19.2 | 6.15 | 39.3 | 419.7 | 21.4 | 2.6 | 24 | 19.2 | 57.94 | 15 | -9.49 | 24.45 | 8.469 | 0 | Diesel-backup
2025-04-21 12:00 | 111 | 4 | Autumn | 12 | 7.26 | -11.9 | 8.66 | 52.6 | 397.1 | 23.83 | 19.23 | 43.06 | 11.9 | 52.69 | 15 | 0 | 9.63 | 3.518 | 0 | Diesel-backup
2025-04-21 13:00 | 111 | 4 | Autumn | 13 | 7.26 | -16.2 | 9.11 | 71.3 | 277.1 | 16.63 | 24.71 | 41.34 | 16.2 | 59.31 | 15 | 0 | 17.97 | 6.372 | 0 | Diesel-backup
2025-04-21 14:00 | 111 | 4 | Autumn | 14 | 7.26 | -14 | 12.86 | 72.8 | 193 | 11.58 | 114.77 | 126.35 | 14 | 50.9 | 42.77 | 75.45 | 0 | 0 | 0 | Normal
2025-04-21 15:00 | 111 | 4 | Autumn | 15 | 7.26 | -14.9 | 13.09 | 49.5 | 110.8 | 6.65 | 120 | 126.65 | 14.9 | 56.08 | 68.74 | 70.57 | 0 | 0 | 0 | Normal
2025-04-21 16:00 | 111 | 4 | Autumn | 16 | 7.26 | -12.6 | 8.83 | 36.8 | 0 | 0 | 21.19 | 21.19 | 12.6 | 55.69 | 54.94 | -34.5 | 0 | 0 | 0 | Battery-supported
2025-04-21 17:00 | 111 | 4 | Autumn | 17 | 7.26 | -15 | 4.68 | 13.5 | 0 | 0 | 0.23 | 0.23 | 15 | 58.62 | 31.58 | -58.39 | 0 | 0 | 0 | Battery-supported
2025-04-21 18:00 | 111 | 4 | Autumn | 18 | 7.26 | -13.1 | 16.49 | 56.2 | 0 | 0 | 120 | 120 | 13.1 | 57.45 | 54.6 | 62.55 | 0 | 0 | 0 | Normal
2025-04-21 19:00 | 111 | 4 | Autumn | 19 | 7.26 | -11.5 | 6.79 | 71.3 | 0 | 0 | 4.98 | 4.98 | 11.5 | 51.41 | 36.03 | -46.43 | 0 | 0 | 0 | Battery-supported
2025-04-21 20:00 | 111 | 4 | Autumn | 20 | 7.26 | -14.7 | 1.33 | 41.3 | 0 | 0 | 0 | 0 | 14.7 | 53.28 | 15 | -52.56 | 0.72 | 0.27 | 0 | Diesel-backup
2025-04-21 21:00 | 111 | 4 | Autumn | 21 | 7.26 | -14.1 | 10.32 | 63.6 | 0 | 0 | 44.4 | 44.4 | 14.1 | 47.18 | 15 | 0 | 2.78 | 1.04 | 0 | Diesel-backup
2025-04-21 22:00 | 111 | 4 | Autumn | 22 | 7.26 | -13.4 | 10.56 | 71.7 | 0 | 0 | 49.25 | 49.25 | 13.4 | 49.13 | 15.04 | 0.12 | 0 | 0 | 0 | Normal
2025-04-21 23:00 | 111 | 4 | Autumn | 23 | 7.26 | -16.1 | 6.96 | 35.3 | 24.3 | 1.46 | 5.8 | 7.26 | 16.1 | 49.89 | 15 | -0.11 | 42.52 | 13.741 | 0 | Diesel-backup
2025-04-22 | 112 | 4 | Autumn | 0 | 7.08 | -14.4 | 3.11 | 56.2 | 217.5 | 13.05 | 0 | 13.05 | 14.4 | 45 | 15 | 0 | 31.95 | 10.758 | 0 | Diesel-backup
2025-04-22 01:00 | 112 | 4 | Autumn | 1 | 7.08 | -13.5 | 2.64 | 10.7 | 100.1 | 6.01 | 0 | 6.01 | 13.5 | 57.31 | 15 | 0 | 51.3 | 16.416 | 0 | Diesel-backup
2025-04-22 02:00 | 112 | 4 | Autumn | 2 | 7.08 | -15.1 | 7.32 | 100 | 0 | 0 | 7.8 | 7.8 | 15.1 | 46.89 | 15 | 0 | 39.09 | 12.805 | 0 | Diesel-backup
2025-04-22 03:00 | 112 | 4 | Autumn | 3 | 7.08 | -15.2 | 4.39 | 0 | 0 | 0 | 0.1 | 0.1 | 15.2 | 45 | 15 | 0 | 44.9 | 14.374 | 0 | Diesel-backup
2025-04-22 04:00 | 112 | 4 | Autumn | 4 | 7.08 | -15 | 14.72 | 28.8 | 0 | 0 | 120 | 120 | 15 | 47.18 | 41.8 | 72.82 | 0 | 0 | 0 | Normal
2025-04-22 05:00 | 112 | 4 | Autumn | 5 | 7.08 | -16.7 | 7.14 | 0.4 | 0 | 0 | 6.75 | 6.75 | 16.7 | 55.15 | 22.44 | -48.4 | 0 | 0 | 0 | Battery-supported
2025-04-22 06:00 | 112 | 4 | Autumn | 6 | 7.08 | -14 | 6.6 | 61.9 | 0 | 0 | 4.17 | 4.17 | 14 | 51.28 | 15 | -18.59 | 28.52 | 9.727 | 0 | Diesel-backup
2025-04-22 07:00 | 112 | 4 | Autumn | 7 | 7.08 | -12.5 | 22.8 | 91.1 | 0 | 0 | 120 | 120 | 12.5 | 54.64 | 39.05 | 65.36 | 0 | 0 | 0 | Normal
2025-04-22 08:00 | 112 | 4 | Autumn | 8 | 7.08 | -16.7 | 1.52 | 77 | 0 | 0 | 0 | 0 | 16.7 | 55.65 | 16.79 | -55.65 | 0 | 0 | 0 | Battery-supported
2025-04-22 09:00 | 112 | 4 | Autumn | 9 | 7.08 | -14.6 | 8.64 | 60.8 | 84.9 | 5.09 | 19.01 | 24.1 | 14.6 | 56.39 | 15 | -4.48 | 27.81 | 9.511 | 0 | Diesel-backup
2025-04-22 10:00 | 112 | 4 | Autumn | 10 | 7.08 | -16 | 2.34 | 85.2 | 149.7 | 8.98 | 0 | 8.98 | 16 | 63.05 | 15 | 0 | 54.07 | 17.302 | 0 | Diesel-backup
2025-04-22 11:00 | 112 | 4 | Autumn | 11 | 7.08 | -14.4 | 17.52 | 66.1 | 298.9 | 17.93 | 120 | 137.93 | 14.4 | 53.2 | 46.18 | 84.73 | 0 | 0 | 0 | Normal
2025-04-22 12:00 | 112 | 4 | Autumn | 12 | 7.08 | -11.5 | 2.91 | 27 | 523.2 | 31.39 | 0 | 31.39 | 11.5 | 59.14 | 35.08 | -27.75 | 0 | 0 | 0 | Battery-supported
2025-04-22 13:00 | 112 | 4 | Autumn | 13 | 7.08 | -13.5 | 10.85 | 89.6 | 194.4 | 11.66 | 55.57 | 67.23 | 13.5 | 56.64 | 38.98 | 10.59 | 0 | 0 | 0 | Normal
2025-04-22 14:00 | 112 | 4 | Autumn | 14 | 7.08 | -18.1 | 9.96 | 49.1 | 261.7 | 13.35 | 37.73 | 51.08 | 18.1 | 57.91 | 36.25 | -6.83 | 0 | 0 | 0 | Battery-supported
2025-04-22 15:00 | 112 | 4 | Autumn | 15 | 7.08 | -12.8 | 2.3 | 26 | 125.6 | 7.54 | 0 | 7.54 | 12.8 | 48.94 | 19.69 | -41.4 | 0 | 0 | 0 | Battery-supported
2025-04-22 16:00 | 112 | 4 | Autumn | 16 | 7.08 | -10.7 | 10.9 | 51.3 | 0 | 0 | 56.72 | 56.72 | 10.7 | 55.79 | 20.03 | 0.93 | 0 | 0 | 0 | Normal
2025-04-22 17:00 | 112 | 4 | Autumn | 17 | 7.08 | -13.6 | 6.15 | 24.4 | 0 | 0 | 2.6 | 2.6 | 13.6 | 62.51 | 15 | -12.57 | 47.34 | 15.149 | 0 | Diesel-backup
2025-04-22 18:00 | 112 | 4 | Autumn | 18 | 7.08 | -10.7 | 12.13 | 52.1 | 0 | 0 | 89.96 | 89.96 | 10.7 | 55.06 | 27.84 | 34.9 | 0 | 0 | 0 | Normal
2025-04-22 19:00 | 112 | 4 | Autumn | 19 | 7.08 | -14.3 | 5.89 | 93.8 | 0 | 0 | 1.91 | 1.91 | 14.3 | 58.89 | 15 | -32.11 | 24.87 | 8.6 | 0 | Diesel-backup
2025-04-22 20:00 | 112 | 4 | Autumn | 20 | 7.08 | -16 | 10.92 | 38.1 | 0 | 0 | 57.18 | 57.18 | 16 | 60.05 | 15 | 0 | 2.87 | 1.073 | 0 | Diesel-backup
2025-04-22 21:00 | 112 | 4 | Autumn | 21 | 7.08 | -12.4 | 8.13 | 25.4 | 0 | 0 | 13.89 | 13.89 | 12.4 | 51.09 | 15 | 0 | 37.2 | 12.275 | 0 | Diesel-backup
2025-04-22 22:00 | 112 | 4 | Autumn | 22 | 7.08 | -16.8 | 10.9 | 95.4 | 0 | 0 | 56.72 | 56.72 | 16.8 | 56.71 | 15 | 0.01 | 0 | 0 | 0 | Normal
2025-04-22 23:00 | 112 | 4 | Autumn | 23 | 7.08 | -13.7 | 12.01 | 25.4 | 88.1 | 5.29 | 86.26 | 91.55 | 13.7 | 45 | 32.13 | 46.55 | 0 | 0 | 0 | Normal
2025-04-23 | 113 | 4 | Autumn | 0 | 6.91 | -10.8 | 7.62 | 47.3 | 286.8 | 17.21 | 9.79 | 27 | 10.8 | 45 | 24.93 | -18 | 0 | 0 | 0 | Battery-supported
2025-04-23 01:00 | 113 | 4 | Autumn | 1 | 6.91 | -18.2 | 6.86 | 20.7 | 158.4 | 8.08 | 5.31 | 13.39 | 18.2 | 50.73 | 15 | -24.84 | 12.5 | 4.522 | 0 | Diesel-backup
2025-04-23 02:00 | 113 | 4 | Autumn | 2 | 6.91 | -17.2 | 11.86 | 78.6 | 0 | 0 | 81.78 | 81.78 | 17.2 | 52.95 | 25.61 | 28.83 | 0 | 0 | 0 | Normal
2025-04-23 03:00 | 113 | 4 | Autumn | 3 | 6.91 | -17 | 6.23 | 28.4 | 0 | 0 | 2.85 | 2.85 | 17 | 50.41 | 15 | -26.52 | 21.04 | 7.377 | 0 | Diesel-backup
2025-04-23 04:00 | 113 | 4 | Autumn | 4 | 6.91 | -15.3 | 7.72 | 18.1 | 0 | 0 | 10.52 | 10.52 | 15.3 | 52.08 | 15 | 0 | 41.56 | 13.482 | 0 | Diesel-backup
2025-04-23 05:00 | 113 | 4 | Autumn | 5 | 6.91 | -16.3 | 19.51 | 33.5 | 0 | 0 | 120 | 120 | 16.3 | 52.64 | 39.79 | 67.36 | 0 | 0 | 0 | Normal
2025-04-23 06:00 | 113 | 4 | Autumn | 6 | 6.91 | -12.6 | 8.73 | 23.1 | 0 | 0 | 20.02 | 20.02 | 12.6 | 45 | 29.8 | -24.98 | 0 | 0 | 0 | Battery-supported
2025-04-23 07:00 | 113 | 4 | Autumn | 7 | 6.91 | -13.7 | 13.19 | 41.1 | 0 | 0 | 120 | 120 | 13.7 | 45 | 57.4 | 75 | 0 | 0 | 0 | Normal
2025-04-23 08:00 | 113 | 4 | Autumn | 8 | 6.91 | -14.8 | 5.63 | 11.6 | 0 | 0 | 1.35 | 1.35 | 14.8 | 60.83 | 33.6 | -59.48 | 0 | 0 | 0 | Battery-supported
2025-04-23 09:00 | 113 | 4 | Autumn | 9 | 6.91 | -15.5 | 10.87 | 39.3 | 94.9 | 5.69 | 56.03 | 61.72 | 15.5 | 55.18 | 36.01 | 6.54 | 0 | 0 | 0 | Normal
2025-04-23 10:00 | 113 | 4 | Autumn | 10 | 6.91 | -14.8 | 7.84 | 0.4 | 401.5 | 24.09 | 11.44 | 35.53 | 14.8 | 64.67 | 24.36 | -29.14 | 0 | 0 | 0 | Battery-supported
2025-04-23 11:00 | 113 | 4 | Autumn | 11 | 6.91 | -17.3 | 6.97 | 68.1 | 288.5 | 17.31 | 5.85 | 23.16 | 17.3 | 63.71 | 15 | -23.39 | 17.16 | 6.103 | 0 | Diesel-backup
2025-04-23 12:00 | 113 | 4 | Autumn | 12 | 6.91 | -13.3 | 2.17 | 33.4 | 491.6 | 29.5 | 0 | 29.5 | 13.3 | 49.15 | 15 | 0 | 19.65 | 6.926 | 0 | Diesel-backup
2025-04-23 13:00 | 113 | 4 | Autumn | 13 | 6.91 | -17.2 | 4.44 | 73 | 266.6 | 16 | 0.12 | 16.12 | 17.2 | 57.01 | 15 | 0 | 40.89 | 13.3 | 0 | Diesel-backup
2025-04-23 14:00 | 113 | 4 | Autumn | 14 | 6.91 | -12.6 | 1.94 | 80.5 | 159.6 | 9.58 | 0 | 9.58 | 12.6 | 56.56 | 15 | 0 | 46.98 | 15.034 | 0 | Diesel-backup
2025-04-23 15:00 | 113 | 4 | Autumn | 15 | 6.91 | -11.4 | 23.72 | 83.1 | 50.7 | 3.04 | 120 | 123.04 | 11.4 | 52.62 | 40.91 | 70.42 | 0 | 0 | 0 | Normal
2025-04-23 16:00 | 113 | 4 | Autumn | 16 | 6.91 | -13.2 | 8.09 | 60.1 | 0 | 0 | 13.53 | 13.53 | 13.2 | 55.51 | 24.12 | -41.98 | 0 | 0 | 0 | Battery-supported
2025-04-23 17:00 | 113 | 4 | Autumn | 17 | 6.91 | -13.7 | 8.76 | 53.5 | 0 | 0 | 20.37 | 20.37 | 13.7 | 52.27 | 15 | -22.81 | 9.09 | 3.328 | 0 | Diesel-backup
2025-04-23 18:00 | 113 | 4 | Autumn | 18 | 6.91 | -12.2 | 14.55 | 53 | 0 | 0 | 120 | 120 | 12.2 | 56.58 | 38.34 | 63.42 | 0 | 0 | 0 | Normal
2025-04-23 19:00 | 113 | 4 | Autumn | 19 | 6.91 | -19.2 | 10.27 | 61.2 | 0 | 0 | 43.43 | 43.43 | 19.2 | 62.28 | 30.8 | -18.85 | 0 | 0 | 0 | Battery-supported
2025-04-23 20:00 | 113 | 4 | Autumn | 20 | 6.91 | -12.2 | 6.94 | 78.3 | 0 | 0 | 5.7 | 5.7 | 12.2 | 58.22 | 15 | -39.5 | 13.02 | 4.701 | 0 | Diesel-backup
2025-04-23 21:00 | 113 | 4 | Autumn | 21 | 6.91 | -13.2 | 6.99 | 90.9 | 0 | 0 | 5.95 | 5.95 | 13.2 | 48.01 | 15 | 0 | 42.06 | 13.617 | 0 | Diesel-backup
2025-04-23 22:00 | 113 | 4 | Autumn | 22 | 6.91 | -13.2 | 4.2 | 69.7 | 0 | 0 | 0.05 | 0.05 | 13.2 | 45.69 | 15 | 0 | 45.64 | 14.605 | 0 | Diesel-backup
2025-04-23 23:00 | 113 | 4 | Autumn | 23 | 6.91 | -11.8 | 11.4 | 67.8 | 92.1 | 5.53 | 69.01 | 74.54 | 11.8 | 47.35 | 25.01 | 27.19 | 0 | 0 | 0 | Normal
2025-04-24 | 114 | 4 | Autumn | 0 | 6.73 | -14 | 11.68 | 96.6 | 140.1 | 8.41 | 76.61 | 85.02 | 14 | 50.45 | 37.73 | 34.57 | 0 | 0 | 0 | Normal
2025-04-24 01:00 | 114 | 4 | Autumn | 1 | 6.73 | -16.7 | 8.86 | 90.3 | 86.5 | 5.19 | 21.55 | 26.74 | 16.7 | 51.71 | 27.74 | -24.97 | 0 | 0 | 0 | Battery-supported
2025-04-24 02:00 | 114 | 4 | Autumn | 2 | 6.73 | -14.9 | 7.99 | 62.1 | 0 | 0 | 12.67 | 12.67 | 14.9 | 54.81 | 15 | -31.85 | 10.29 | 3.75 | 0 | Diesel-backup
2025-04-24 03:00 | 114 | 4 | Autumn | 3 | 6.73 | -14.8 | 11.74 | 25.8 | 0 | 0 | 78.31 | 78.31 | 14.8 | 45.46 | 27.09 | 32.85 | 0 | 0 | 0 | Normal
2025-04-24 04:00 | 114 | 4 | Autumn | 4 | 6.73 | -15.1 | 4.15 | 36.2 | 0 | 0 | 0.04 | 0.04 | 15.1 | 53.73 | 15 | -30.22 | 23.47 | 8.157 | 0 | Diesel-backup
2025-04-24 05:00 | 114 | 4 | Autumn | 5 | 6.73 | -15.3 | 10.64 | 40.1 | 0 | 0 | 50.95 | 50.95 | 15.3 | 45.42 | 17.04 | 5.53 | 0 | 0 | 0 | Normal
2025-04-24 06:00 | 114 | 4 | Autumn | 6 | 6.73 | -13.6 | 20.19 | 38.4 | 0 | 0 | 120 | 120 | 13.6 | 51.21 | 42.35 | 68.79 | 0 | 0 | 0 | Normal
2025-04-24 07:00 | 114 | 4 | Autumn | 7 | 6.73 | -18.4 | 5.76 | 40.8 | 0 | 0 | 1.62 | 1.62 | 18.4 | 45.18 | 24.93 | -43.56 | 0 | 0 | 0 | Battery-supported
2025-04-24 08:00 | 114 | 4 | Autumn | 8 | 6.73 | -15.7 | 7.53 | 46.3 | 0 | 0 | 9.16 | 9.16 | 15.7 | 57.5 | 15 | -24.81 | 23.53 | 8.175 | 0 | Diesel-backup
2025-04-24 09:00 | 114 | 4 | Autumn | 9 | 6.73 | -13.2 | 17.22 | 42.3 | 76.1 | 4.57 | 120 | 124.57 | 13.2 | 60.01 | 38.76 | 64.56 | 0 | 0 | 0 | Normal
2025-04-24 10:00 | 114 | 4 | Autumn | 10 | 6.73 | -19.7 | 8.87 | 66.6 | 195.5 | 9.97 | 21.67 | 31.64 | 19.7 | 61.04 | 27 | -29.4 | 0 | 0 | 0 | Battery-supported
2025-04-24 11:00 | 114 | 4 | Autumn | 11 | 6.73 | -15.3 | 13.83 | 59.4 | 325 | 19.5 | 120 | 139.5 | 15.3 | 57.88 | 57.03 | 81.62 | 0 | 0 | 0 | Normal
2025-04-24 12:00 | 114 | 4 | Autumn | 12 | 6.73 | -16.6 | 11 | 69 | 316.6 | 19 | 59.05 | 78.05 | 16.6 | 60.65 | 63.44 | 17.4 | 0 | 0 | 0 | Normal
2025-04-24 13:00 | 114 | 4 | Autumn | 13 | 6.73 | -15.8 | 11.54 | 60.1 | 321.6 | 19.3 | 72.74 | 92.04 | 15.8 | 49.45 | 79.11 | 42.59 | 0 | 0 | 0 | Normal
2025-04-24 14:00 | 114 | 4 | Autumn | 14 | 6.73 | -16.6 | 5.55 | 91.5 | 122.4 | 7.34 | 1.21 | 8.55 | 16.6 | 60.73 | 58.24 | -52.18 | 0 | 0 | 0 | Battery-supported
2025-04-24 15:00 | 114 | 4 | Autumn | 15 | 6.73 | -14.6 | 5.44 | 30.9 | 85.7 | 5.14 | 1.02 | 6.16 | 14.6 | 53.72 | 39.21 | -47.56 | 0 | 0 | 0 | Battery-supported
2025-04-24 16:00 | 114 | 4 | Autumn | 16 | 6.73 | -9.8 | 12.79 | 23.1 | 0 | 0 | 112.22 | 112.22 | 9.8 | 56.49 | 59.72 | 55.73 | 0 | 0 | 0 | Normal
2025-04-24 17:00 | 114 | 4 | Autumn | 17 | 6.73 | -16.3 | 3.33 | 19.3 | 0 | 0 | 0 | 0 | 16.3 | 58.8 | 36.2 | -58.8 | 0 | 0 | 0 | Battery-supported
2025-04-24 18:00 | 114 | 4 | Autumn | 18 | 6.73 | -15.9 | 7.74 | 18.2 | 0 | 0 | 10.67 | 10.67 | 15.9 | 59.87 | 16.52 | -49.2 | 0 | 0 | 0 | Battery-supported
2025-04-24 19:00 | 114 | 4 | Autumn | 19 | 6.73 | -16 | 11.75 | 53.8 | 0 | 0 | 78.59 | 78.59 | 16 | 54.11 | 25.53 | 24.48 | 0 | 0 | 0 | Normal
2025-04-24 20:00 | 114 | 4 | Autumn | 20 | 6.73 | -9.3 | 7.5 | 43.8 | 0 | 0 | 8.96 | 8.96 | 9.3 | 55.35 | 15 | -26.33 | 20.06 | 7.06 | 0 | Diesel-backup
2025-04-24 21:00 | 114 | 4 | Autumn | 21 | 6.73 | -14.2 | 8.04 | 31.7 | 0 | 0 | 13.1 | 13.1 | 14.2 | 48.92 | 15 | 0 | 35.82 | 11.883 | 0 | Diesel-backup
2025-04-24 22:00 | 114 | 4 | Autumn | 22 | 6.73 | -13.4 | 20.25 | 50.1 | 0 | 0 | 120 | 120 | 13.4 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-04-24 23:00 | 114 | 4 | Autumn | 23 | 6.73 | -14.4 | 14.22 | 54.6 | 158.2 | 9.49 | 120 | 129.49 | 14.4 | 47.17 | 72.89 | 82.32 | 0 | 0 | 0 | Normal
2025-04-25 | 115 | 4 | Autumn | 0 | 6.55 | -16.1 | 18.46 | 24.9 | 460.1 | 27.61 | 120 | 147.61 | 16.1 | 53.58 | 95 | 60.07 | 0 | 0 | 0 | Normal
2025-04-25 01:00 | 115 | 4 | Autumn | 1 | 6.55 | -14.9 | 29.24 | 71.7 | 161 | 9.66 | 0 | 9.66 | 14.9 | 50.23 | 78.77 | -40.57 | 0 | 0 | 0 | Battery-supported
2025-04-25 02:00 | 115 | 4 | Autumn | 2 | 6.55 | -9.4 | 17.57 | 0 | 53 | 3.18 | 120 | 123.18 | 9.4 | 47.03 | 95 | 44.1 | 0 | 0 | 0 | Normal
2025-04-25 03:00 | 115 | 4 | Autumn | 3 | 6.55 | -12.1 | 6.58 | 39.5 | 0 | 0 | 4.09 | 4.09 | 12.1 | 45.43 | 78.46 | -41.34 | 0 | 0 | 0 | Battery-supported
2025-04-25 04:00 | 115 | 4 | Autumn | 4 | 6.55 | -17.4 | 4.97 | 69.2 | 0 | 0 | 0.44 | 0.44 | 17.4 | 57.03 | 55.83 | -56.59 | 0 | 0 | 0 | Battery-supported
2025-04-25 05:00 | 115 | 4 | Autumn | 5 | 6.55 | -14.4 | 6.64 | 65.8 | 0 | 0 | 4.33 | 4.33 | 14.4 | 54.82 | 35.63 | -50.49 | 0 | 0 | 0 | Battery-supported
2025-04-25 06:00 | 115 | 4 | Autumn | 6 | 6.55 | -17.9 | 11.9 | 52.4 | 0 | 0 | 82.96 | 82.96 | 17.9 | 45.67 | 49.35 | 37.29 | 0 | 0 | 0 | Normal
2025-04-25 07:00 | 115 | 4 | Autumn | 7 | 6.55 | -20.2 | 7.07 | 7.2 | 0 | 0 | 6.37 | 6.37 | 20.2 | 57.34 | 28.97 | -50.97 | 0 | 0 | 0 | Battery-supported
2025-04-25 08:00 | 115 | 4 | Autumn | 8 | 6.55 | -14.1 | 5.71 | 26.5 | 0 | 0 | 1.51 | 1.51 | 14.1 | 62.94 | 15 | -34.92 | 26.51 | 9.112 | 0 | Diesel-backup
2025-04-25 09:00 | 115 | 4 | Autumn | 9 | 6.55 | -13.7 | 19.73 | 68.3 | 42.3 | 2.54 | 120 | 122.54 | 13.7 | 58.4 | 38.6 | 64.14 | 0 | 0 | 0 | Normal
2025-04-25 10:00 | 115 | 4 | Autumn | 10 | 6.55 | -13.8 | 6.93 | 46.4 | 245.6 | 14.74 | 5.65 | 20.39 | 13.8 | 56.42 | 24.19 | -36.03 | 0 | 0 | 0 | Battery-supported
2025-04-25 11:00 | 115 | 4 | Autumn | 11 | 6.55 | -16.9 | 11.37 | 80.8 | 229.3 | 13.76 | 68.22 | 81.98 | 16.9 | 54.38 | 34.35 | 27.6 | 0 | 0 | 0 | Normal
2025-04-25 12:00 | 115 | 4 | Autumn | 12 | 6.55 | -15.9 | 11.19 | 41.2 | 453.4 | 27.2 | 63.65 | 90.85 | 15.9 | 57.44 | 46.64 | 33.41 | 0 | 0 | 0 | Normal
2025-04-25 13:00 | 115 | 4 | Autumn | 13 | 6.55 | -13.5 | 2.23 | 22.9 | 481.8 | 28.91 | 0 | 28.91 | 13.5 | 54.25 | 36.51 | -25.34 | 0 | 0 | 0 | Battery-supported
2025-04-25 14:00 | 115 | 4 | Autumn | 14 | 6.55 | -13.9 | 19.06 | 29 | 295 | 17.7 | 120 | 137.7 | 13.9 | 60.21 | 65.02 | 77.49 | 0 | 0 | 0 | Normal
2025-04-25 15:00 | 115 | 4 | Autumn | 15 | 6.55 | -15.3 | 3.99 | 44.6 | 57.8 | 3.47 | 0.02 | 3.49 | 15.3 | 62.07 | 41.59 | -58.58 | 0 | 0 | 0 | Battery-supported
2025-04-25 16:00 | 115 | 4 | Autumn | 16 | 6.55 | -17.6 | 3.1 | 57.8 | 0 | 0 | 0 | 0 | 17.6 | 59.72 | 17.7 | -59.72 | 0 | 0 | 0 | Battery-supported
2025-04-25 17:00 | 115 | 4 | Autumn | 17 | 6.55 | -13.5 | 6.44 | 40.6 | 0 | 0 | 3.56 | 3.56 | 13.5 | 52.49 | 15 | -6.76 | 42.17 | 13.647 | 0 | Diesel-backup
2025-04-25 18:00 | 115 | 4 | Autumn | 18 | 6.55 | -11.1 | 5.01 | 41.7 | 0 | 0 | 0.48 | 0.48 | 11.1 | 45.37 | 15 | 0 | 44.89 | 14.371 | 0 | Diesel-backup
2025-04-25 19:00 | 115 | 4 | Autumn | 19 | 6.55 | -16 | 17.37 | 72.4 | 0 | 0 | 120 | 120 | 16 | 61.14 | 36.66 | 58.86 | 0 | 0 | 0 | Normal
2025-04-25 20:00 | 115 | 4 | Autumn | 20 | 6.55 | -11.9 | 10.24 | 42.5 | 0 | 0 | 42.85 | 42.85 | 11.9 | 56.7 | 31.12 | -13.85 | 0 | 0 | 0 | Battery-supported
2025-04-25 21:00 | 115 | 4 | Autumn | 21 | 6.55 | -12.6 | 6.07 | 71.5 | 0 | 0 | 2.38 | 2.38 | 12.6 | 45 | 15 | -40.3 | 2.32 | 0.869 | 0 | Diesel-backup
2025-04-25 22:00 | 115 | 4 | Autumn | 22 | 6.55 | -11.9 | 3.02 | 26.6 | 42.4 | 2.54 | 0 | 2.54 | 11.9 | 48.77 | 15 | 0 | 46.23 | 14.794 | 0 | Diesel-backup
2025-04-25 23:00 | 115 | 4 | Autumn | 23 | 6.55 | -11.8 | 10.95 | 31.1 | 267.2 | 16.03 | 57.87 | 73.9 | 11.8 | 50.07 | 23.77 | 23.83 | 0 | 0 | 0 | Normal
2025-04-26 | 116 | 4 | Autumn | 0 | 6.37 | -15.8 | 7.35 | 63.5 | 320.3 | 19.22 | 7.99 | 27.21 | 15.8 | 45 | 16.65 | -17.79 | 0 | 0 | 0 | Battery-supported
2025-04-26 01:00 | 116 | 4 | Autumn | 1 | 6.37 | -18.2 | 11.88 | 26.5 | 342.3 | 17.46 | 82.36 | 99.82 | 18.2 | 48.95 | 35.37 | 50.87 | 0 | 0 | 0 | Normal
2025-04-26 02:00 | 116 | 4 | Autumn | 2 | 6.37 | -16.2 | 10.32 | 86.4 | 49.6 | 2.98 | 44.4 | 47.38 | 16.2 | 60.94 | 29.95 | -13.56 | 0 | 0 | 0 | Battery-supported
2025-04-26 03:00 | 116 | 4 | Autumn | 3 | 6.37 | -13.4 | 5.14 | 36.5 | 0 | 0 | 0.62 | 0.62 | 13.4 | 48.49 | 15 | -37.37 | 10.5 | 3.822 | 0 | Diesel-backup
2025-04-26 04:00 | 116 | 4 | Autumn | 4 | 6.37 | -16.9 | 12.76 | 65.8 | 0 | 0 | 111.13 | 111.13 | 16.9 | 60.88 | 33.49 | 50.25 | 0 | 0 | 0 | Normal
2025-04-26 05:00 | 116 | 4 | Autumn | 5 | 6.37 | -17.6 | 3.68 | 55.5 | 0 | 0 | 0 | 0 | 17.6 | 53.37 | 15 | -46.23 | 7.14 | 2.631 | 0 | Diesel-backup
2025-04-26 06:00 | 116 | 4 | Autumn | 6 | 6.37 | -20.3 | 7.16 | 32.3 | 0 | 0 | 6.86 | 6.86 | 20.3 | 59.6 | 15 | 0 | 52.74 | 16.877 | 0 | Diesel-backup
2025-04-26 07:00 | 116 | 4 | Autumn | 7 | 6.37 | -12.6 | 7.77 | 88 | 0 | 0 | 10.9 | 10.9 | 12.6 | 46.28 | 15 | 0 | 35.38 | 11.757 | 0 | Diesel-backup
2025-04-26 08:00 | 116 | 4 | Autumn | 8 | 6.37 | -14.7 | 8.43 | 43.8 | 0 | 0 | 16.77 | 16.77 | 14.7 | 54.93 | 15 | 0 | 38.16 | 12.545 | 0 | Diesel-backup
2025-04-26 09:00 | 116 | 4 | Autumn | 9 | 6.37 | -14.8 | 3.52 | 51.7 | 37 | 2.22 | 0 | 2.22 | 14.8 | 51.32 | 15 | 0 | 49.1 | 15.712 | 0 | Diesel-backup
2025-04-26 10:00 | 116 | 4 | Autumn | 10 | 6.37 | -14.2 | 16.94 | 23.4 | 298.7 | 17.92 | 120 | 137.92 | 14.2 | 59.28 | 43.94 | 78.64 | 0 | 0 | 0 | Normal
2025-04-26 11:00 | 116 | 4 | Autumn | 11 | 6.37 | -14.8 | 5.13 | 51.5 | 354.8 | 21.29 | 0.61 | 21.9 | 14.8 | 54.32 | 30.97 | -32.42 | 0 | 0 | 0 | Battery-supported
2025-04-26 12:00 | 116 | 4 | Autumn | 12 | 6.37 | -16.3 | 2.53 | 71 | 306.6 | 18.4 | 0 | 18.4 | 16.3 | 55.39 | 16.18 | -36.99 | 0 | 0 | 0 | Battery-supported
2025-04-26 13:00 | 116 | 4 | Autumn | 13 | 6.37 | -15.8 | 10.51 | 31.4 | 441.7 | 26.5 | 48.21 | 74.71 | 15.8 | 52.49 | 24.35 | 22.22 | 0 | 0 | 0 | Normal
2025-04-26 14:00 | 116 | 4 | Autumn | 14 | 6.37 | -15.9 | 23.78 | 78.2 | 149.7 | 8.98 | 120 | 128.98 | 15.9 | 58.98 | 50.11 | 70 | 0 | 0 | 0 | Normal
2025-04-26 15:00 | 116 | 4 | Autumn | 15 | 6.37 | -8.8 | 2.23 | 50.5 | 37.5 | 2.25 | 0 | 2.25 | 8.8 | 54.8 | 29.09 | -52.55 | 0 | 0 | 0 | Battery-supported
2025-04-26 16:00 | 116 | 4 | Autumn | 16 | 6.37 | -13 | 4.46 | 38.5 | 0 | 0 | 0.12 | 0.12 | 13 | 55 | 15 | -35.23 | 19.65 | 6.925 | 0 | Diesel-backup
2025-04-26 17:00 | 116 | 4 | Autumn | 17 | 6.37 | -15 | 14.43 | 57.2 | 0 | 0 | 120 | 120 | 15 | 56.66 | 38.31 | 63.34 | 0 | 0 | 0 | Normal
2025-04-26 18:00 | 116 | 4 | Autumn | 18 | 6.37 | -12.7 | 8.8 | 81.6 | 0 | 0 | 20.84 | 20.84 | 12.7 | 61.78 | 21.93 | -40.94 | 0 | 0 | 0 | Battery-supported
2025-04-26 19:00 | 116 | 4 | Autumn | 19 | 6.37 | -15.8 | 3.62 | 77.8 | 0 | 0 | 0 | 0 | 15.8 | 52.31 | 15 | -17.33 | 34.98 | 11.641 | 0 | Diesel-backup
2025-04-26 20:00 | 116 | 4 | Autumn | 20 | 6.37 | -10.2 | 7.73 | 76.7 | 0 | 0 | 10.59 | 10.59 | 10.2 | 60.41 | 15 | 0 | 49.82 | 15.942 | 0 | Diesel-backup
2025-04-26 21:00 | 116 | 4 | Autumn | 21 | 6.37 | -15 | 20.58 | 55.7 | 0 | 0 | 120 | 120 | 15 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-04-26 22:00 | 116 | 4 | Autumn | 22 | 6.37 | -12.6 | 17.98 | 11.6 | 128.6 | 7.72 | 120 | 127.72 | 12.6 | 47.1 | 72.27 | 80.62 | 0 | 0 | 0 | Normal
2025-04-26 23:00 | 116 | 4 | Autumn | 23 | 6.37 | -11.6 | 32.47 | 33.2 | 320.8 | 19.25 | 0 | 19.25 | 11.6 | 48.06 | 60.74 | -28.81 | 0 | 0 | 0 | Battery-supported
2025-04-27 | 117 | 4 | Autumn | 0 | 6.19 | -13.6 | 13.14 | 89.5 | 211.5 | 12.69 | 120 | 132.69 | 13.6 | 52.51 | 90.25 | 80.18 | 0 | 0 | 0 | Normal
2025-04-27 01:00 | 117 | 4 | Autumn | 1 | 6.19 | -14.6 | 6.36 | 32.5 | 379 | 22.74 | 3.27 | 26.01 | 14.6 | 45 | 82.65 | -18.99 | 0 | 0 | 0 | Battery-supported
2025-04-27 02:00 | 117 | 4 | Autumn | 2 | 6.19 | -15.2 | 14.33 | 77.1 | 97.8 | 5.87 | 120 | 125.87 | 15.2 | 50.85 | 95 | 33.55 | 0 | 0 | 0 | Normal
2025-04-27 03:00 | 117 | 4 | Autumn | 3 | 6.19 | -15.7 | 5.52 | 60.7 | 0 | 0 | 1.15 | 1.15 | 15.7 | 48.23 | 76.17 | -47.08 | 0 | 0 | 0 | Battery-supported
2025-04-27 04:00 | 117 | 4 | Autumn | 4 | 6.19 | -17.2 | 8.17 | 14.9 | 0 | 0 | 14.25 | 14.25 | 17.2 | 56.17 | 59.4 | -41.92 | 0 | 0 | 0 | Battery-supported
2025-04-27 05:00 | 117 | 4 | Autumn | 5 | 6.19 | -17.3 | 5.55 | 66.3 | 0 | 0 | 1.21 | 1.21 | 17.3 | 49.78 | 39.97 | -48.57 | 0 | 0 | 0 | Battery-supported
2025-04-27 06:00 | 117 | 4 | Autumn | 6 | 6.19 | -13.3 | 13.11 | 50.7 | 0 | 0 | 120 | 120 | 13.3 | 45 | 67.57 | 75 | 0 | 0 | 0 | Normal
2025-04-27 07:00 | 117 | 4 | Autumn | 7 | 6.19 | -16.9 | 12.45 | 72.5 | 0 | 0 | 100.34 | 100.34 | 16.9 | 53.36 | 84.86 | 46.98 | 0 | 0 | 0 | Normal
2025-04-27 08:00 | 117 | 4 | Autumn | 8 | 6.19 | -18.4 | 5.86 | 57.4 | 0 | 0 | 1.84 | 1.84 | 18.4 | 61.27 | 61.09 | -59.43 | 0 | 0 | 0 | Battery-supported
2025-04-27 09:00 | 117 | 4 | Autumn | 9 | 6.19 | -17.8 | 16.23 | 87.7 | 10.9 | 0.65 | 120 | 120.65 | 17.8 | 67.9 | 80.5 | 52.75 | 0 | 0 | 0 | Normal
2025-04-27 10:00 | 117 | 4 | Autumn | 10 | 6.19 | -14.1 | 19.17 | 80.6 | 136.8 | 8.21 | 120 | 128.21 | 14.1 | 60.94 | 95 | 39.4 | 0 | 0 | 0 | Normal
2025-04-27 11:00 | 117 | 4 | Autumn | 11 | 6.19 | -14.8 | 6.4 | 55.1 | 336.5 | 20.19 | 3.41 | 23.6 | 14.8 | 54.28 | 82.73 | -30.68 | 0 | 0 | 0 | Battery-supported
2025-04-27 12:00 | 117 | 4 | Autumn | 12 | 6.19 | -14.7 | 11.15 | 89.5 | 215.5 | 12.93 | 62.66 | 75.59 | 14.7 | 61.59 | 87.88 | 14 | 0 | 0 | 0 | Normal
2025-04-27 13:00 | 117 | 4 | Autumn | 13 | 6.19 | -16.2 | 19.84 | 18.6 | 493.1 | 29.59 | 120 | 149.59 | 16.2 | 59.58 | 95 | 19.35 | 0 | 0 | 0 | Normal
2025-04-27 14:00 | 117 | 4 | Autumn | 14 | 6.19 | -13.9 | 10.58 | 34.4 | 256.8 | 15.41 | 49.67 | 65.08 | 13.9 | 59.75 | 95 | 0 | 0 | 0 | 0 | Normal
2025-04-27 15:00 | 117 | 4 | Autumn | 15 | 6.19 | -16.2 | 7.19 | 31.3 | 24.4 | 1.46 | 7.03 | 8.49 | 16.2 | 56.17 | 75.93 | -47.68 | 0 | 0 | 0 | Battery-supported
2025-04-27 16:00 | 117 | 4 | Autumn | 16 | 6.19 | -15 | 8.37 | 65.6 | 0 | 0 | 16.17 | 16.17 | 15 | 56.48 | 59.8 | -40.31 | 0 | 0 | 0 | Battery-supported
2025-04-27 17:00 | 117 | 4 | Autumn | 17 | 6.19 | -12 | 6.35 | 52.9 | 0 | 0 | 3.24 | 3.24 | 12 | 57.6 | 38.06 | -54.36 | 0 | 0 | 0 | Battery-supported
2025-04-27 18:00 | 117 | 4 | Autumn | 18 | 6.19 | -12 | 16.52 | 37.5 | 0 | 0 | 120 | 120 | 12 | 57.92 | 60.91 | 62.08 | 0 | 0 | 0 | Normal
2025-04-27 19:00 | 117 | 4 | Autumn | 19 | 6.19 | -15.9 | 15.38 | 26.6 | 0 | 0 | 120 | 120 | 15.9 | 50.47 | 86.49 | 69.53 | 0 | 0 | 0 | Normal
2025-04-27 20:00 | 117 | 4 | Autumn | 20 | 6.19 | -15.6 | 26.46 | 16 | 0 | 0 | 120 | 120 | 15.6 | 60.91 | 95 | 23.12 | 0 | 0 | 0 | Normal
2025-04-27 21:00 | 117 | 4 | Autumn | 21 | 6.19 | -13.5 | 5.43 | 69.5 | 0 | 0 | 1.01 | 1.01 | 13.5 | 45.12 | 77.36 | -44.11 | 0 | 0 | 0 | Battery-supported
2025-04-27 22:00 | 117 | 4 | Autumn | 22 | 6.19 | -10.1 | 6.1 | 36 | 169.4 | 10.16 | 2.46 | 12.62 | 10.1 | 46.04 | 63.99 | -33.42 | 0 | 0 | 0 | Battery-supported
2025-04-27 23:00 | 117 | 4 | Autumn | 23 | 6.19 | -18.4 | 3.16 | 40.1 | 350.1 | 17.86 | 0 | 17.86 | 18.4 | 46.78 | 52.42 | -28.92 | 0 | 0 | 0 | Battery-supported
2025-04-28 | 118 | 4 | Autumn | 0 | 6.01 | -14 | 12.08 | 12.6 | 593.7 | 35.62 | 88.4 | 124.02 | 14 | 52.53 | 78.73 | 71.49 | 0 | 0 | 0 | Normal
2025-04-28 01:00 | 118 | 4 | Autumn | 1 | 6.01 | -18 | 4.11 | 51.9 | 345.9 | 20.75 | 0.03 | 20.78 | 18 | 55.7 | 64.76 | -34.92 | 0 | 0 | 0 | Battery-supported
2025-04-28 02:00 | 118 | 4 | Autumn | 2 | 6.01 | -16.8 | 25.8 | 79.9 | 130.1 | 7.81 | 120 | 127.81 | 16.8 | 48.5 | 93.95 | 79.31 | 0 | 0 | 0 | Normal
2025-04-28 03:00 | 118 | 4 | Autumn | 3 | 6.01 | -16.6 | 5.07 | 30.9 | 0 | 0 | 0.54 | 0.54 | 16.6 | 53.21 | 72.88 | -52.67 | 0 | 0 | 0 | Battery-supported
2025-04-28 04:00 | 118 | 4 | Autumn | 4 | 6.01 | -17.1 | 2.12 | 56.8 | 0 | 0 | 0 | 0 | 17.1 | 51.95 | 52.1 | -51.95 | 0 | 0 | 0 | Battery-supported
2025-04-28 05:00 | 118 | 4 | Autumn | 5 | 6.01 | -17.6 | 4 | 32 | 0 | 0 | 0.02 | 0.02 | 17.6 | 55.02 | 30.1 | -55 | 0 | 0 | 0 | Battery-supported
2025-04-28 06:00 | 118 | 4 | Autumn | 6 | 6.01 | -16.7 | 10.43 | 45.5 | 0 | 0 | 46.58 | 46.58 | 16.7 | 46.16 | 30.25 | 0.42 | 0 | 0 | 0 | Normal
2025-04-28 07:00 | 118 | 4 | Autumn | 7 | 6.01 | -18 | 8.32 | 19.4 | 0 | 0 | 15.67 | 15.67 | 18 | 48.15 | 17.26 | -32.48 | 0 | 0 | 0 | Battery-supported
2025-04-28 08:00 | 118 | 4 | Autumn | 8 | 6.01 | -20.1 | 4.99 | 32.5 | 0 | 0 | 0.46 | 0.46 | 20.1 | 60.17 | 15 | -5.65 | 54.06 | 17.298 | 0 | Diesel-backup
2025-04-28 09:00 | 118 | 4 | Autumn | 9 | 6.01 | -15.1 | 8.07 | 38.9 | 0.8 | 0.05 | 13.36 | 13.41 | 15.1 | 57.89 | 15 | 0 | 44.48 | 14.263 | 0 | Diesel-backup
2025-04-28 10:00 | 118 | 4 | Autumn | 10 | 6.01 | -15.1 | 5.97 | 53.6 | 196.4 | 11.78 | 2.11 | 13.89 | 15.1 | 64.63 | 15 | 0 | 50.74 | 16.237 | 0 | Diesel-backup
2025-04-28 11:00 | 118 | 4 | Autumn | 11 | 6.01 | -14.6 | 11.91 | 7.9 | 534.4 | 32.06 | 83.25 | 115.31 | 14.6 | 58.29 | 35.98 | 57.02 | 0 | 0 | 0 | Normal
2025-04-28 12:00 | 118 | 4 | Autumn | 12 | 6.01 | -19.6 | 4.22 | 53.2 | 394.1 | 20.1 | 0.05 | 20.15 | 19.6 | 66.38 | 17.49 | -46.23 | 0 | 0 | 0 | Battery-supported
2025-04-28 13:00 | 118 | 4 | Autumn | 13 | 6.01 | -15.1 | 9.56 | 45.3 | 375.4 | 22.52 | 31.15 | 53.67 | 15.1 | 54.59 | 17.12 | -0.92 | 0 | 0 | 0 | Battery-supported
2025-04-28 14:00 | 118 | 4 | Autumn | 14 | 6.01 | -13.9 | 9.8 | 7.1 | 311.2 | 18.67 | 35 | 53.67 | 13.9 | 54.61 | 16.75 | -0.94 | 0 | 0 | 0 | Battery-supported
2025-04-28 15:00 | 118 | 4 | Autumn | 15 | 6.01 | -17.3 | 8.48 | 100 | 0.3 | 0.02 | 17.29 | 17.31 | 17.3 | 57.6 | 15 | -4.37 | 35.92 | 11.912 | 0 | Diesel-backup
2025-04-28 16:00 | 118 | 4 | Autumn | 16 | 6.01 | -14.6 | 11.09 | 63.1 | 0 | 0 | 61.2 | 61.2 | 14.6 | 56.81 | 16.62 | 4.39 | 0 | 0 | 0 | Normal
2025-04-28 17:00 | 118 | 4 | Autumn | 17 | 6.01 | -14.6 | 8.02 | 51.3 | 0 | 0 | 12.92 | 12.92 | 14.6 | 60.27 | 15 | -4.04 | 43.31 | 13.953 | 0 | Diesel-backup
2025-04-28 18:00 | 118 | 4 | Autumn | 18 | 6.01 | -10.1 | 13.08 | 78 | 0 | 0 | 120 | 120 | 10.1 | 51.76 | 40.11 | 68.24 | 0 | 0 | 0 | Normal
2025-04-28 19:00 | 118 | 4 | Autumn | 19 | 6.01 | -9.7 | 8.48 | 80.8 | 0 | 0 | 17.29 | 17.29 | 9.7 | 51.49 | 26.43 | -34.2 | 0 | 0 | 0 | Battery-supported
2025-04-28 20:00 | 118 | 4 | Autumn | 20 | 6.01 | -17.6 | 16.99 | 31.1 | 0 | 0 | 120 | 120 | 17.6 | 62.92 | 47.44 | 57.08 | 0 | 0 | 0 | Normal
2025-04-28 21:00 | 118 | 4 | Autumn | 21 | 6.01 | -8.5 | 9.53 | 35.1 | 0 | 0 | 30.69 | 30.69 | 8.5 | 45 | 41.71 | -14.31 | 0 | 0 | 0 | Battery-supported
2025-04-28 22:00 | 118 | 4 | Autumn | 22 | 6.01 | -16.1 | 16.38 | 12.8 | 293.5 | 17.61 | 120 | 137.61 | 16.1 | 48 | 74.69 | 89.61 | 0 | 0 | 0 | Normal
2025-04-28 23:00 | 118 | 4 | Autumn | 23 | 6.01 | -12.2 | 6.04 | 3.1 | 552.8 | 33.17 | 2.29 | 35.46 | 12.2 | 45.86 | 70.53 | -10.4 | 0 | 0 | 0 | Battery-supported
2025-04-29 | 119 | 4 | Autumn | 0 | 5.82 | -12.7 | 4.57 | 63.3 | 338 | 20.28 | 0.17 | 20.45 | 12.7 | 55 | 56.71 | -34.55 | 0 | 0 | 0 | Battery-supported
2025-04-29 01:00 | 119 | 4 | Autumn | 1 | 5.82 | -17.4 | 13.06 | 62.2 | 329.5 | 19.77 | 120 | 139.77 | 17.4 | 55.92 | 87.57 | 83.85 | 0 | 0 | 0 | Normal
2025-04-29 02:00 | 119 | 4 | Autumn | 2 | 5.82 | -14.5 | 8.6 | 48.3 | 265.2 | 15.91 | 18.57 | 34.48 | 14.5 | 57.09 | 78.52 | -22.61 | 0 | 0 | 0 | Battery-supported
2025-04-29 03:00 | 119 | 4 | Autumn | 3 | 5.82 | -16.2 | 1.59 | 44.7 | 63.7 | 3.82 | 0 | 3.82 | 16.2 | 45.99 | 61.66 | -42.17 | 0 | 0 | 0 | Battery-supported
2025-04-29 04:00 | 119 | 4 | Autumn | 4 | 5.82 | -15.1 | 5.39 | 0 | 0 | 0 | 0.94 | 0.94 | 15.1 | 51.66 | 41.37 | -50.72 | 0 | 0 | 0 | Battery-supported
2025-04-29 05:00 | 119 | 4 | Autumn | 5 | 5.82 | -16.2 | 10.49 | 63.6 | 0 | 0 | 47.8 | 47.8 | 16.2 | 49.71 | 40.6 | -1.91 | 0 | 0 | 0 | Battery-supported
2025-04-29 06:00 | 119 | 4 | Autumn | 6 | 5.82 | -14.3 | 8.15 | 90.6 | 0 | 0 | 14.07 | 14.07 | 14.3 | 48.05 | 27.01 | -33.98 | 0 | 0 | 0 | Battery-supported
2025-04-29 07:00 | 119 | 4 | Autumn | 7 | 5.82 | -16.9 | 5.24 | 47.5 | 0 | 0 | 0.74 | 0.74 | 16.9 | 45.74 | 15 | -30.03 | 14.97 | 5.367 | 0 | Diesel-backup
2025-04-29 08:00 | 119 | 4 | Autumn | 8 | 5.82 | -17.5 | 8.56 | 60.8 | 0 | 0 | 18.13 | 18.13 | 17.5 | 65.7 | 15 | 0 | 47.57 | 15.222 | 0 | Diesel-backup
2025-04-29 09:00 | 119 | 4 | Autumn | 9 | 5.82 | -14.7 | 9.42 | 79.6 | 0 | 0 | 29.04 | 29.04 | 14.7 | 51.21 | 15 | 0 | 22.17 | 7.742 | 0 | Diesel-backup
2025-04-29 10:00 | 119 | 4 | Autumn | 10 | 5.82 | -15.6 | 2.56 | 26.6 | 247.6 | 14.86 | 0 | 14.86 | 15.6 | 62.16 | 15 | 0 | 47.3 | 15.136 | 0 | Diesel-backup
2025-04-29 11:00 | 119 | 4 | Autumn | 11 | 5.82 | -15.1 | 16.18 | 89.1 | 186.7 | 11.2 | 120 | 131.2 | 15.1 | 56.52 | 42.48 | 74.68 | 0 | 0 | 0 | Normal
2025-04-29 12:00 | 119 | 4 | Autumn | 12 | 5.82 | -17.8 | 18.27 | 55.5 | 382.7 | 22.96 | 120 | 142.96 | 17.8 | 57.16 | 74.06 | 85.8 | 0 | 0 | 0 | Normal
2025-04-29 13:00 | 119 | 4 | Autumn | 13 | 5.82 | -18.3 | 5.37 | 35.5 | 413 | 21.06 | 0.92 | 21.98 | 18.3 | 57.48 | 59.86 | -35.5 | 0 | 0 | 0 | Battery-supported
2025-04-29 14:00 | 119 | 4 | Autumn | 14 | 5.82 | -16.9 | 23.57 | 78.1 | 128.2 | 7.69 | 120 | 127.69 | 16.9 | 60.1 | 84.73 | 67.59 | 0 | 0 | 0 | Normal
2025-04-29 15:00 | 119 | 4 | Autumn | 15 | 5.82 | -16.6 | 8.2 | 18.3 | 0 | 0 | 14.53 | 14.53 | 16.6 | 58.13 | 67.29 | -43.6 | 0 | 0 | 0 | Battery-supported
2025-04-29 16:00 | 119 | 4 | Autumn | 16 | 5.82 | -13.1 | 5.78 | 47.2 | 0 | 0 | 1.66 | 1.66 | 13.1 | 56.12 | 45.51 | -54.46 | 0 | 0 | 0 | Battery-supported
2025-04-29 17:00 | 119 | 4 | Autumn | 17 | 5.82 | -12.4 | 5.67 | 42.3 | 0 | 0 | 1.43 | 1.43 | 12.4 | 47.46 | 27.09 | -46.03 | 0 | 0 | 0 | Battery-supported
2025-04-29 18:00 | 119 | 4 | Autumn | 18 | 5.82 | -14.7 | 22.69 | 21.3 | 0 | 0 | 120 | 120 | 14.7 | 49.44 | 53.06 | 70.56 | 0 | 0 | 0 | Normal
2025-04-29 19:00 | 119 | 4 | Autumn | 19 | 5.82 | -11 | 4.29 | 19.1 | 0 | 0 | 0.07 | 0.07 | 11 | 46.72 | 34.4 | -46.65 | 0 | 0 | 0 | Battery-supported
2025-04-29 20:00 | 119 | 4 | Autumn | 20 | 5.82 | -11.1 | 9.54 | 39.1 | 0 | 0 | 30.84 | 30.84 | 11.1 | 57.31 | 23.81 | -26.47 | 0 | 0 | 0 | Battery-supported
2025-04-29 21:00 | 119 | 4 | Autumn | 21 | 5.82 | -13.6 | 10.23 | 55.2 | 56.2 | 3.37 | 42.66 | 46.03 | 13.6 | 54.39 | 20.47 | -8.36 | 0 | 0 | 0 | Battery-supported
2025-04-29 22:00 | 119 | 4 | Autumn | 22 | 5.82 | -16.1 | 13.12 | 30.8 | 319.8 | 19.19 | 120 | 139.19 | 16.1 | 50.05 | 53.27 | 89.14 | 0 | 0 | 0 | Normal
2025-04-29 23:00 | 119 | 4 | Autumn | 23 | 5.82 | -11.1 | 9.08 | 69 | 298 | 17.88 | 24.32 | 42.2 | 11.1 | 49.08 | 50.52 | -6.88 | 0 | 0 | 0 | Battery-supported
2025-04-30 | 120 | 4 | Autumn | 0 | 5.63 | -15.2 | 21.84 | 70.6 | 282.4 | 16.94 | 120 | 136.94 | 15.2 | 51.59 | 81.93 | 85.35 | 0 | 0 | 0 | Normal
2025-04-30 01:00 | 120 | 4 | Autumn | 1 | 5.63 | -15.1 | 24.17 | 53.6 | 388.3 | 23.3 | 120 | 143.3 | 15.1 | 54.78 | 95 | 35.52 | 0 | 0 | 0 | Normal
2025-04-30 02:00 | 120 | 4 | Autumn | 2 | 5.63 | -16.6 | 19.06 | 62.5 | 266 | 15.96 | 120 | 135.96 | 16.6 | 56.42 | 95 | 0 | 0 | 0 | 0 | Normal
2025-04-30 03:00 | 120 | 4 | Autumn | 3 | 5.63 | -18.2 | 10.87 | 22 | 167.6 | 8.55 | 56.03 | 64.58 | 18.2 | 48.26 | 95 | 0 | 0 | 0 | 0 | Normal
2025-04-30 04:00 | 120 | 4 | Autumn | 4 | 5.63 | -19.8 | 14.73 | 67.1 | 0 | 0 | 120 | 120 | 19.8 | 55.57 | 95 | 0 | 0 | 0 | 0 | Normal
2025-04-30 05:00 | 120 | 4 | Autumn | 5 | 5.63 | -15.5 | 7.2 | 72.9 | 0 | 0 | 7.09 | 7.09 | 15.5 | 53.93 | 76.26 | -46.84 | 0 | 0 | 0 | Battery-supported
2025-04-30 06:00 | 120 | 4 | Autumn | 6 | 5.63 | -18.8 | 16.58 | 47.6 | 0 | 0 | 120 | 120 | 18.8 | 57.24 | 95 | 50.91 | 0 | 0 | 0 | Normal
2025-04-30 07:00 | 120 | 4 | Autumn | 7 | 5.63 | -10.5 | 6.02 | 42.7 | 0 | 0 | 2.24 | 2.24 | 10.5 | 48.57 | 76.47 | -46.33 | 0 | 0 | 0 | Battery-supported
2025-04-30 08:00 | 120 | 4 | Autumn | 8 | 5.63 | -19.7 | 4.8 | 50.8 | 0 | 0 | 0.31 | 0.31 | 19.7 | 62.57 | 51.56 | -62.26 | 0 | 0 | 0 | Battery-supported
2025-04-30 09:00 | 120 | 4 | Autumn | 9 | 5.63 | -20 | 4.71 | 64.6 | 0 | 0 | 0.25 | 0.25 | 20 | 65.71 | 25.38 | -65.46 | 0 | 0 | 0 | Battery-supported
2025-04-30 10:00 | 120 | 4 | Autumn | 10 | 5.63 | -16 | 12.16 | 48.3 | 183.7 | 11.02 | 90.9 | 101.92 | 16 | 53.32 | 43.26 | 48.6 | 0 | 0 | 0 | Normal
2025-04-30 11:00 | 120 | 4 | Autumn | 11 | 5.63 | -13.5 | 20.34 | 73.9 | 248 | 14.88 | 120 | 134.88 | 13.5 | 51.01 | 74.13 | 83.87 | 0 | 0 | 0 | Normal
2025-04-30 12:00 | 120 | 4 | Autumn | 12 | 5.63 | -16.4 | 21.26 | 81.6 | 254.6 | 15.28 | 120 | 135.28 | 16.4 | 65.43 | 95 | 56.71 | 0 | 0 | 0 | Normal
2025-04-30 13:00 | 120 | 4 | Autumn | 13 | 5.63 | -14.9 | 1.7 | 57.7 | 315.6 | 18.94 | 0 | 18.94 | 14.9 | 62.25 | 77.68 | -43.31 | 0 | 0 | 0 | Battery-supported
2025-04-30 14:00 | 120 | 4 | Autumn | 14 | 5.63 | -19.9 | 15.25 | 79.5 | 116.2 | 5.93 | 120 | 125.93 | 19.9 | 69.23 | 95 | 47.08 | 0 | 0 | 0 | Normal
2025-04-30 15:00 | 120 | 4 | Autumn | 15 | 5.63 | -16.9 | 4.59 | 16.1 | 0 | 0 | 0.18 | 0.18 | 16.9 | 59.28 | 71.36 | -59.1 | 0 | 0 | 0 | Battery-supported
2025-04-30 16:00 | 120 | 4 | Autumn | 16 | 5.63 | -17.4 | 29.49 | 96.2 | 0 | 0 | 0 | 0 | 17.4 | 56.49 | 48.76 | -56.49 | 0 | 0 | 0 | Battery-supported
2025-04-30 17:00 | 120 | 4 | Autumn | 17 | 5.63 | -18.9 | 3.62 | 29.8 | 0 | 0 | 0 | 0 | 18.9 | 61.15 | 24.3 | -61.15 | 0 | 0 | 0 | Battery-supported
2025-04-30 18:00 | 120 | 4 | Autumn | 18 | 5.63 | -14.3 | 2.61 | 43.6 | 0 | 0 | 0 | 0 | 14.3 | 65.05 | 15 | -23.26 | 41.79 | 13.545 | 0 | Diesel-backup
2025-04-30 19:00 | 120 | 4 | Autumn | 19 | 5.63 | -19.3 | 15.43 | 32.8 | 0 | 0 | 120 | 120 | 19.3 | 58.95 | 37.47 | 61.05 | 0 | 0 | 0 | Normal
2025-04-30 20:00 | 120 | 4 | Autumn | 20 | 5.63 | -17.2 | 6.93 | 68.5 | 0 | 0 | 5.65 | 5.65 | 17.2 | 59.51 | 15.92 | -53.86 | 0 | 0 | 0 | Battery-supported
2025-04-30 21:00 | 120 | 4 | Autumn | 21 | 5.63 | -15.5 | 6.67 | 85.6 | 72 | 4.32 | 4.46 | 8.78 | 15.5 | 55.37 | 15 | -2.31 | 44.28 | 14.211 | 0 | Diesel-backup
2025-04-30 22:00 | 120 | 4 | Autumn | 22 | 5.63 | -16.3 | 5.34 | 52.5 | 303.8 | 18.23 | 0.87 | 19.1 | 16.3 | 51.62 | 15 | 0 | 32.52 | 10.926 | 0 | Diesel-backup
2025-04-30 23:00 | 120 | 4 | Autumn | 23 | 5.63 | -13.9 | 5.94 | 6.8 | 615.9 | 36.95 | 2.03 | 38.98 | 13.9 | 47.35 | 15 | 0 | 8.37 | 3.071 | 0 | Diesel-backup
2025-05-01 | 121 | 5 | Autumn | 0 | 5.43 | -14.6 | 15.87 | 75.2 | 226.8 | 13.61 | 120 | 133.61 | 14.6 | 52.62 | 44.8 | 80.99 | 0 | 0 | 0 | Normal
2025-05-01 01:00 | 121 | 5 | Autumn | 1 | 5.43 | -13.7 | 4.72 | 6.9 | 620.2 | 37.21 | 0.25 | 37.46 | 13.7 | 46.79 | 41.07 | -9.33 | 0 | 0 | 0 | Battery-supported
2025-05-01 02:00 | 121 | 5 | Autumn | 2 | 5.43 | -14.4 | 8.06 | 75.4 | 249.6 | 14.98 | 13.27 | 28.25 | 14.4 | 51.31 | 31.85 | -23.06 | 0 | 0 | 0 | Battery-supported
2025-05-01 03:00 | 121 | 5 | Autumn | 3 | 5.43 | -13.9 | 4.39 | 58.1 | 174.3 | 10.46 | 0.1 | 10.56 | 13.9 | 45 | 18.07 | -34.44 | 0 | 0 | 0 | Battery-supported
2025-05-01 04:00 | 121 | 5 | Autumn | 4 | 5.43 | -16.8 | 9.38 | 88.2 | 0 | 0 | 28.45 | 28.45 | 16.8 | 45 | 15 | -7.68 | 8.87 | 3.248 | 0 | Diesel-backup
2025-05-01 05:00 | 121 | 5 | Autumn | 5 | 5.43 | -16.4 | 6.62 | 62.9 | 0 | 0 | 4.25 | 4.25 | 16.4 | 50.47 | 15 | 0 | 46.22 | 14.79 | 0 | Diesel-backup
2025-05-01 06:00 | 121 | 5 | Autumn | 6 | 5.43 | -16.2 | 11.6 | 49.9 | 0 | 0 | 74.38 | 74.38 | 16.2 | 56.54 | 21.57 | 17.84 | 0 | 0 | 0 | Normal
2025-05-01 07:00 | 121 | 5 | Autumn | 7 | 5.43 | -17.2 | 12.5 | 39.6 | 0 | 0 | 102.03 | 102.03 | 17.2 | 51.54 | 40.15 | 50.49 | 0 | 0 | 0 | Normal
2025-05-01 08:00 | 121 | 5 | Autumn | 8 | 5.43 | -18.4 | 20.61 | 48.8 | 0 | 0 | 120 | 120 | 18.4 | 61.19 | 61.79 | 58.81 | 0 | 0 | 0 | Normal
2025-05-01 09:00 | 121 | 5 | Autumn | 9 | 5.43 | -18.2 | 28.51 | 51 | 0 | 0 | 0 | 0 | 18.2 | 62.2 | 36.91 | -62.2 | 0 | 0 | 0 | Battery-supported
2025-05-01 10:00 | 121 | 5 | Autumn | 10 | 5.43 | -19.1 | 5.72 | 49.1 | 167 | 8.52 | 1.53 | 10.05 | 19.1 | 60.45 | 16.75 | -50.4 | 0 | 0 | 0 | Battery-supported
2025-05-01 11:00 | 121 | 5 | Autumn | 11 | 5.43 | -16.1 | 13.35 | 63.6 | 287.5 | 17.25 | 120 | 137.25 | 16.1 | 52.66 | 47.88 | 84.59 | 0 | 0 | 0 | Normal
2025-05-01 12:00 | 121 | 5 | Autumn | 12 | 5.43 | -17 | 6.55 | 11.4 | 599.6 | 35.98 | 3.97 | 39.95 | 17 | 62.75 | 38.76 | -22.8 | 0 | 0 | 0 | Battery-supported
2025-05-01 13:00 | 121 | 5 | Autumn | 13 | 5.43 | -17.9 | 12.29 | 69.5 | 262.9 | 15.77 | 95.06 | 110.83 | 17.9 | 61.96 | 56.74 | 48.87 | 0 | 0 | 0 | Normal
2025-05-01 14:00 | 121 | 5 | Autumn | 14 | 5.43 | -17.5 | 11.98 | 95.3 | 75.3 | 4.52 | 85.35 | 89.87 | 17.5 | 61.87 | 67.04 | 28 | 0 | 0 | 0 | Normal
2025-05-01 15:00 | 121 | 5 | Autumn | 15 | 5.43 | -18.3 | 11.77 | 59.9 | 0 | 0 | 79.16 | 79.16 | 18.3 | 56.84 | 75.26 | 22.32 | 0 | 0 | 0 | Normal
2025-05-01 16:00 | 121 | 5 | Autumn | 16 | 5.43 | -13.1 | 13.95 | 73.3 | 0 | 0 | 120 | 120 | 13.1 | 62.21 | 95 | 53.65 | 0 | 0 | 0 | Normal
2025-05-01 17:00 | 121 | 5 | Autumn | 17 | 5.43 | -14.8 | 9.75 | 91.7 | 0 | 0 | 34.17 | 34.17 | 14.8 | 56.08 | 86.24 | -21.91 | 0 | 0 | 0 | Battery-supported
2025-05-01 18:00 | 121 | 5 | Autumn | 18 | 5.43 | -16.6 | 6.97 | 90.8 | 0 | 0 | 5.85 | 5.85 | 16.6 | 65.32 | 62.45 | -59.47 | 0 | 0 | 0 | Battery-supported
2025-05-01 19:00 | 121 | 5 | Autumn | 19 | 5.43 | -12.8 | 9.45 | 27.8 | 0 | 0 | 29.48 | 29.48 | 12.8 | 47.36 | 55.3 | -17.88 | 0 | 0 | 0 | Battery-supported
2025-05-01 20:00 | 121 | 5 | Autumn | 20 | 5.43 | -15.7 | 27.3 | 61.8 | 0 | 0 | 120 | 120 | 15.7 | 56.99 | 78.48 | 63.01 | 0 | 0 | 0 | Normal
2025-05-01 21:00 | 121 | 5 | Autumn | 21 | 5.43 | -17.7 | 6.15 | 19 | 265 | 15.9 | 2.6 | 18.5 | 17.7 | 58.79 | 62.37 | -40.29 | 0 | 0 | 0 | Battery-supported
2025-05-01 22:00 | 121 | 5 | Autumn | 22 | 5.43 | -12.5 | 7.32 | 59.5 | 318.5 | 19.11 | 7.8 | 26.91 | 12.5 | 46.93 | 54.36 | -20.02 | 0 | 0 | 0 | Battery-supported
2025-05-01 23:00 | 121 | 5 | Autumn | 23 | 5.43 | -16.1 | 5.44 | 10.4 | 602.8 | 36.17 | 1.02 | 37.19 | 16.1 | 45 | 51.24 | -7.81 | 0 | 0 | 0 | Battery-supported
2025-05-02 | 122 | 5 | Autumn | 0 | 5.24 | -16.4 | 2.26 | 52.5 | 242.4 | 14.54 | 0 | 14.54 | 16.4 | 47.56 | 38.03 | -33.02 | 0 | 0 | 0 | Battery-supported
2025-05-02 01:00 | 122 | 5 | Autumn | 1 | 5.24 | -15.7 | 8.54 | 93.7 | 185.5 | 11.13 | 17.92 | 29.05 | 15.7 | 51.82 | 28.92 | -22.77 | 0 | 0 | 0 | Battery-supported
2025-05-02 02:00 | 122 | 5 | Autumn | 2 | 5.24 | -13.7 | 12.82 | 58.8 | 351.8 | 21.11 | 113.31 | 134.42 | 13.7 | 54.44 | 58.35 | 79.98 | 0 | 0 | 0 | Normal
2025-05-02 03:00 | 122 | 5 | Autumn | 3 | 5.24 | -16.6 | 4.88 | 66.7 | 207.8 | 12.47 | 0.37 | 12.84 | 16.6 | 50.45 | 43.31 | -37.61 | 0 | 0 | 0 | Battery-supported
2025-05-02 04:00 | 122 | 5 | Autumn | 4 | 5.24 | -19.6 | 18.88 | 84.7 | 20.7 | 1.06 | 120 | 121.06 | 19.6 | 58.98 | 66.15 | 62.08 | 0 | 0 | 0 | Normal
2025-05-02 05:00 | 122 | 5 | Autumn | 5 | 5.24 | -16.1 | 11.43 | 71.6 | 0 | 0 | 69.8 | 69.8 | 16.1 | 52.68 | 72.45 | 17.12 | 0 | 0 | 0 | Normal
2025-05-02 06:00 | 122 | 5 | Autumn | 6 | 5.24 | -18.6 | 16.01 | 37.9 | 0 | 0 | 120 | 120 | 18.6 | 51.95 | 95 | 61.27 | 0 | 0 | 0 | Normal
2025-05-02 07:00 | 122 | 5 | Autumn | 7 | 5.24 | -13.5 | 10.8 | 13.6 | 0 | 0 | 54.45 | 54.45 | 13.5 | 51.65 | 95 | 0 | 0 | 0 | 0 | Normal
2025-05-02 08:00 | 122 | 5 | Autumn | 8 | 5.24 | -17.7 | 8.06 | 38 | 0 | 0 | 13.27 | 13.27 | 17.7 | 64.54 | 74.49 | -51.27 | 0 | 0 | 0 | Battery-supported
2025-05-02 09:00 | 122 | 5 | Autumn | 9 | 5.24 | -22.6 | 7.09 | 23.9 | 0 | 0 | 6.48 | 6.48 | 22.6 | 64.45 | 51.3 | -57.97 | 0 | 0 | 0 | Battery-supported
2025-05-02 10:00 | 122 | 5 | Autumn | 10 | 5.24 | -16.7 | 10.54 | 42.6 | 161.8 | 9.71 | 48.83 | 58.54 | 16.7 | 56.82 | 51.94 | 1.72 | 0 | 0 | 0 | Normal
2025-05-02 11:00 | 122 | 5 | Autumn | 11 | 5.24 | -13 | 11.1 | 50.9 | 334.5 | 20.07 | 61.44 | 81.51 | 13 | 49.53 | 63.71 | 31.98 | 0 | 0 | 0 | Normal
2025-05-02 12:00 | 122 | 5 | Autumn | 12 | 5.24 | -13.5 | 6.46 | 14.8 | 583 | 34.98 | 3.63 | 38.61 | 13.5 | 58.17 | 55.88 | -19.56 | 0 | 0 | 0 | Battery-supported
2025-05-02 13:00 | 122 | 5 | Autumn | 13 | 5.24 | -12.6 | 7.94 | 74 | 241 | 14.46 | 12.25 | 26.71 | 12.6 | 53.29 | 45.25 | -26.58 | 0 | 0 | 0 | Battery-supported
2025-05-02 14:00 | 122 | 5 | Autumn | 14 | 5.24 | -18.5 | 24.43 | 33.8 | 177.6 | 9.06 | 120 | 129.06 | 18.5 | 63.59 | 69.34 | 65.47 | 0 | 0 | 0 | Normal
2025-05-02 15:00 | 122 | 5 | Autumn | 15 | 5.24 | -13.8 | 9.59 | 45 | 0 | 0 | 31.61 | 31.61 | 13.8 | 57.97 | 58.8 | -26.36 | 0 | 0 | 0 | Battery-supported
2025-05-02 16:00 | 122 | 5 | Autumn | 16 | 5.24 | -17.1 | 10.18 | 69.7 | 0 | 0 | 41.72 | 41.72 | 17.1 | 61.51 | 50.88 | -19.79 | 0 | 0 | 0 | Battery-supported
2025-05-02 17:00 | 122 | 5 | Autumn | 17 | 5.24 | -14.7 | 21.12 | 29.5 | 0 | 0 | 120 | 120 | 14.7 | 57.04 | 74.05 | 62.96 | 0 | 0 | 0 | Normal
2025-05-02 18:00 | 122 | 5 | Autumn | 18 | 5.24 | -17.7 | 11.19 | 42.8 | 0 | 0 | 63.65 | 63.65 | 17.7 | 55.6 | 77.01 | 8.05 | 0 | 0 | 0 | Normal
2025-05-02 19:00 | 122 | 5 | Autumn | 19 | 5.24 | -16.2 | 8.87 | 43.7 | 0 | 0 | 21.67 | 21.67 | 16.2 | 61.09 | 61.25 | -39.42 | 0 | 0 | 0 | Battery-supported
2025-05-02 20:00 | 122 | 5 | Autumn | 20 | 5.24 | -16.2 | 15.75 | 44 | 38.1 | 2.29 | 120 | 122.29 | 16.2 | 62.55 | 83.23 | 59.74 | 0 | 0 | 0 | Normal
2025-05-02 21:00 | 122 | 5 | Autumn | 21 | 5.24 | -12.8 | 13.76 | 43.2 | 281.1 | 16.87 | 120 | 136.87 | 12.8 | 57.1 | 95 | 31.98 | 0 | 0 | 0 | Normal
2025-05-02 22:00 | 122 | 5 | Autumn | 22 | 5.24 | -13.2 | 10.33 | 70 | 299.1 | 17.95 | 44.59 | 62.54 | 13.2 | 45.82 | 95 | 0 | 0 | 0 | 0 | Normal
2025-05-02 23:00 | 122 | 5 | Autumn | 23 | 5.24 | -14.5 | 10.86 | 32.4 | 472 | 28.32 | 55.8 | 84.12 | 14.5 | 45.31 | 95 | 0 | 0 | 0 | 0 | Normal
2025-05-03 | 123 | 5 | Autumn | 0 | 5.04 | -18.6 | 7.51 | 52 | 143.5 | 7.32 | 9.02 | 16.34 | 18.6 | 48.93 | 81.96 | -32.59 | 0 | 0 | 0 | Battery-supported
2025-05-03 01:00 | 123 | 5 | Autumn | 1 | 5.04 | -16.7 | 4.2 | 33.8 | 409.5 | 24.57 | 0.05 | 24.62 | 16.7 | 51.5 | 71.21 | -26.88 | 0 | 0 | 0 | Battery-supported
2025-05-03 02:00 | 123 | 5 | Autumn | 2 | 5.04 | -18.1 | 12.67 | 59.8 | 361.6 | 18.44 | 107.92 | 126.36 | 18.1 | 56.31 | 95 | 64.64 | 0 | 0 | 0 | Normal
2025-05-03 03:00 | 123 | 5 | Autumn | 3 | 5.04 | -14.9 | 3.11 | 75.6 | 223.1 | 13.39 | 0 | 13.39 | 14.9 | 53.46 | 78.97 | -40.07 | 0 | 0 | 0 | Battery-supported
2025-05-03 04:00 | 123 | 5 | Autumn | 4 | 5.04 | -14.6 | 4.33 | 33.1 | 135.7 | 8.14 | 0.08 | 8.22 | 14.6 | 55.88 | 59.91 | -47.66 | 0 | 0 | 0 | Battery-supported
2025-05-03 05:00 | 123 | 5 | Autumn | 5 | 5.04 | -15.1 | 7.9 | 78 | 0 | 0 | 11.92 | 11.92 | 15.1 | 51.64 | 44.02 | -39.72 | 0 | 0 | 0 | Battery-supported
2025-05-03 06:00 | 123 | 5 | Autumn | 6 | 5.04 | -19.4 | 7.42 | 48.2 | 0 | 0 | 8.43 | 8.43 | 19.4 | 49.6 | 27.55 | -41.17 | 0 | 0 | 0 | Battery-supported
2025-05-03 07:00 | 123 | 5 | Autumn | 7 | 5.04 | -23.9 | 13.46 | 49 | 0 | 0 | 120 | 120 | 23.9 | 59.86 | 49.68 | 60.14 | 0 | 0 | 0 | Normal
2025-05-03 08:00 | 123 | 5 | Autumn | 8 | 5.04 | -21.8 | 15.5 | 65.2 | 0 | 0 | 120 | 120 | 21.8 | 56.4 | 73.09 | 63.6 | 0 | 0 | 0 | Normal
2025-05-03 09:00 | 123 | 5 | Autumn | 9 | 5.04 | -14.7 | 26.47 | 69.2 | 0 | 0 | 120 | 120 | 14.7 | 56.31 | 95 | 59.54 | 0 | 0 | 0 | Normal
2025-05-03 10:00 | 123 | 5 | Autumn | 10 | 5.04 | -18.6 | 2.77 | 56.5 | 120 | 6.12 | 0 | 6.12 | 18.6 | 59.9 | 73.49 | -53.78 | 0 | 0 | 0 | Battery-supported
2025-05-03 11:00 | 123 | 5 | Autumn | 11 | 5.04 | -19.1 | 11.81 | 38 | 380.5 | 19.41 | 80.32 | 99.73 | 19.1 | 63.94 | 86.66 | 35.79 | 0 | 0 | 0 | Normal
2025-05-03 12:00 | 123 | 5 | Autumn | 12 | 5.04 | -13.5 | 11.53 | 57.7 | 372.2 | 22.33 | 72.47 | 94.8 | 13.5 | 58.26 | 95 | 22.67 | 0 | 0 | 0 | Normal
2025-05-03 13:00 | 123 | 5 | Autumn | 13 | 5.04 | -14 | 10.7 | 78.2 | 220.2 | 13.21 | 52.24 | 65.45 | 14 | 54.04 | 95 | 0 | 0 | 0 | 0 | Normal
2025-05-03 14:00 | 123 | 5 | Autumn | 14 | 5.04 | -16.4 | 12.67 | 12.8 | 188.3 | 11.3 | 107.92 | 119.22 | 16.4 | 56.56 | 95 | 0 | 0 | 0 | 0 | Normal
2025-05-03 15:00 | 123 | 5 | Autumn | 15 | 5.04 | -16.7 | 14.22 | 83.1 | 0 | 0 | 120 | 120 | 16.7 | 59.96 | 95 | 0 | 0 | 0 | 0 | Normal
2025-05-03 16:00 | 123 | 5 | Autumn | 16 | 5.04 | -16 | 19.28 | 82 | 0 | 0 | 120 | 120 | 16 | 60.91 | 95 | 0 | 0 | 0 | 0 | Normal
2025-05-03 17:00 | 123 | 5 | Autumn | 17 | 5.04 | -14.9 | 10.89 | 92.5 | 0 | 0 | 56.49 | 56.49 | 14.9 | 60.84 | 93.26 | -4.35 | 0 | 0 | 0 | Battery-supported
2025-05-03 18:00 | 123 | 5 | Autumn | 18 | 5.04 | -11.6 | 22.6 | 89.9 | 0 | 0 | 120 | 120 | 11.6 | 52.66 | 95 | 4.73 | 0 | 0 | 0 | Normal
2025-05-03 19:00 | 123 | 5 | Autumn | 19 | 5.04 | -14 | 10.93 | 21.1 | 0 | 0 | 57.41 | 57.41 | 14 | 56.8 | 95 | 0 | 0 | 0 | 0 | Normal
2025-05-03 20:00 | 123 | 5 | Autumn | 20 | 5.04 | -13.3 | 6.79 | 71.7 | 83.5 | 5.01 | 4.98 | 9.99 | 13.3 | 52.13 | 78.14 | -42.14 | 0 | 0 | 0 | Battery-supported
2025-05-03 21:00 | 123 | 5 | Autumn | 21 | 5.04 | -12.4 | 10.36 | 40.2 | 359.8 | 21.59 | 45.18 | 66.77 | 12.4 | 45 | 86.16 | 21.77 | 0 | 0 | 0 | Normal
2025-05-03 22:00 | 123 | 5 | Autumn | 22 | 5.04 | -17.7 | 5.18 | 24.5 | 534.9 | 32.09 | 0.66 | 32.75 | 17.7 | 45 | 81.26 | -12.25 | 0 | 0 | 0 | Battery-supported
2025-05-03 23:00 | 123 | 5 | Autumn | 23 | 5.04 | -13.7 | 5.36 | 50.1 | 342.5 | 20.55 | 0.9 | 21.45 | 13.7 | 46.17 | 71.37 | -24.72 | 0 | 0 | 0 | Battery-supported
2025-05-04 | 124 | 5 | Autumn | 0 | 4.83 | -16.5 | 8.34 | 74.1 | 13.8 | 0.83 | 15.87 | 16.7 | 16.5 | 56.62 | 55.4 | -39.92 | 0 | 0 | 0 | Battery-supported
2025-05-04 01:00 | 124 | 5 | Autumn | 1 | 4.83 | -21.8 | 7.63 | 21.3 | 354.2 | 18.06 | 9.86 | 27.92 | 21.8 | 62.47 | 41.58 | -34.55 | 0 | 0 | 0 | Battery-supported
2025-05-04 02:00 | 124 | 5 | Autumn | 2 | 4.83 | -21.3 | 19.04 | 72.4 | 292.5 | 14.92 | 120 | 134.92 | 21.3 | 58.57 | 69.68 | 76.35 | 0 | 0 | 0 | Normal
2025-05-04 03:00 | 124 | 5 | Autumn | 3 | 4.83 | -19.2 | 8.28 | 21.7 | 499.5 | 25.47 | 15.29 | 40.76 | 19.2 | 58.22 | 62.69 | -17.46 | 0 | 0 | 0 | Battery-supported
2025-05-04 04:00 | 124 | 5 | Autumn | 4 | 4.83 | -16.2 | 4.71 | 1.9 | 305.3 | 18.32 | 0.25 | 18.57 | 16.2 | 54.44 | 48.34 | -35.87 | 0 | 0 | 0 | Battery-supported
2025-05-04 05:00 | 124 | 5 | Autumn | 5 | 4.83 | -17.4 | 9.27 | 51 | 0 | 0 | 26.89 | 26.89 | 17.4 | 53.09 | 37.86 | -26.2 | 0 | 0 | 0 | Battery-supported
2025-05-04 06:00 | 124 | 5 | Autumn | 6 | 4.83 | -17.5 | 10.9 | 50.2 | 0 | 0 | 56.72 | 56.72 | 17.5 | 45 | 42.18 | 11.72 | 0 | 0 | 0 | Normal
2025-05-04 07:00 | 124 | 5 | Autumn | 7 | 4.83 | -13.8 | 9.87 | 44.7 | 0 | 0 | 36.18 | 36.18 | 13.8 | 57.86 | 33.51 | -21.68 | 0 | 0 | 0 | Battery-supported
2025-05-04 08:00 | 124 | 5 | Autumn | 8 | 4.83 | -20.9 | 4.56 | 27.9 | 0 | 0 | 0.17 | 0.17 | 20.9 | 63.07 | 15 | -46.26 | 16.64 | 5.928 | 0 | Diesel-backup
2025-05-04 09:00 | 124 | 5 | Autumn | 9 | 4.83 | -18.1 | 20.21 | 86 | 0 | 0 | 120 | 120 | 18.1 | 60.25 | 36.99 | 59.75 | 0 | 0 | 0 | Normal
2025-05-04 10:00 | 124 | 5 | Autumn | 10 | 4.83 | -17.2 | 2.55 | 33.8 | 130.5 | 7.83 | 0 | 7.83 | 17.2 | 66.04 | 15 | -54.97 | 3.24 | 1.21 | 0 | Diesel-backup
2025-05-04 11:00 | 124 | 5 | Autumn | 11 | 4.83 | -19.3 | 9.78 | 66.4 | 262.2 | 13.37 | 34.66 | 48.03 | 19.3 | 62.94 | 15 | 0 | 14.91 | 5.345 | 0 | Diesel-backup
2025-05-04 12:00 | 124 | 5 | Autumn | 12 | 4.83 | -17.3 | 4.46 | 67.9 | 322.1 | 19.33 | 0.12 | 19.45 | 17.3 | 70.37 | 15 | 0 | 50.92 | 16.294 | 0 | Diesel-backup
2025-05-04 13:00 | 124 | 5 | Autumn | 13 | 4.83 | -20.5 | 16.38 | 9.1 | 486.5 | 24.81 | 120 | 144.81 | 20.5 | 60.18 | 46.14 | 84.63 | 0 | 0 | 0 | Normal
2025-05-04 14:00 | 124 | 5 | Autumn | 14 | 4.83 | -13.5 | 11.88 | 42.1 | 119.6 | 7.18 | 82.36 | 89.54 | 13.5 | 60.65 | 56.78 | 28.89 | 0 | 0 | 0 | Normal
2025-05-04 15:00 | 124 | 5 | Autumn | 15 | 4.83 | -17.7 | 10.9 | 81.2 | 0 | 0 | 56.72 | 56.72 | 17.7 | 59.72 | 55.58 | -3 | 0 | 0 | 0 | Battery-supported
2025-05-04 16:00 | 124 | 5 | Autumn | 16 | 4.83 | -11.4 | 7.89 | 43.9 | 0 | 0 | 11.84 | 11.84 | 11.4 | 54.8 | 38.39 | -42.96 | 0 | 0 | 0 | Battery-supported
2025-05-04 17:00 | 124 | 5 | Autumn | 17 | 4.83 | -15.6 | 19.22 | 89.9 | 0 | 0 | 120 | 120 | 15.6 | 55.08 | 62.28 | 64.92 | 0 | 0 | 0 | Normal
2025-05-04 18:00 | 124 | 5 | Autumn | 18 | 4.83 | -13 | 7.88 | 63.9 | 0 | 0 | 11.76 | 11.76 | 13 | 53.48 | 45.59 | -41.72 | 0 | 0 | 0 | Battery-supported
2025-05-04 19:00 | 124 | 5 | Autumn | 19 | 4.83 | -15.3 | 23.81 | 11.9 | 0 | 0 | 120 | 120 | 15.3 | 63.46 | 66.4 | 56.54 | 0 | 0 | 0 | Normal
2025-05-04 20:00 | 124 | 5 | Autumn | 20 | 4.83 | -15.2 | 5.28 | 74.4 | 136.9 | 8.21 | 0.79 | 9 | 15.2 | 60.27 | 45.89 | -51.27 | 0 | 0 | 0 | Battery-supported
2025-05-04 21:00 | 124 | 5 | Autumn | 21 | 4.83 | -16.4 | 9.31 | 17.2 | 519.9 | 31.19 | 27.45 | 58.64 | 16.4 | 53.09 | 47.94 | 5.55 | 0 | 0 | 0 | Normal
2025-05-04 22:00 | 124 | 5 | Autumn | 22 | 4.83 | -15 | 14.05 | 52.7 | 387 | 23.22 | 120 | 143.22 | 15 | 45 | 84.08 | 98.22 | 0 | 0 | 0 | Normal
2025-05-04 23:00 | 124 | 5 | Autumn | 23 | 4.83 | -14.8 | 12.36 | 23.6 | 346.8 | 20.81 | 97.34 | 118.15 | 14.8 | 45 | 95 | 29.67 | 0 | 0 | 0 | Normal
2025-05-05 | 125 | 5 | Autumn | 0 | 4.62 | -17.8 | 8.9 | 51.6 | 0 | 0 | 22.04 | 22.04 | 17.8 | 49.11 | 84.17 | -27.07 | 0 | 0 | 0 | Battery-supported
2025-05-05 01:00 | 125 | 5 | Autumn | 1 | 4.62 | -16.7 | 2.82 | 21.6 | 199.1 | 11.95 | 0 | 11.95 | 16.7 | 50.12 | 68.9 | -38.17 | 0 | 0 | 0 | Battery-supported
2025-05-05 02:00 | 125 | 5 | Autumn | 2 | 4.62 | -18.1 | 10.21 | 54.3 | 337.4 | 17.21 | 42.28 | 59.49 | 18.1 | 52.69 | 71.41 | 6.8 | 0 | 0 | 0 | Normal
2025-05-05 03:00 | 125 | 5 | Autumn | 3 | 4.62 | -12.1 | 7.33 | 80.4 | 256.9 | 15.41 | 7.86 | 23.27 | 12.1 | 48.37 | 61.37 | -25.1 | 0 | 0 | 0 | Battery-supported
2025-05-05 04:00 | 125 | 5 | Autumn | 4 | 4.62 | -17.8 | 6.26 | 40.2 | 305.7 | 18.34 | 2.94 | 21.28 | 17.8 | 56.89 | 47.12 | -35.61 | 0 | 0 | 0 | Battery-supported
2025-05-05 05:00 | 125 | 5 | Autumn | 5 | 4.62 | -14.5 | 14.57 | 35.9 | 23.8 | 1.43 | 120 | 121.43 | 14.5 | 55.38 | 71.43 | 66.05 | 0 | 0 | 0 | Normal
2025-05-05 06:00 | 125 | 5 | Autumn | 6 | 4.62 | -18.5 | 2.39 | 56.9 | 0 | 0 | 0 | 0 | 18.5 | 54.28 | 49.72 | -54.28 | 0 | 0 | 0 | Battery-supported
2025-05-05 07:00 | 125 | 5 | Autumn | 7 | 4.62 | -17.7 | 9.1 | 17.5 | 0 | 0 | 24.58 | 24.58 | 17.7 | 49.32 | 39.82 | -24.74 | 0 | 0 | 0 | Battery-supported
2025-05-05 08:00 | 125 | 5 | Autumn | 8 | 4.62 | -21.2 | 1.11 | 21.4 | 0 | 0 | 0 | 0 | 21.2 | 67.12 | 15 | -62.05 | 5.07 | 1.881 | 0 | Diesel-backup
2025-05-05 09:00 | 125 | 5 | Autumn | 9 | 4.62 | -19.2 | 12.45 | 24.4 | 0 | 0 | 100.34 | 100.34 | 19.2 | 62.94 | 28.76 | 37.4 | 0 | 0 | 0 | Normal
2025-05-05 10:00 | 125 | 5 | Autumn | 10 | 4.62 | -17.6 | 14.66 | 53.9 | 81.5 | 4.89 | 120 | 124.89 | 17.6 | 62.47 | 51.73 | 62.42 | 0 | 0 | 0 | Normal
2025-05-05 11:00 | 125 | 5 | Autumn | 11 | 4.62 | -14.4 | 10.12 | 29 | 399.1 | 23.95 | 40.61 | 64.56 | 14.4 | 62.22 | 52.59 | 2.34 | 0 | 0 | 0 | Normal
2025-05-05 12:00 | 125 | 5 | Autumn | 12 | 4.62 | -17.1 | 6.9 | 41.2 | 453.2 | 27.19 | 5.5 | 32.69 | 17.1 | 58.55 | 42.25 | -25.86 | 0 | 0 | 0 | Battery-supported
2025-05-05 13:00 | 125 | 5 | Autumn | 13 | 4.62 | -14.2 | 19.12 | 64.1 | 264.7 | 15.88 | 120 | 135.88 | 14.2 | 63.02 | 69.06 | 72.86 | 0 | 0 | 0 | Normal
2025-05-05 14:00 | 125 | 5 | Autumn | 14 | 4.62 | -15.4 | 19.85 | 66 | 69.1 | 4.15 | 120 | 124.15 | 15.4 | 52.7 | 95 | 70.48 | 0 | 0 | 0 | Normal
2025-05-05 15:00 | 125 | 5 | Autumn | 15 | 4.62 | -12.8 | 11.28 | 29 | 0 | 0 | 65.91 | 65.91 | 12.8 | 58.71 | 95 | 0 | 0 | 0 | 0 | Normal
2025-05-05 16:00 | 125 | 5 | Autumn | 16 | 4.62 | -16.2 | 21.55 | 8.1 | 0 | 0 | 120 | 120 | 16.2 | 56.6 | 95 | 0 | 0 | 0 | 0 | Normal
2025-05-05 17:00 | 125 | 5 | Autumn | 17 | 4.62 | -10.5 | 5.29 | 69.6 | 0 | 0 | 0.8 | 0.8 | 10.5 | 54.4 | 73.56 | -53.6 | 0 | 0 | 0 | Battery-supported
2025-05-05 18:00 | 125 | 5 | Autumn | 18 | 4.62 | -16.6 | 8.56 | 90 | 0 | 0 | 18.13 | 18.13 | 16.6 | 60.92 | 56.44 | -42.79 | 0 | 0 | 0 | Battery-supported
2025-05-05 19:00 | 125 | 5 | Autumn | 19 | 4.62 | -17 | 1.58 | 52.1 | 19.9 | 1.19 | 0 | 1.19 | 17 | 58.6 | 33.48 | -57.41 | 0 | 0 | 0 | Battery-supported
2025-05-05 20:00 | 125 | 5 | Autumn | 20 | 4.62 | -18 | 4.26 | 30 | 338.9 | 20.33 | 0.06 | 20.39 | 18 | 58.43 | 18.26 | -38.04 | 0 | 0 | 0 | Battery-supported
2025-05-05 21:00 | 125 | 5 | Autumn | 21 | 4.62 | -10.2 | 4 | 8.2 | 607.9 | 36.47 | 0.02 | 36.49 | 10.2 | 45 | 15 | -8.16 | 0.35 | 0.132 | 0 | Diesel-backup
2025-05-05 22:00 | 125 | 5 | Autumn | 22 | 4.62 | -13.7 | 12.41 | 97.2 | 154.1 | 9.25 | 99 | 108.25 | 13.7 | 49.85 | 36.49 | 58.4 | 0 | 0 | 0 | Normal
2025-05-05 23:00 | 125 | 5 | Autumn | 23 | 4.62 | -16.5 | 4.46 | 84.9 | 86.3 | 5.18 | 0.12 | 5.3 | 16.5 | 54.04 | 17 | -48.74 | 0 | 0 | 0 | Battery-supported
2025-05-06 | 126 | 5 | Autumn | 0 | 4.4 | -13.5 | 2.28 | 60.2 | 0 | 0 | 0 | 0 | 13.5 | 55.78 | 15 | -4.99 | 50.79 | 16.253 | 0 | Diesel-backup
2025-05-06 01:00 | 126 | 5 | Autumn | 1 | 4.4 | -15.1 | 5.97 | 62.3 | 0.5 | 0.03 | 2.11 | 2.14 | 15.1 | 49.08 | 15 | 0 | 46.94 | 15.021 | 0 | Diesel-backup
2025-05-06 02:00 | 126 | 5 | Autumn | 2 | 4.4 | -12.7 | 6.47 | 70.2 | 203.8 | 12.23 | 3.67 | 15.9 | 12.7 | 45 | 15 | 0 | 29.1 | 9.904 | 0 | Diesel-backup
2025-05-06 03:00 | 126 | 5 | Autumn | 3 | 4.4 | -20.8 | 3.7 | 23.7 | 533.8 | 27.22 | 0 | 27.22 | 20.8 | 57.69 | 15 | 0 | 30.47 | 10.317 | 0 | Diesel-backup
2025-05-06 04:00 | 126 | 5 | Autumn | 4 | 4.4 | -18.3 | 9.69 | 91.2 | 174.1 | 8.88 | 33.2 | 42.08 | 18.3 | 46.34 | 15 | 0 | 4.26 | 1.585 | 0 | Diesel-backup
2025-05-06 05:00 | 126 | 5 | Autumn | 5 | 4.4 | -19.1 | 10.77 | 47.9 | 118 | 6.02 | 53.78 | 59.8 | 19.1 | 60.51 | 15 | 0 | 0.71 | 0.267 | 0 | Diesel-backup
2025-05-06 06:00 | 126 | 5 | Autumn | 6 | 4.4 | -22.6 | 3.08 | 46.9 | 0 | 0 | 0 | 0 | 22.6 | 60.63 | 15 | 0 | 60.63 | 19.402 | 0 | Diesel-backup
2025-05-06 07:00 | 126 | 5 | Autumn | 7 | 4.4 | -16.1 | 13.57 | 33.7 | 0 | 0 | 120 | 120 | 16.1 | 47.07 | 41.84 | 72.93 | 0 | 0 | 0 | Normal
2025-05-06 08:00 | 126 | 5 | Autumn | 8 | 4.4 | -19.1 | 5.06 | 58.8 | 0 | 0 | 0.53 | 0.53 | 19.1 | 55.76 | 19.75 | -55.23 | 0 | 0 | 0 | Battery-supported
2025-05-06 09:00 | 126 | 5 | Autumn | 9 | 4.4 | -16.8 | 6.4 | 79.1 | 0 | 0 | 3.41 | 3.41 | 16.8 | 56.35 | 15 | -11.87 | 41.07 | 13.35 | 0 | Diesel-backup
2025-05-06 10:00 | 126 | 5 | Autumn | 10 | 4.4 | -13.1 | 12.01 | 38.7 | 66.4 | 3.98 | 86.26 | 90.24 | 13.1 | 58.22 | 26.78 | 32.02 | 0 | 0 | 0 | Normal
2025-05-06 11:00 | 126 | 5 | Autumn | 11 | 4.4 | -18.8 | 6.44 | 20.2 | 420.7 | 21.46 | 3.56 | 25.02 | 18.8 | 58.72 | 15 | -29.46 | 4.24 | 1.579 | 0 | Diesel-backup
2025-05-06 12:00 | 126 | 5 | Autumn | 12 | 4.4 | -18.7 | 4.32 | 28.4 | 516.3 | 26.33 | 0.08 | 26.41 | 18.7 | 64.67 | 15 | 0 | 38.26 | 12.573 | 0 | Diesel-backup
2025-05-06 13:00 | 126 | 5 | Autumn | 13 | 4.4 | -17.1 | 9.36 | 91.6 | 155.3 | 9.32 | 28.16 | 37.48 | 17.1 | 63.85 | 15 | 0 | 26.37 | 9.067 | 0 | Diesel-backup
2025-05-06 14:00 | 126 | 5 | Autumn | 14 | 4.4 | -14.8 | 16.59 | 61.4 | 50.5 | 3.03 | 120 | 123.03 | 14.8 | 55.51 | 39.85 | 67.52 | 0 | 0 | 0 | Normal
2025-05-06 15:00 | 126 | 5 | Autumn | 15 | 4.4 | -17.9 | 15.45 | 73.2 | 0 | 0 | 120 | 120 | 17.9 | 64.43 | 60.3 | 55.57 | 0 | 0 | 0 | Normal
2025-05-06 16:00 | 126 | 5 | Autumn | 16 | 4.4 | -17.6 | 6.05 | 65.8 | 0 | 0 | 2.32 | 2.32 | 17.6 | 65.43 | 35.05 | -63.11 | 0 | 0 | 0 | Battery-supported
2025-05-06 17:00 | 126 | 5 | Autumn | 17 | 4.4 | -13.6 | 4.82 | 15 | 0 | 0 | 0.32 | 0.32 | 13.6 | 58.86 | 15 | -50.13 | 8.41 | 3.084 | 0 | Diesel-backup
2025-05-06 18:00 | 126 | 5 | Autumn | 18 | 4.4 | -14.9 | 5.5 | 81.1 | 0 | 0 | 1.12 | 1.12 | 14.9 | 60.08 | 15 | 0 | 58.96 | 18.867 | 0 | Diesel-backup
2025-05-06 19:00 | 126 | 5 | Autumn | 19 | 4.4 | -20.1 | 15.54 | 70.5 | 86.8 | 4.43 | 120 | 124.43 | 20.1 | 60.85 | 38.4 | 63.58 | 0 | 0 | 0 | Normal
2025-05-06 20:00 | 126 | 5 | Autumn | 20 | 4.4 | -18.2 | 5.44 | 23.1 | 455.9 | 23.25 | 1.02 | 24.27 | 18.2 | 69.32 | 20.38 | -45.05 | 0 | 0 | 0 | Battery-supported
2025-05-06 21:00 | 126 | 5 | Autumn | 21 | 4.4 | -12.3 | 21.01 | 88.2 | 219.8 | 13.19 | 120 | 133.19 | 12.3 | 45 | 52.83 | 88.19 | 0 | 0 | 0 | Normal
2025-05-06 22:00 | 126 | 5 | Autumn | 22 | 4.4 | -14.8 | 11.92 | 31.6 | 328.2 | 19.69 | 83.55 | 103.24 | 14.8 | 48.03 | 73.15 | 55.21 | 0 | 0 | 0 | Normal
2025-05-06 23:00 | 126 | 5 | Autumn | 23 | 4.4 | -17.6 | 8.72 | 30 | 0.7 | 0.04 | 19.91 | 19.95 | 17.6 | 56.35 | 58.59 | -36.4 | 0 | 0 | 0 | Battery-supported
2025-05-07 | 127 | 5 | Autumn | 0 | 4.18 | -16.8 | 6.01 | 1.7 | 0 | 0 | 2.21 | 2.21 | 16.8 | 50.3 | 39.35 | -48.09 | 0 | 0 | 0 | Battery-supported
2025-05-07 01:00 | 127 | 5 | Autumn | 1 | 4.18 | -16.8 | 9.46 | 29.6 | 0 | 0 | 29.63 | 29.63 | 16.8 | 50.6 | 30.96 | -20.97 | 0 | 0 | 0 | Battery-supported
2025-05-07 02:00 | 127 | 5 | Autumn | 2 | 4.18 | -15.6 | 4.31 | 74.5 | 94.4 | 5.66 | 0.07 | 5.73 | 15.6 | 45.16 | 15.19 | -39.43 | 0 | 0 | 0 | Battery-supported
2025-05-07 03:00 | 127 | 5 | Autumn | 3 | 4.18 | -20.6 | 3.16 | 35.2 | 426.9 | 21.77 | 0 | 21.77 | 20.6 | 53.72 | 15 | -0.48 | 31.47 | 10.615 | 0 | Diesel-backup
2025-05-07 04:00 | 127 | 5 | Autumn | 4 | 4.18 | -19.8 | 12.02 | 70.6 | 297.7 | 15.18 | 86.56 | 101.74 | 19.8 | 64.46 | 28.72 | 37.28 | 0 | 0 | 0 | Normal
2025-05-07 05:00 | 127 | 5 | Autumn | 5 | 4.18 | -17.7 | 8.72 | 54.2 | 204.4 | 12.26 | 19.91 | 32.17 | 17.7 | 51.26 | 21.08 | -19.09 | 0 | 0 | 0 | Battery-supported
2025-05-07 06:00 | 127 | 5 | Autumn | 6 | 4.18 | -18.7 | 13.9 | 33.7 | 0 | 0 | 120 | 120 | 18.7 | 58.82 | 43.6 | 61.18 | 0 | 0 | 0 | Normal
2025-05-07 07:00 | 127 | 5 | Autumn | 7 | 4.18 | -17.4 | 10.6 | 40.3 | 0 | 0 | 50.09 | 50.09 | 17.4 | 50.4 | 43.47 | -0.31 | 0 | 0 | 0 | Battery-supported
2025-05-07 08:00 | 127 | 5 | Autumn | 8 | 4.18 | -21.4 | 5.95 | 54 | 0 | 0 | 2.06 | 2.06 | 21.4 | 60.14 | 20.24 | -58.08 | 0 | 0 | 0 | Battery-supported
2025-05-07 09:00 | 127 | 5 | Autumn | 9 | 4.18 | -17.9 | 15.49 | 39.2 | 0 | 0 | 120 | 120 | 17.9 | 57.78 | 43.14 | 62.22 | 0 | 0 | 0 | Normal
2025-05-07 10:00 | 127 | 5 | Autumn | 10 | 4.18 | -16.1 | 6.41 | 3.1 | 42.6 | 2.56 | 3.45 | 6.01 | 16.1 | 62 | 20.74 | -55.99 | 0 | 0 | 0 | Battery-supported
2025-05-07 11:00 | 127 | 5 | Autumn | 11 | 4.18 | -17.2 | 18 | 45.5 | 315.4 | 18.92 | 120 | 138.92 | 17.2 | 51.47 | 52.92 | 87.45 | 0 | 0 | 0 | Normal
2025-05-07 12:00 | 127 | 5 | Autumn | 12 | 4.18 | -17.6 | 6.28 | 92.8 | 199.4 | 11.96 | 3.01 | 14.97 | 17.6 | 67.42 | 31.94 | -52.45 | 0 | 0 | 0 | Battery-supported
2025-05-07 13:00 | 127 | 5 | Autumn | 13 | 4.18 | -17.8 | 3.54 | 74.5 | 211.3 | 12.68 | 0 | 12.68 | 17.8 | 62.71 | 15 | -42.36 | 7.67 | 2.821 | 0 | Diesel-backup
2025-05-07 14:00 | 127 | 5 | Autumn | 14 | 4.18 | -19 | 19.85 | 56.8 | 25 | 1.27 | 120 | 121.27 | 19 | 60.5 | 37.36 | 60.77 | 0 | 0 | 0 | Normal
2025-05-07 15:00 | 127 | 5 | Autumn | 15 | 4.18 | -17 | 6.14 | 79.6 | 0 | 0 | 2.58 | 2.58 | 17 | 56.83 | 15.66 | -54.25 | 0 | 0 | 0 | Battery-supported
2025-05-07 16:00 | 127 | 5 | Autumn | 16 | 4.18 | -13.7 | 6.42 | 63.1 | 0 | 0 | 3.48 | 3.48 | 13.7 | 54.61 | 15 | -1.66 | 49.47 | 15.831 | 0 | Diesel-backup
2025-05-07 17:00 | 127 | 5 | Autumn | 17 | 4.18 | -16.4 | 3.65 | 58.2 | 0 | 0 | 0 | 0 | 16.4 | 64 | 15 | 0 | 64 | 20.48 | 0 | Diesel-backup
2025-05-07 18:00 | 127 | 5 | Autumn | 18 | 4.18 | -17.9 | 8.29 | 63.5 | 0 | 0 | 15.38 | 15.38 | 17.9 | 54.59 | 15 | 0 | 39.21 | 12.838 | 0 | Diesel-backup
2025-05-07 19:00 | 127 | 5 | Autumn | 19 | 4.18 | -16.8 | 3.99 | 28.1 | 271.7 | 16.3 | 0.02 | 16.32 | 16.8 | 59.58 | 15 | 0 | 43.26 | 13.94 | 0 | Diesel-backup
2025-05-07 20:00 | 127 | 5 | Autumn | 20 | 4.18 | -15.3 | 19.19 | 100 | 158.2 | 9.49 | 120 | 129.49 | 15.3 | 62.82 | 39.53 | 66.67 | 0 | 0 | 0 | Normal
2025-05-07 21:00 | 127 | 5 | Autumn | 21 | 4.18 | -16.6 | 7.04 | 66.7 | 290 | 17.4 | 6.21 | 23.61 | 16.6 | 45 | 30.98 | -21.39 | 0 | 0 | 0 | Battery-supported
2025-05-07 22:00 | 127 | 5 | Autumn | 22 | 4.18 | -14.8 | 4.89 | 42 | 146.6 | 8.8 | 0.38 | 9.18 | 14.8 | 47.29 | 15.73 | -38.11 | 0 | 0 | 0 | Battery-supported
2025-05-07 23:00 | 127 | 5 | Autumn | 23 | 4.18 | -15 | 9.18 | 75.8 | 0 | 0 | 25.65 | 25.65 | 15 | 45 | 15 | -1.84 | 17.51 | 6.221 | 0 | Diesel-backup
2025-05-08 | 128 | 5 | Autumn | 0 | 3.94 | -14.7 | 28.78 | 18.2 | 0 | 0 | 0 | 0 | 14.7 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-05-08 01:00 | 128 | 5 | Autumn | 1 | 3.94 | -13.9 | 9.46 | 48.8 | 0 | 0 | 29.63 | 29.63 | 13.9 | 49.77 | 15 | 0 | 20.14 | 7.086 | 0 | Diesel-backup
2025-05-08 02:00 | 128 | 5 | Autumn | 2 | 3.94 | -15.2 | 7.69 | 28.1 | 0 | 0 | 10.3 | 10.3 | 15.2 | 52.8 | 15 | 0 | 42.5 | 13.736 | 0 | Diesel-backup
2025-05-08 03:00 | 128 | 5 | Autumn | 3 | 3.94 | -19.8 | 9.08 | 36.1 | 303.4 | 15.47 | 24.32 | 39.79 | 19.8 | 53.16 | 15 | 0 | 13.37 | 4.82 | 0 | Diesel-backup
2025-05-08 04:00 | 128 | 5 | Autumn | 4 | 3.94 | -20.1 | 14.35 | 75.6 | 283.1 | 14.44 | 120 | 134.44 | 20.1 | 49.1 | 46.41 | 85.34 | 0 | 0 | 0 | Normal
2025-05-08 05:00 | 128 | 5 | Autumn | 5 | 3.94 | -18.6 | 13.61 | 44.4 | 332.1 | 16.94 | 120 | 136.94 | 18.6 | 50.14 | 78.35 | 86.8 | 0 | 0 | 0 | Normal
2025-05-08 06:00 | 128 | 5 | Autumn | 6 | 3.94 | -19.7 | 10.44 | 66 | 21.7 | 1.11 | 46.78 | 47.89 | 19.7 | 56.29 | 74.99 | -8.4 | 0 | 0 | 0 | Battery-supported
2025-05-08 07:00 | 128 | 5 | Autumn | 7 | 3.94 | -21.3 | 15.9 | 10.6 | 0 | 0 | 120 | 120 | 21.3 | 56.16 | 95 | 54.38 | 0 | 0 | 0 | Normal
2025-05-08 08:00 | 128 | 5 | Autumn | 8 | 3.94 | -19.9 | 9.39 | 62.9 | 0 | 0 | 28.6 | 28.6 | 19.9 | 58.18 | 83.17 | -29.58 | 0 | 0 | 0 | Battery-supported
2025-05-08 09:00 | 128 | 5 | Autumn | 9 | 3.94 | -19.9 | 8.09 | 32.2 | 0 | 0 | 13.53 | 13.53 | 19.9 | 60.95 | 64.2 | -47.42 | 0 | 0 | 0 | Battery-supported
2025-05-08 10:00 | 128 | 5 | Autumn | 10 | 3.94 | -20.2 | 9.27 | 3.5 | 0 | 0 | 26.89 | 26.89 | 20.2 | 66.32 | 48.43 | -39.43 | 0 | 0 | 0 | Battery-supported
2025-05-08 11:00 | 128 | 5 | Autumn | 11 | 3.94 | -19.1 | 6.32 | 66.8 | 229 | 11.68 | 3.14 | 14.82 | 19.1 | 62.9 | 29.2 | -48.08 | 0 | 0 | 0 | Battery-supported
2025-05-08 12:00 | 128 | 5 | Autumn | 12 | 3.94 | -15.5 | 14.53 | 47.8 | 421 | 25.26 | 120 | 145.26 | 15.5 | 54.32 | 62.66 | 90.94 | 0 | 0 | 0 | Normal
2025-05-08 13:00 | 128 | 5 | Autumn | 13 | 3.94 | -17.3 | 6.13 | 28.7 | 359.9 | 21.59 | 2.55 | 24.14 | 17.3 | 61.32 | 47.79 | -37.18 | 0 | 0 | 0 | Battery-supported
2025-05-08 14:00 | 128 | 5 | Autumn | 14 | 3.94 | -12 | 2.07 | 51.8 | 0 | 0 | 0 | 0 | 12 | 52.75 | 26.69 | -52.75 | 0 | 0 | 0 | Battery-supported
2025-05-08 15:00 | 128 | 5 | Autumn | 15 | 3.94 | -16.6 | 3.16 | 95.2 | 0 | 0 | 0 | 0 | 16.6 | 57.02 | 15 | -29.22 | 27.8 | 9.507 | 0 | Diesel-backup
2025-05-08 16:00 | 128 | 5 | Autumn | 16 | 3.94 | -17.3 | 11.07 | 73.2 | 0 | 0 | 60.72 | 60.72 | 17.3 | 60.83 | 15 | 0 | 0.11 | 0.042 | 0 | Diesel-backup
2025-05-08 17:00 | 128 | 5 | Autumn | 17 | 3.94 | -16.3 | 5.49 | 18.5 | 0 | 0 | 1.1 | 1.1 | 16.3 | 54.91 | 15 | 0 | 53.81 | 17.219 | 0 | Diesel-backup
2025-05-08 18:00 | 128 | 5 | Autumn | 18 | 3.94 | -15.5 | 13.79 | 75.2 | 18.8 | 1.13 | 120 | 121.13 | 15.5 | 56.74 | 38.7 | 64.39 | 0 | 0 | 0 | Normal
2025-05-08 19:00 | 128 | 5 | Autumn | 19 | 3.94 | -15 | 8.8 | 41.1 | 344.5 | 20.67 | 20.84 | 41.51 | 15 | 62.19 | 30.42 | -20.68 | 0 | 0 | 0 | Battery-supported
2025-05-08 20:00 | 128 | 5 | Autumn | 20 | 3.94 | -11.3 | 14.47 | 19.7 | 556.7 | 33.4 | 120 | 153.4 | 11.3 | 64.18 | 63.26 | 89.22 | 0 | 0 | 0 | Normal
2025-05-08 21:00 | 128 | 5 | Autumn | 21 | 3.94 | -17.8 | 2.22 | 52.8 | 251.3 | 15.08 | 0 | 15.08 | 17.8 | 45.95 | 50.91 | -30.87 | 0 | 0 | 0 | Battery-supported
2025-05-08 22:00 | 128 | 5 | Autumn | 22 | 3.94 | -14.2 | 6.1 | 29.9 | 0 | 0 | 2.46 | 2.46 | 14.2 | 45.69 | 33.62 | -43.23 | 0 | 0 | 0 | Battery-supported
2025-05-08 23:00 | 128 | 5 | Autumn | 23 | 3.94 | -15.9 | 4.8 | 18.9 | 0 | 0 | 0.31 | 0.31 | 15.9 | 55.42 | 15 | -46.54 | 8.57 | 3.142 | 0 | Diesel-backup
2025-05-09 | 129 | 5 | Autumn | 0 | 3.7 | -20.3 | 32.09 | 98.4 | 0 | 0 | 0 | 0 | 20.3 | 50.28 | 15 | 0 | 50.28 | 16.09 | 0 | Diesel-backup
2025-05-09 01:00 | 129 | 5 | Autumn | 1 | 3.7 | -15.5 | 6.79 | 71.9 | 0 | 0 | 4.98 | 4.98 | 15.5 | 49.99 | 15 | 0 | 45.01 | 14.403 | 0 | Diesel-backup
2025-05-09 02:00 | 129 | 5 | Autumn | 2 | 3.7 | -14.8 | 3.13 | 17.5 | 0 | 0 | 0 | 0 | 14.8 | 56.99 | 15 | 0 | 56.99 | 18.237 | 0 | Diesel-backup
2025-05-09 03:00 | 129 | 5 | Autumn | 3 | 3.7 | -19.9 | 10.98 | 18.4 | 123.4 | 6.29 | 58.58 | 64.87 | 19.9 | 51.99 | 19.74 | 12.88 | 0 | 0 | 0 | Normal
2025-05-09 04:00 | 129 | 5 | Autumn | 4 | 3.7 | -18.3 | 4.54 | 71.7 | 265.6 | 13.55 | 0.16 | 13.71 | 18.3 | 52.29 | 15 | -11.85 | 26.73 | 9.179 | 0 | Diesel-backup
2025-05-09 05:00 | 129 | 5 | Autumn | 5 | 3.7 | -22.4 | 15.38 | 49.5 | 388.1 | 19.79 | 120 | 139.79 | 22.4 | 52.25 | 47.21 | 87.54 | 0 | 0 | 0 | Normal
2025-05-09 06:00 | 129 | 5 | Autumn | 6 | 3.7 | -21.6 | 16.86 | 34.3 | 179.4 | 9.15 | 120 | 129.15 | 21.6 | 59.35 | 72.9 | 69.8 | 0 | 0 | 0 | Normal
2025-05-09 07:00 | 129 | 5 | Autumn | 7 | 3.7 | -16.7 | 4.85 | 30.1 | 0 | 0 | 0.34 | 0.34 | 16.7 | 45 | 55.04 | -44.66 | 0 | 0 | 0 | Battery-supported
2025-05-09 08:00 | 129 | 5 | Autumn | 8 | 3.7 | -20.1 | 5.61 | 39.3 | 0 | 0 | 1.31 | 1.31 | 20.1 | 60.33 | 31.43 | -59.02 | 0 | 0 | 0 | Battery-supported
2025-05-09 09:00 | 129 | 5 | Autumn | 9 | 3.7 | -21.5 | 10.39 | 88.5 | 0 | 0 | 45.78 | 45.78 | 21.5 | 59.31 | 26.02 | -13.53 | 0 | 0 | 0 | Battery-supported
2025-05-09 10:00 | 129 | 5 | Autumn | 10 | 3.7 | -18.4 | 15.64 | 36.4 | 0 | 0 | 120 | 120 | 18.4 | 60.11 | 48.06 | 59.89 | 0 | 0 | 0 | Normal
2025-05-09 11:00 | 129 | 5 | Autumn | 11 | 3.7 | -19.8 | 11.1 | 50.5 | 269.5 | 13.74 | 61.44 | 75.18 | 19.8 | 70.22 | 49.88 | 4.96 | 0 | 0 | 0 | Normal
2025-05-09 12:00 | 129 | 5 | Autumn | 12 | 3.7 | -19.4 | 6.79 | 44.1 | 439.2 | 22.4 | 4.98 | 27.38 | 19.4 | 63.94 | 35.26 | -36.56 | 0 | 0 | 0 | Battery-supported
2025-05-09 13:00 | 129 | 5 | Autumn | 13 | 3.7 | -16.3 | 3.58 | 22.6 | 360.3 | 21.62 | 0 | 21.62 | 16.3 | 60.25 | 19.81 | -38.63 | 0 | 0 | 0 | Battery-supported
2025-05-09 14:00 | 129 | 5 | Autumn | 14 | 3.7 | -20.1 | 22.3 | 52 | 0 | 0 | 120 | 120 | 20.1 | 64.28 | 40.31 | 55.72 | 0 | 0 | 0 | Normal
2025-05-09 15:00 | 129 | 5 | Autumn | 15 | 3.7 | -19.2 | 11.26 | 57.2 | 0 | 0 | 65.4 | 65.4 | 19.2 | 62.11 | 41.52 | 3.29 | 0 | 0 | 0 | Normal
2025-05-09 16:00 | 129 | 5 | Autumn | 16 | 3.7 | -16.5 | 24.99 | 76.4 | 0 | 0 | 120 | 120 | 16.5 | 64.64 | 61.89 | 55.36 | 0 | 0 | 0 | Normal
2025-05-09 17:00 | 129 | 5 | Autumn | 17 | 3.7 | -14.4 | 12.22 | 14.5 | 0 | 0 | 92.8 | 92.8 | 14.4 | 60.5 | 73.78 | 32.3 | 0 | 0 | 0 | Normal
2025-05-09 18:00 | 129 | 5 | Autumn | 18 | 3.7 | -13.6 | 23.15 | 62.8 | 127.8 | 7.67 | 120 | 127.67 | 13.6 | 51.4 | 95 | 57.66 | 0 | 0 | 0 | Normal
2025-05-09 19:00 | 129 | 5 | Autumn | 19 | 3.7 | -17.6 | 5.28 | 45 | 408.9 | 24.53 | 0.79 | 25.32 | 17.6 | 64.5 | 79.33 | -39.18 | 0 | 0 | 0 | Battery-supported
2025-05-09 20:00 | 129 | 5 | Autumn | 20 | 3.7 | -14 | 5.54 | 13.3 | 517.4 | 31.04 | 1.19 | 32.23 | 14 | 57.94 | 69.04 | -25.71 | 0 | 0 | 0 | Battery-supported
2025-05-09 21:00 | 129 | 5 | Autumn | 21 | 3.7 | -17.9 | 7.92 | 74.5 | 63.1 | 3.79 | 12.09 | 15.88 | 17.9 | 54.72 | 53.51 | -38.84 | 0 | 0 | 0 | Battery-supported
2025-05-09 22:00 | 129 | 5 | Autumn | 22 | 3.7 | -12.3 | 5.01 | 81.1 | 0 | 0 | 0.48 | 0.48 | 12.3 | 45 | 35.7 | -44.52 | 0 | 0 | 0 | Battery-supported
2025-05-09 23:00 | 129 | 5 | Autumn | 23 | 3.7 | -19 | 2.77 | 42.4 | 0 | 0 | 0 | 0 | 19 | 54 | 15 | -51.75 | 2.25 | 0.843 | 0 | Diesel-backup
2025-05-10 | 130 | 5 | Autumn | 0 | 3.45 | -14.1 | 5.95 | 47 | 0 | 0 | 2.06 | 2.06 | 14.1 | 48.54 | 15 | 0 | 46.48 | 14.874 | 0 | Diesel-backup
2025-05-10 01:00 | 130 | 5 | Autumn | 1 | 3.45 | -18.8 | 12.15 | 70 | 0 | 0 | 90.59 | 90.59 | 18.8 | 51.03 | 29.56 | 39.56 | 0 | 0 | 0 | Normal
2025-05-10 02:00 | 130 | 5 | Autumn | 2 | 3.45 | -13.3 | 3.9 | 31.6 | 0 | 0 | 0.01 | 0.01 | 13.3 | 52.59 | 15 | -36.4 | 16.18 | 5.776 | 0 | Diesel-backup
2025-05-10 03:00 | 130 | 5 | Autumn | 3 | 3.45 | -16.9 | 4.21 | 97.5 | 0 | 0 | 0.05 | 0.05 | 16.9 | 45.36 | 15 | 0 | 45.31 | 14.499 | 0 | Diesel-backup
2025-05-10 04:00 | 130 | 5 | Autumn | 4 | 3.45 | -20.8 | 6.2 | 53.4 | 212.8 | 10.85 | 2.75 | 13.6 | 20.8 | 67.91 | 15 | 0 | 54.31 | 17.379 | 0 | Diesel-backup
2025-05-10 05:00 | 130 | 5 | Autumn | 5 | 3.45 | -20 | 4.65 | 5.6 | 626 | 31.93 | 0.21 | 32.14 | 20 | 50.53 | 15 | 0 | 18.39 | 6.511 | 0 | Diesel-backup
2025-05-10 06:00 | 130 | 5 | Autumn | 6 | 3.45 | -17.4 | 6.42 | 34.3 | 332 | 19.92 | 3.48 | 23.4 | 17.4 | 54.28 | 15 | 0 | 30.88 | 10.44 | 0 | Diesel-backup
2025-05-10 07:00 | 130 | 5 | Autumn | 7 | 3.45 | -16.9 | 8.31 | 25 | 0 | 0 | 15.58 | 15.58 | 16.9 | 52.76 | 15 | 0 | 37.18 | 12.27 | 0 | Diesel-backup
2025-05-10 08:00 | 130 | 5 | Autumn | 8 | 3.45 | -19.4 | 4.09 | 58.9 | 0 | 0 | 0.03 | 0.03 | 19.4 | 67.07 | 15 | 0 | 67.04 | 21.453 | 0 | Diesel-backup
2025-05-10 09:00 | 130 | 5 | Autumn | 9 | 3.45 | -19.1 | 6.29 | 42.7 | 0 | 0 | 3.04 | 3.04 | 19.1 | 68.78 | 15 | 0 | 65.74 | 21.037 | 0 | Diesel-backup
2025-05-10 10:00 | 130 | 5 | Autumn | 10 | 3.45 | -17.4 | 8.78 | 41.3 | 0 | 0 | 20.6 | 20.6 | 17.4 | 58.66 | 15 | 0 | 38.06 | 12.517 | 0 | Diesel-backup
2025-05-10 11:00 | 130 | 5 | Autumn | 11 | 3.45 | -18.5 | 5.16 | 17.7 | 349 | 17.8 | 0.64 | 18.44 | 18.5 | 62.2 | 15 | 0 | 43.76 | 14.073 | 0 | Diesel-backup
2025-05-10 12:00 | 130 | 5 | Autumn | 12 | 3.45 | -21.4 | 3.59 | 73.5 | 294.6 | 15.02 | 0 | 15.02 | 21.4 | 62.69 | 15 | 0 | 47.67 | 15.254 | 0 | Diesel-backup
2025-05-10 13:00 | 130 | 5 | Autumn | 13 | 3.45 | -19.9 | 5.41 | 67.9 | 197.5 | 10.07 | 0.98 | 11.05 | 19.9 | 59.03 | 15 | 0 | 47.98 | 15.354 | 0 | Diesel-backup
2025-05-10 14:00 | 130 | 5 | Autumn | 14 | 3.45 | -17.3 | 7.06 | 43.9 | 0 | 0 | 6.31 | 6.31 | 17.3 | 60.44 | 15 | 0 | 54.13 | 17.322 | 0 | Diesel-backup
2025-05-10 15:00 | 130 | 5 | Autumn | 15 | 3.45 | -14.7 | 2.67 | 4.5 | 0 | 0 | 0 | 0 | 14.7 | 57.59 | 15 | 0 | 57.59 | 18.429 | 0 | Diesel-backup
2025-05-10 16:00 | 130 | 5 | Autumn | 16 | 3.45 | -13.5 | 12.26 | 56.6 | 0 | 0 | 94.09 | 94.09 | 13.5 | 56.54 | 28.82 | 37.55 | 0 | 0 | 0 | Normal
2025-05-10 17:00 | 130 | 5 | Autumn | 17 | 3.45 | -15 | 7.3 | 26.2 | 0 | 0 | 7.68 | 7.68 | 15 | 56.49 | 15 | -34.55 | 14.26 | 5.126 | 0 | Diesel-backup
2025-05-10 18:00 | 130 | 5 | Autumn | 18 | 3.45 | -15.8 | 5.43 | 95 | 128.5 | 7.71 | 1.01 | 8.72 | 15.8 | 60.16 | 15 | 0 | 51.44 | 16.461 | 0 | Diesel-backup
2025-05-10 19:00 | 130 | 5 | Autumn | 19 | 3.45 | -14.7 | 3 | 46.2 | 427.1 | 25.63 | 0 | 25.63 | 14.7 | 60.83 | 15 | 0 | 35.2 | 11.706 | 0 | Diesel-backup
2025-05-10 20:00 | 130 | 5 | Autumn | 20 | 3.45 | -17.7 | 11.36 | 45.6 | 233.4 | 14 | 67.96 | 81.96 | 17.7 | 55.88 | 24.6 | 26.08 | 0 | 0 | 0 | Normal
2025-05-10 21:00 | 130 | 5 | Autumn | 21 | 3.45 | -16.7 | 17.01 | 54.9 | 0 | 0 | 120 | 120 | 16.7 | 54.17 | 48.82 | 65.83 | 0 | 0 | 0 | Normal
2025-05-10 22:00 | 130 | 5 | Autumn | 22 | 3.45 | -18.3 | 6.11 | 15.9 | 0 | 0 | 2.49 | 2.49 | 18.3 | 59.55 | 26 | -57.06 | 0 | 0 | 0 | Battery-supported
2025-05-10 23:00 | 130 | 5 | Autumn | 23 | 3.45 | -19.5 | 23.83 | 75.6 | 0 | 0 | 120 | 120 | 19.5 | 49.4 | 51.98 | 70.6 | 0 | 0 | 0 | Normal
2025-05-11 | 131 | 5 | Autumn | 0 | 3.18 | -16.5 | 8.55 | 64.3 | 253.5 | 15.21 | 18.03 | 33.24 | 16.5 | 52.12 | 44.43 | -18.88 | 0 | 0 | 0 | Battery-supported
2025-05-11 01:00 | 131 | 5 | Autumn | 1 | 3.18 | -17.2 | 8.75 | 67.4 | 0 | 0 | 20.25 | 20.25 | 17.2 | 54.02 | 30.92 | -33.77 | 0 | 0 | 0 | Battery-supported
2025-05-11 02:00 | 131 | 5 | Autumn | 2 | 3.18 | -16.4 | 14.3 | 22.2 | 0 | 0 | 120 | 120 | 16.4 | 54.53 | 55.01 | 65.47 | 0 | 0 | 0 | Normal
2025-05-11 03:00 | 131 | 5 | Autumn | 3 | 3.18 | -17.1 | 11.74 | 62.2 | 0 | 0 | 78.31 | 78.31 | 17.1 | 55.69 | 63.34 | 22.62 | 0 | 0 | 0 | Normal
2025-05-11 04:00 | 131 | 5 | Autumn | 4 | 3.18 | -18.2 | 3.9 | 63 | 0 | 0 | 0.01 | 0.01 | 18.2 | 58.02 | 40.13 | -58.01 | 0 | 0 | 0 | Battery-supported
2025-05-11 05:00 | 131 | 5 | Autumn | 5 | 3.18 | -17.8 | 5.98 | 34.1 | 396.8 | 23.81 | 2.13 | 25.94 | 17.8 | 53.34 | 29.17 | -27.4 | 0 | 0 | 0 | Battery-supported
2025-05-11 06:00 | 131 | 5 | Autumn | 6 | 3.18 | -19.4 | 15.71 | 30.1 | 474.6 | 24.2 | 120 | 144.2 | 19.4 | 50.41 | 63.69 | 93.79 | 0 | 0 | 0 | Normal
2025-05-11 07:00 | 131 | 5 | Autumn | 7 | 3.18 | -18.5 | 11.88 | 96.7 | 39.3 | 2 | 82.36 | 84.36 | 18.5 | 52.07 | 75.57 | 32.29 | 0 | 0 | 0 | Normal
2025-05-11 08:00 | 131 | 5 | Autumn | 8 | 3.18 | -21.1 | 24.02 | 29 | 0 | 0 | 120 | 120 | 21.1 | 69.87 | 94.02 | 50.13 | 0 | 0 | 0 | Normal
2025-05-11 09:00 | 131 | 5 | Autumn | 9 | 3.18 | -18.6 | 10.83 | 46.8 | 0 | 0 | 55.12 | 55.12 | 18.6 | 58.08 | 92.83 | -2.96 | 0 | 0 | 0 | Battery-supported
2025-05-11 10:00 | 131 | 5 | Autumn | 10 | 3.18 | -17.8 | 12.12 | 90.7 | 0 | 0 | 89.65 | 89.65 | 17.8 | 62.88 | 95 | 5.89 | 0 | 0 | 0 | Normal
2025-05-11 11:00 | 131 | 5 | Autumn | 11 | 3.18 | -20.5 | 5.42 | 67.4 | 178.9 | 9.12 | 0.99 | 10.11 | 20.5 | 66.88 | 72.29 | -56.77 | 0 | 0 | 0 | Battery-supported
2025-05-11 12:00 | 131 | 5 | Autumn | 12 | 3.18 | -18.6 | 16.91 | 14.9 | 582.6 | 29.71 | 120 | 149.71 | 18.6 | 64.05 | 95 | 61.71 | 0 | 0 | 0 | Normal
2025-05-11 13:00 | 131 | 5 | Autumn | 13 | 3.18 | -19.7 | 1.59 | 63.5 | 189.4 | 9.66 | 0 | 9.66 | 19.7 | 66.42 | 72.3 | -56.76 | 0 | 0 | 0 | Battery-supported
2025-05-11 14:00 | 131 | 5 | Autumn | 14 | 3.18 | -19.1 | 9.68 | 51.2 | 0 | 0 | 33.04 | 33.04 | 19.1 | 61.97 | 60.72 | -28.93 | 0 | 0 | 0 | Battery-supported
2025-05-11 15:00 | 131 | 5 | Autumn | 15 | 3.18 | -20 | 12.33 | 62.6 | 0 | 0 | 96.36 | 96.36 | 20 | 62.59 | 73.15 | 33.77 | 0 | 0 | 0 | Normal
2025-05-11 16:00 | 131 | 5 | Autumn | 16 | 3.18 | -14.4 | 10.41 | 27.3 | 0 | 0 | 46.18 | 46.18 | 14.4 | 64.66 | 65.76 | -18.48 | 0 | 0 | 0 | Battery-supported
2025-05-11 17:00 | 131 | 5 | Autumn | 17 | 3.18 | -14.6 | 8.6 | 46.9 | 92.8 | 5.57 | 18.57 | 24.14 | 14.6 | 65.49 | 49.22 | -41.35 | 0 | 0 | 0 | Battery-supported
2025-05-11 18:00 | 131 | 5 | Autumn | 18 | 3.18 | -15.5 | 8.02 | 22.1 | 511.5 | 30.69 | 12.92 | 43.61 | 15.5 | 64.29 | 40.95 | -20.68 | 0 | 0 | 0 | Battery-supported
2025-05-11 19:00 | 131 | 5 | Autumn | 19 | 3.18 | -12.2 | 8.81 | 39.7 | 374.5 | 22.47 | 20.96 | 43.43 | 12.2 | 57.4 | 35.36 | -13.97 | 0 | 0 | 0 | Battery-supported
2025-05-11 20:00 | 131 | 5 | Autumn | 20 | 3.18 | -16.9 | 4.33 | 36.9 | 0 | 0 | 0.08 | 0.08 | 16.9 | 57.6 | 15 | -50.9 | 6.62 | 2.444 | 0 | Diesel-backup
2025-05-11 21:00 | 131 | 5 | Autumn | 21 | 3.18 | -9.8 | 10.38 | 49 | 0 | 0 | 45.58 | 45.58 | 9.8 | 45.35 | 15.08 | 0.23 | 0 | 0 | 0 | Normal
2025-05-11 22:00 | 131 | 5 | Autumn | 22 | 3.18 | -17.2 | 5.46 | 94.2 | 0 | 0 | 1.05 | 1.05 | 17.2 | 51.68 | 15 | -0.21 | 50.42 | 16.134 | 0 | Diesel-backup
2025-05-11 23:00 | 131 | 5 | Autumn | 23 | 3.18 | -16.3 | 6.13 | 46.6 | 0 | 0 | 2.55 | 2.55 | 16.3 | 55.7 | 15 | 0 | 53.15 | 17.008 | 0 | Diesel-backup
2025-05-12 | 132 | 5 | Autumn | 0 | 2.9 | -18.3 | 4.01 | 59 | 331.9 | 16.93 | 0.02 | 16.95 | 18.3 | 54.86 | 15 | 0 | 37.91 | 12.475 | 0 | Diesel-backup
2025-05-12 01:00 | 132 | 5 | Autumn | 1 | 2.9 | -16.9 | 36.42 | 69 | 251.6 | 15.1 | 0 | 15.1 | 16.9 | 54.24 | 15 | 0 | 39.14 | 12.818 | 0 | Diesel-backup
2025-05-12 02:00 | 132 | 5 | Autumn | 2 | 2.9 | -16.3 | 9.98 | 39.4 | 0 | 0 | 38.08 | 38.08 | 16.3 | 51.17 | 15 | 0 | 13.09 | 4.723 | 0 | Diesel-backup
2025-05-12 03:00 | 132 | 5 | Autumn | 3 | 2.9 | -18.8 | 3.44 | 54.5 | 0 | 0 | 0 | 0 | 18.8 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-05-12 04:00 | 132 | 5 | Autumn | 4 | 2.9 | -15 | 9.37 | 45.1 | 0 | 0 | 28.31 | 28.31 | 15 | 55.25 | 15 | 0 | 26.94 | 9.244 | 0 | Diesel-backup
2025-05-12 05:00 | 132 | 5 | Autumn | 5 | 2.9 | -18.7 | 16.86 | 82.7 | 66.8 | 3.41 | 120 | 123.41 | 18.7 | 53.44 | 40.75 | 69.97 | 0 | 0 | 0 | Normal
2025-05-12 06:00 | 132 | 5 | Autumn | 6 | 2.9 | -18.9 | 10.34 | 52.1 | 390.2 | 19.9 | 44.79 | 64.69 | 18.9 | 57.77 | 43.3 | 6.92 | 0 | 0 | 0 | Normal
2025-05-12 07:00 | 132 | 5 | Autumn | 7 | 2.9 | -21.6 | 8.49 | 25.9 | 342 | 17.44 | 17.39 | 34.83 | 21.6 | 55.25 | 35.13 | -20.42 | 0 | 0 | 0 | Battery-supported
2025-05-12 08:00 | 132 | 5 | Autumn | 8 | 2.9 | -18.7 | 5.18 | 52.5 | 0 | 0 | 0.66 | 0.66 | 18.7 | 68.19 | 15 | -50.32 | 17.21 | 6.12 | 0 | Diesel-backup
2025-05-12 09:00 | 132 | 5 | Autumn | 9 | 2.9 | -19.9 | 10.35 | 12.1 | 0 | 0 | 44.99 | 44.99 | 19.9 | 60.76 | 15 | 0 | 15.77 | 5.636 | 0 | Diesel-backup
2025-05-12 10:00 | 132 | 5 | Autumn | 10 | 2.9 | -20.8 | 13.49 | 92.2 | 0 | 0 | 120 | 120 | 20.8 | 63.52 | 35.78 | 56.48 | 0 | 0 | 0 | Normal
2025-05-12 11:00 | 132 | 5 | Autumn | 11 | 2.9 | -20.9 | 13.58 | 47.7 | 197.4 | 10.07 | 120 | 130.07 | 20.9 | 63.96 | 60.11 | 66.11 | 0 | 0 | 0 | Normal
2025-05-12 12:00 | 132 | 5 | Autumn | 12 | 2.9 | -13 | 9.78 | 43 | 444.4 | 26.66 | 34.66 | 61.32 | 13 | 49.97 | 64.29 | 11.35 | 0 | 0 | 0 | Normal
2025-05-12 13:00 | 132 | 5 | Autumn | 13 | 2.9 | -19.1 | 9.76 | 44.1 | 205.6 | 10.49 | 34.33 | 44.82 | 19.1 | 63.74 | 56.72 | -18.92 | 0 | 0 | 0 | Battery-supported
2025-05-12 14:00 | 132 | 5 | Autumn | 14 | 2.9 | -21.4 | 18.45 | 37.3 | 0 | 0 | 120 | 120 | 21.4 | 67.71 | 75.96 | 52.29 | 0 | 0 | 0 | Normal
2025-05-12 15:00 | 132 | 5 | Autumn | 15 | 2.9 | -19.3 | 17.36 | 5.8 | 0 | 0 | 120 | 120 | 19.3 | 63.98 | 95 | 51.73 | 0 | 0 | 0 | Normal
2025-05-12 16:00 | 132 | 5 | Autumn | 16 | 2.9 | -17.5 | 7.76 | 26.5 | 0 | 0 | 10.82 | 10.82 | 17.5 | 69.77 | 71.42 | -58.95 | 0 | 0 | 0 | Battery-supported
2025-05-12 17:00 | 132 | 5 | Autumn | 17 | 2.9 | -15.9 | 22.93 | 7.6 | 400.1 | 24.01 | 120 | 144.01 | 15.9 | 55.34 | 95 | 64.08 | 0 | 0 | 0 | Normal
2025-05-12 18:00 | 132 | 5 | Autumn | 18 | 2.9 | -15.6 | 3.49 | 25.4 | 518.7 | 31.12 | 0 | 31.12 | 15.6 | 51.7 | 86.77 | -20.58 | 0 | 0 | 0 | Battery-supported
2025-05-12 19:00 | 132 | 5 | Autumn | 19 | 2.9 | -15.2 | 10.04 | 33.5 | 131.7 | 7.9 | 39.15 | 47.05 | 15.2 | 53.44 | 84.21 | -6.39 | 0 | 0 | 0 | Battery-supported
2025-05-12 20:00 | 132 | 5 | Autumn | 20 | 2.9 | -18.1 | 10.65 | 88 | 0 | 0 | 51.16 | 51.16 | 18.1 | 61.44 | 80.1 | -10.28 | 0 | 0 | 0 | Battery-supported
2025-05-12 21:00 | 132 | 5 | Autumn | 21 | 2.9 | -15.9 | 4.98 | 53.4 | 0 | 0 | 0.45 | 0.45 | 15.9 | 55.7 | 58 | -55.25 | 0 | 0 | 0 | Battery-supported
2025-05-12 22:00 | 132 | 5 | Autumn | 22 | 2.9 | -18.8 | 2.97 | 33.5 | 0 | 0 | 0 | 0 | 18.8 | 54.5 | 36.2 | -54.5 | 0 | 0 | 0 | Battery-supported
2025-05-12 23:00 | 132 | 5 | Autumn | 23 | 2.9 | -18.4 | 5.06 | 55.5 | 304.7 | 15.54 | 0.53 | 16.07 | 18.4 | 51.43 | 22.06 | -35.36 | 0 | 0 | 0 | Battery-supported
2025-05-13 | 133 | 5 | Autumn | 0 | 2.59 | -19.6 | 15.1 | 7.6 | 0 | 0 | 120 | 120 | 19.6 | 60.59 | 43.92 | 59.41 | 0 | 0 | 0 | Normal
2025-05-13 01:00 | 133 | 5 | Autumn | 1 | 2.59 | -20.6 | 15.36 | 66.4 | 237.6 | 12.12 | 120 | 132.12 | 20.6 | 55.14 | 72.25 | 76.98 | 0 | 0 | 0 | Normal
2025-05-13 02:00 | 133 | 5 | Autumn | 2 | 2.59 | -16 | 13.11 | 21.2 | 497.2 | 29.83 | 120 | 149.83 | 16 | 45.5 | 95 | 61.83 | 0 | 0 | 0 | Normal
2025-05-13 03:00 | 133 | 5 | Autumn | 3 | 2.59 | -17.2 | 5.55 | 79.5 | 0 | 0 | 1.21 | 1.21 | 17.2 | 56.19 | 73.01 | -54.98 | 0 | 0 | 0 | Battery-supported
2025-05-13 04:00 | 133 | 5 | Autumn | 4 | 2.59 | -16.9 | 15.47 | 74.4 | 0 | 0 | 120 | 120 | 16.9 | 54.48 | 95 | 59.76 | 0 | 0 | 0 | Normal
2025-05-13 05:00 | 133 | 5 | Autumn | 5 | 2.59 | -19.3 | 5.81 | 18.1 | 0 | 0 | 1.73 | 1.73 | 19.3 | 55.25 | 73.59 | -53.52 | 0 | 0 | 0 | Battery-supported
2025-05-13 06:00 | 133 | 5 | Autumn | 6 | 2.59 | -17.9 | 10.44 | 38.5 | 256.6 | 15.4 | 46.78 | 62.18 | 17.9 | 59.39 | 74.62 | 2.79 | 0 | 0 | 0 | Normal
2025-05-13 07:00 | 133 | 5 | Autumn | 7 | 2.59 | -23.7 | 8.83 | 93.5 | 191.2 | 9.75 | 21.19 | 30.94 | 23.7 | 58.28 | 63.68 | -27.34 | 0 | 0 | 0 | Battery-supported
2025-05-13 08:00 | 133 | 5 | Autumn | 8 | 2.59 | -17.9 | 6.94 | 35.3 | 65 | 3.9 | 5.7 | 9.6 | 17.9 | 62.02 | 42.71 | -52.42 | 0 | 0 | 0 | Battery-supported
2025-05-13 09:00 | 133 | 5 | Autumn | 9 | 2.59 | -19.4 | 12.74 | 70.4 | 0 | 0 | 110.41 | 110.41 | 19.4 | 58.5 | 61.82 | 51.91 | 0 | 0 | 0 | Normal
2025-05-13 10:00 | 133 | 5 | Autumn | 10 | 2.59 | -18.3 | 14.22 | 68.4 | 0 | 0 | 120 | 120 | 18.3 | 58.48 | 84.46 | 61.52 | 0 | 0 | 0 | Normal
2025-05-13 11:00 | 133 | 5 | Autumn | 11 | 2.59 | -18.6 | 5.34 | 60.7 | 125.5 | 6.4 | 0.87 | 7.27 | 18.6 | 59.7 | 63.48 | -52.43 | 0 | 0 | 0 | Battery-supported
2025-05-13 12:00 | 133 | 5 | Autumn | 12 | 2.59 | -21.3 | 9.15 | 36.4 | 476.7 | 24.31 | 25.24 | 49.55 | 21.3 | 67.07 | 56.48 | -17.52 | 0 | 0 | 0 | Battery-supported
2025-05-13 13:00 | 133 | 5 | Autumn | 13 | 2.59 | -22 | 13.79 | 84.3 | 84.7 | 4.32 | 120 | 124.32 | 22 | 62.3 | 79.3 | 62.02 | 0 | 0 | 0 | Normal
2025-05-13 14:00 | 133 | 5 | Autumn | 14 | 2.59 | -19.9 | 1.04 | 74 | 0 | 0 | 0 | 0 | 19.9 | 62.51 | 54.3 | -62.51 | 0 | 0 | 0 | Battery-supported
2025-05-13 15:00 | 133 | 5 | Autumn | 15 | 2.59 | -16.7 | 11.26 | 11.6 | 0 | 0 | 65.4 | 65.4 | 16.7 | 58.81 | 56.72 | 6.59 | 0 | 0 | 0 | Normal
2025-05-13 16:00 | 133 | 5 | Autumn | 16 | 2.59 | -16.1 | 13.96 | 29 | 69.2 | 4.15 | 120 | 124.15 | 16.1 | 58.89 | 80.74 | 65.26 | 0 | 0 | 0 | Normal
2025-05-13 17:00 | 133 | 5 | Autumn | 17 | 2.59 | -20.3 | 11.56 | 56.4 | 369 | 18.82 | 73.29 | 92.11 | 20.3 | 60.24 | 92.47 | 31.87 | 0 | 0 | 0 | Normal
2025-05-13 18:00 | 133 | 5 | Autumn | 18 | 2.59 | -19.2 | 11.89 | 31.8 | 274.7 | 14.01 | 82.66 | 96.67 | 19.2 | 61.37 | 95 | 6.89 | 0 | 0 | 0 | Normal
2025-05-13 19:00 | 133 | 5 | Autumn | 19 | 2.59 | -18.5 | 8.45 | 49.8 | 0 | 0 | 16.98 | 16.98 | 18.5 | 56.89 | 79.04 | -39.91 | 0 | 0 | 0 | Battery-supported
2025-05-13 20:00 | 133 | 5 | Autumn | 20 | 2.59 | -17.6 | 13.41 | 83.7 | 0 | 0 | 120 | 120 | 17.6 | 60.44 | 95 | 43.38 | 0 | 0 | 0 | Normal
2025-05-13 21:00 | 133 | 5 | Autumn | 21 | 2.59 | -19.9 | 3.84 | 52.1 | 0 | 0 | 0.01 | 0.01 | 19.9 | 54.79 | 73.09 | -54.78 | 0 | 0 | 0 | Battery-supported
2025-05-13 22:00 | 133 | 5 | Autumn | 22 | 2.59 | -20.2 | 5.09 | 30.1 | 457.8 | 23.35 | 0.56 | 23.91 | 20.2 | 55.49 | 60.46 | -31.58 | 0 | 0 | 0 | Battery-supported
2025-05-13 23:00 | 133 | 5 | Autumn | 23 | 2.59 | -19.1 | 11.77 | 80 | 189.3 | 9.65 | 79.16 | 88.81 | 19.1 | 56.34 | 72.4 | 32.47 | 0 | 0 | 0 | Normal
2025-05-14 | 134 | 5 | Autumn | 0 | 2.25 | -17.6 | 13.48 | 23.8 | 0 | 0 | 120 | 120 | 17.6 | 59.84 | 94.54 | 60.16 | 0 | 0 | 0 | Normal
2025-05-14 01:00 | 134 | 5 | Autumn | 1 | 2.25 | -20.7 | 17.02 | 45.3 | 0 | 0 | 120 | 120 | 20.7 | 49.06 | 95 | 1.24 | 0 | 0 | 0 | Normal
2025-05-14 02:00 | 134 | 5 | Autumn | 2 | 2.25 | -18.8 | 21.15 | 2.1 | 115.9 | 5.91 | 120 | 125.91 | 18.8 | 52.32 | 95 | 0 | 0 | 0 | 0 | Normal
2025-05-14 03:00 | 134 | 5 | Autumn | 3 | 2.25 | -16.6 | 5.62 | 61.4 | 353.8 | 21.23 | 1.33 | 22.56 | 16.6 | 47.95 | 84.84 | -25.39 | 0 | 0 | 0 | Battery-supported
2025-05-14 04:00 | 134 | 5 | Autumn | 4 | 2.25 | -22.1 | 4.31 | 76 | 47.6 | 2.43 | 0.07 | 2.5 | 22.1 | 58.35 | 62.5 | -55.85 | 0 | 0 | 0 | Battery-supported
2025-05-14 05:00 | 134 | 5 | Autumn | 5 | 2.25 | -20 | 14.95 | 41.6 | 0 | 0 | 120 | 120 | 20 | 57.83 | 85.38 | 62.17 | 0 | 0 | 0 | Normal
2025-05-14 06:00 | 134 | 5 | Autumn | 6 | 2.25 | -17.6 | 6.77 | 85.1 | 0 | 0 | 4.89 | 4.89 | 17.6 | 47.75 | 68.24 | -42.86 | 0 | 0 | 0 | Battery-supported
2025-05-14 07:00 | 134 | 5 | Autumn | 7 | 2.25 | -20.9 | 8.68 | 68.1 | 246.3 | 12.56 | 19.45 | 32.01 | 20.9 | 57.17 | 58.17 | -25.16 | 0 | 0 | 0 | Battery-supported
2025-05-14 08:00 | 134 | 5 | Autumn | 8 | 2.25 | -21.3 | 14.09 | 47.7 | 321.9 | 16.42 | 120 | 136.42 | 21.3 | 67.76 | 83.44 | 68.66 | 0 | 0 | 0 | Normal
2025-05-14 09:00 | 134 | 5 | Autumn | 9 | 2.25 | -17.4 | 10.09 | 57.6 | 0 | 0 | 40.06 | 40.06 | 17.4 | 62.1 | 74.63 | -22.04 | 0 | 0 | 0 | Battery-supported
2025-05-14 10:00 | 134 | 5 | Autumn | 10 | 2.25 | -20.5 | 13.21 | 41.9 | 0 | 0 | 120 | 120 | 20.5 | 62.15 | 95 | 55.37 | 0 | 0 | 0 | Normal
2025-05-14 11:00 | 134 | 5 | Autumn | 11 | 2.25 | -17.1 | 5.27 | 24.3 | 93.5 | 5.61 | 0.78 | 6.39 | 17.1 | 62.8 | 72.44 | -56.41 | 0 | 0 | 0 | Battery-supported
2025-05-14 12:00 | 134 | 5 | Autumn | 12 | 2.25 | -18.3 | 10.79 | 60.9 | 356.3 | 18.17 | 54.22 | 72.39 | 18.3 | 60.28 | 76.89 | 12.11 | 0 | 0 | 0 | Normal
2025-05-14 13:00 | 134 | 5 | Autumn | 13 | 2.25 | -19.7 | 10.65 | 14.6 | 101.8 | 5.19 | 51.16 | 56.35 | 19.7 | 66.32 | 72.9 | -9.97 | 0 | 0 | 0 | Battery-supported
2025-05-14 14:00 | 134 | 5 | Autumn | 14 | 2.25 | -17.5 | 16.85 | 52 | 0 | 0 | 120 | 120 | 17.5 | 61.91 | 94.28 | 58.09 | 0 | 0 | 0 | Normal
2025-05-14 15:00 | 134 | 5 | Autumn | 15 | 2.25 | -17.4 | 18.99 | 23.7 | 0 | 0 | 120 | 120 | 17.4 | 59.65 | 95 | 1.95 | 0 | 0 | 0 | Normal
2025-05-14 16:00 | 134 | 5 | Autumn | 16 | 2.25 | -15.5 | 6.68 | 35.1 | 369.4 | 22.16 | 4.5 | 26.66 | 15.5 | 53.47 | 84.28 | -26.81 | 0 | 0 | 0 | Battery-supported
2025-05-14 17:00 | 134 | 5 | Autumn | 17 | 2.25 | -18.7 | 4.66 | 97.8 | 134.2 | 6.84 | 0.22 | 7.06 | 18.7 | 61.77 | 62.39 | -54.71 | 0 | 0 | 0 | Battery-supported
2025-05-14 18:00 | 134 | 5 | Autumn | 18 | 2.25 | -17.1 | 13.66 | 77.5 | 0 | 0 | 120 | 120 | 17.1 | 55.81 | 86.01 | 64.19 | 0 | 0 | 0 | Normal
2025-05-14 19:00 | 134 | 5 | Autumn | 19 | 2.25 | -17.2 | 2.78 | 18.8 | 0 | 0 | 0 | 0 | 17.2 | 55.85 | 63.67 | -55.85 | 0 | 0 | 0 | Battery-supported
2025-05-14 20:00 | 134 | 5 | Autumn | 20 | 2.25 | -15.5 | 14.21 | 44.1 | 74.2 | 4.45 | 120 | 124.45 | 15.5 | 57.11 | 88.46 | 67.34 | 0 | 0 | 0 | Normal
2025-05-14 21:00 | 134 | 5 | Autumn | 21 | 2.25 | -19.3 | 14.85 | 40.4 | 457.1 | 23.31 | 120 | 143.31 | 19.3 | 54 | 95 | 17.79 | 0 | 0 | 0 | Normal
2025-05-14 22:00 | 134 | 5 | Autumn | 22 | 2.25 | -15 | 6.34 | 62.3 | 62.7 | 3.76 | 3.21 | 6.97 | 15 | 45.22 | 79.7 | -38.25 | 0 | 0 | 0 | Battery-supported
2025-05-14 23:00 | 134 | 5 | Autumn | 23 | 2.25 | -16.4 | 1.26 | 30.2 | 0 | 0 | 0 | 0 | 16.4 | 50.74 | 59.4 | -50.74 | 0 | 0 | 0 | Battery-supported
2025-05-15 | 135 | 5 | Autumn | 0 | 1.86 | -20.8 | 15.79 | 15.3 | 76.4 | 3.9 | 120 | 123.9 | 20.8 | 54.85 | 84.81 | 69.05 | 0 | 0 | 0 | Normal
2025-05-15 01:00 | 135 | 5 | Autumn | 1 | 1.86 | -15.7 | 19.8 | 19.4 | 542.8 | 32.57 | 120 | 152.57 | 15.7 | 48.3 | 95 | 27.68 | 0 | 0 | 0 | Normal
2025-05-15 02:00 | 135 | 5 | Autumn | 2 | 1.86 | -13.8 | 19.04 | 57.5 | 0 | 0 | 120 | 120 | 13.8 | 47.77 | 95 | 0 | 0 | 0 | 0 | Normal
2025-05-15 03:00 | 135 | 5 | Autumn | 3 | 1.86 | -16.9 | 19.4 | 54.1 | 0 | 0 | 120 | 120 | 16.9 | 54.48 | 95 | 0 | 0 | 0 | 0 | Normal
2025-05-15 04:00 | 135 | 5 | Autumn | 4 | 1.86 | -16.3 | 3.66 | 79.8 | 151.3 | 9.08 | 0 | 9.08 | 16.3 | 49.75 | 78.73 | -40.67 | 0 | 0 | 0 | Battery-supported
2025-05-15 05:00 | 135 | 5 | Autumn | 5 | 1.86 | -19.6 | 9.37 | 81.4 | 190.1 | 9.7 | 28.31 | 38.01 | 19.6 | 56.93 | 71.16 | -18.92 | 0 | 0 | 0 | Battery-supported
2025-05-15 06:00 | 135 | 5 | Autumn | 6 | 1.86 | -23.7 | 10.65 | 72.2 | 0 | 0 | 51.16 | 51.16 | 23.7 | 58.38 | 68.28 | -7.22 | 0 | 0 | 0 | Battery-supported
2025-05-15 07:00 | 135 | 5 | Autumn | 7 | 1.86 | -24.2 | 9.71 | 60.9 | 0 | 0 | 33.52 | 33.52 | 24.2 | 63.27 | 56.38 | -29.75 | 0 | 0 | 0 | Battery-supported
2025-05-15 08:00 | 135 | 5 | Autumn | 8 | 1.86 | -19.6 | 13.33 | 84.4 | 213.4 | 10.88 | 120 | 130.88 | 19.6 | 65.85 | 80.31 | 65.03 | 0 | 0 | 0 | Normal
2025-05-15 09:00 | 135 | 5 | Autumn | 9 | 1.86 | -21.5 | 4.48 | 52.6 | 139.8 | 7.13 | 0.13 | 7.26 | 21.5 | 63.65 | 57.75 | -56.39 | 0 | 0 | 0 | Battery-supported
2025-05-15 10:00 | 135 | 5 | Autumn | 10 | 1.86 | -22 | 2.73 | 37.4 | 0 | 0 | 0 | 0 | 22 | 62.28 | 32.84 | -62.28 | 0 | 0 | 0 | Battery-supported
2025-05-15 11:00 | 135 | 5 | Autumn | 11 | 1.86 | -19.9 | 2.11 | 82.5 | 0 | 0 | 0 | 0 | 19.9 | 64.84 | 15 | -44.6 | 20.24 | 7.119 | 0 | Diesel-backup
2025-05-15 12:00 | 135 | 5 | Autumn | 12 | 1.86 | -18.1 | 15.99 | 35.5 | 481.5 | 24.56 | 120 | 144.56 | 18.1 | 59 | 46.49 | 85.56 | 0 | 0 | 0 | Normal
2025-05-15 13:00 | 135 | 5 | Autumn | 13 | 1.86 | -22.3 | 3.63 | 73.2 | 0 | 0 | 0 | 0 | 22.3 | 59.03 | 22.87 | -59.03 | 0 | 0 | 0 | Battery-supported
2025-05-15 14:00 | 135 | 5 | Autumn | 14 | 1.86 | -19.7 | 9.68 | 25.1 | 0 | 0 | 33.04 | 33.04 | 19.7 | 65.64 | 15 | -19.69 | 12.91 | 4.663 | 0 | Diesel-backup
2025-05-15 15:00 | 135 | 5 | Autumn | 15 | 1.86 | -15 | 6.17 | 99.6 | 58.4 | 3.5 | 2.66 | 6.16 | 15 | 55.55 | 15 | 0 | 49.39 | 15.805 | 0 | Diesel-backup
2025-05-15 16:00 | 135 | 5 | Autumn | 16 | 1.86 | -20.3 | 6.36 | 45.2 | 384.5 | 19.61 | 3.27 | 22.88 | 20.3 | 55.02 | 15 | 0 | 32.14 | 10.814 | 0 | Diesel-backup
2025-05-15 17:00 | 135 | 5 | Autumn | 17 | 1.86 | -15.7 | 7.99 | 19.3 | 0 | 0 | 12.67 | 12.67 | 15.7 | 58.39 | 15 | 0 | 45.72 | 14.63 | 0 | Diesel-backup
2025-05-15 18:00 | 135 | 5 | Autumn | 18 | 1.86 | -18.5 | 6.54 | 38.4 | 0 | 0 | 3.93 | 3.93 | 18.5 | 65.24 | 15 | 0 | 61.31 | 19.619 | 0 | Diesel-backup
2025-05-15 19:00 | 135 | 5 | Autumn | 19 | 1.86 | -16 | 2.74 | 63.8 | 254.6 | 15.28 | 0 | 15.28 | 16 | 56.64 | 15 | 0 | 41.36 | 13.428 | 0 | Diesel-backup
2025-05-15 20:00 | 135 | 5 | Autumn | 20 | 1.86 | -14.8 | 7.99 | 21.5 | 316 | 18.96 | 12.67 | 31.63 | 14.8 | 56.41 | 15 | 0 | 24.78 | 8.571 | 0 | Diesel-backup
2025-05-15 21:00 | 135 | 5 | Autumn | 21 | 1.86 | -15.6 | 5.37 | 17.3 | 0 | 0 | 0.92 | 0.92 | 15.6 | 52.59 | 15 | 0 | 51.67 | 16.534 | 0 | Diesel-backup
2025-05-15 22:00 | 135 | 5 | Autumn | 22 | 1.86 | -15.4 | 5.19 | 47.3 | 0 | 0 | 0.68 | 0.68 | 15.4 | 48.58 | 15 | 0 | 47.9 | 15.328 | 0 | Diesel-backup
2025-05-15 23:00 | 135 | 5 | Autumn | 23 | 1.86 | -20.2 | 23 | 22.2 | 529.3 | 26.99 | 120 | 146.99 | 20.2 | 54.78 | 48.93 | 92.21 | 0 | 0 | 0 | Normal
2025-05-16 | 136 | 5 | Autumn | 0 | 1.37 | -15.7 | 3.24 | 46.2 | 0 | 0 | 0 | 0 | 15.7 | 54.28 | 27.22 | -54.28 | 0 | 0 | 0 | Battery-supported
2025-05-16 01:00 | 136 | 5 | Autumn | 1 | 1.37 | -20.4 | 7.78 | 41.8 | 448.7 | 22.88 | 10.97 | 33.85 | 20.4 | 58.11 | 17.52 | -24.26 | 0 | 0 | 0 | Battery-supported
2025-05-16 02:00 | 136 | 5 | Autumn | 2 | 1.37 | -18.3 | 10.21 | 66 | 0 | 0 | 42.28 | 42.28 | 18.3 | 54.2 | 15 | -6.29 | 5.63 | 2.084 | 0 | Diesel-backup
2025-05-16 03:00 | 136 | 5 | Autumn | 3 | 1.37 | -18.7 | 23.09 | 30.7 | 0 | 0 | 120 | 120 | 18.7 | 47.03 | 41.85 | 72.97 | 0 | 0 | 0 | Normal
2025-05-16 04:00 | 136 | 5 | Autumn | 4 | 1.37 | -18.6 | 4.17 | 29.6 | 445.8 | 22.74 | 0.04 | 22.78 | 18.6 | 55.94 | 28.59 | -33.16 | 0 | 0 | 0 | Battery-supported
2025-05-16 05:00 | 136 | 5 | Autumn | 5 | 1.37 | -19.2 | 18.54 | 53.3 | 0 | 0 | 120 | 120 | 19.2 | 52.62 | 53.38 | 67.38 | 0 | 0 | 0 | Normal
2025-05-16 06:00 | 136 | 5 | Autumn | 6 | 1.37 | -22 | 7.98 | 59 | 136.3 | 6.95 | 12.58 | 19.53 | 22 | 58.96 | 37.61 | -39.43 | 0 | 0 | 0 | Battery-supported
2025-05-16 07:00 | 136 | 5 | Autumn | 7 | 1.37 | -23.3 | 8.16 | 67.8 | 145.3 | 7.41 | 14.16 | 21.57 | 23.3 | 52.23 | 25.35 | -30.66 | 0 | 0 | 0 | Battery-supported
2025-05-16 08:00 | 136 | 5 | Autumn | 8 | 1.37 | -18.5 | 12.91 | 26.1 | 0 | 0 | 116.62 | 116.62 | 18.5 | 65.25 | 44.25 | 51.37 | 0 | 0 | 0 | Normal
2025-05-16 09:00 | 136 | 5 | Autumn | 9 | 1.37 | -19.9 | 20.19 | 15.6 | 479.9 | 24.47 | 120 | 144.47 | 19.9 | 59.54 | 75.51 | 84.93 | 0 | 0 | 0 | Normal
2025-05-16 10:00 | 136 | 5 | Autumn | 10 | 1.37 | -17.7 | 6.52 | 78.2 | 0 | 0 | 3.86 | 3.86 | 17.7 | 62.42 | 52.08 | -58.56 | 0 | 0 | 0 | Battery-supported
2025-05-16 11:00 | 136 | 5 | Autumn | 11 | 1.37 | -20 | 10.67 | 91.1 | 0 | 0 | 51.59 | 51.59 | 20 | 66.73 | 46.03 | -15.14 | 0 | 0 | 0 | Battery-supported
2025-05-16 12:00 | 136 | 5 | Autumn | 12 | 1.37 | -22.7 | 9.81 | 65.3 | 334.6 | 17.06 | 35.16 | 52.22 | 22.7 | 67.26 | 40.01 | -15.04 | 0 | 0 | 0 | Battery-supported
2025-05-16 13:00 | 136 | 5 | Autumn | 13 | 1.37 | -17.1 | 9.53 | 49.6 | 0 | 0 | 30.69 | 30.69 | 17.1 | 61.64 | 27.63 | -30.95 | 0 | 0 | 0 | Battery-supported
2025-05-16 14:00 | 136 | 5 | Autumn | 14 | 1.37 | -19.7 | 14.21 | 80.6 | 0 | 0 | 120 | 120 | 19.7 | 63.05 | 48.59 | 56.95 | 0 | 0 | 0 | Normal
2025-05-16 15:00 | 136 | 5 | Autumn | 15 | 1.37 | -17.7 | 5.63 | 43 | 368.3 | 22.1 | 1.35 | 23.45 | 17.7 | 55.82 | 35.64 | -32.37 | 0 | 0 | 0 | Battery-supported
2025-05-16 16:00 | 136 | 5 | Autumn | 16 | 1.37 | -19.6 | 7.11 | 55.4 | 0 | 0 | 6.58 | 6.58 | 19.6 | 67.9 | 15 | -51.6 | 9.72 | 3.549 | 0 | Diesel-backup
2025-05-16 17:00 | 136 | 5 | Autumn | 17 | 1.37 | -14.2 | 2.8 | 35.9 | 216 | 12.96 | 0 | 12.96 | 14.2 | 61.58 | 15 | 0 | 48.62 | 15.558 | 0 | Diesel-backup
2025-05-16 18:00 | 136 | 5 | Autumn | 18 | 1.37 | -19.5 | 12.33 | 62.6 | 129.7 | 6.61 | 96.36 | 102.97 | 19.5 | 60.97 | 30.46 | 42 | 0 | 0 | 0 | Normal
2025-05-16 19:00 | 136 | 5 | Autumn | 19 | 1.37 | -18.2 | 9.26 | 70.1 | 0 | 0 | 26.75 | 26.75 | 18.2 | 47.49 | 22.16 | -20.74 | 0 | 0 | 0 | Battery-supported
2025-05-16 20:00 | 136 | 5 | Autumn | 20 | 1.37 | -17.1 | 19.91 | 37 | 413.9 | 24.83 | 120 | 144.83 | 17.1 | 64.13 | 51.86 | 80.7 | 0 | 0 | 0 | Normal
2025-05-16 21:00 | 136 | 5 | Autumn | 21 | 1.37 | -19.8 | 4.1 | 48.8 | 0 | 0 | 0.03 | 0.03 | 19.8 | 47.52 | 32.86 | -47.49 | 0 | 0 | 0 | Battery-supported
2025-05-16 22:00 | 136 | 5 | Autumn | 22 | 1.37 | -16.9 | 24.72 | 50.3 | 0 | 0 | 120 | 120 | 16.9 | 54.03 | 57.14 | 65.97 | 0 | 0 | 0 | Normal
2025-05-16 23:00 | 136 | 5 | Autumn | 23 | 1.37 | -14.3 | 13.54 | 30.8 | 502.5 | 30.15 | 120 | 150.15 | 14.3 | 46.39 | 95 | 102.88 | 0 | 0 | 0 | Normal
2025-05-17 | 137 | 5 | Autumn | 0 | 0.59 | -19.4 | 1.29 | 85.1 | 0 | 0 | 0 | 0 | 19.4 | 56.32 | 72.47 | -56.32 | 0 | 0 | 0 | Battery-supported
2025-05-17 01:00 | 137 | 5 | Autumn | 1 | 0.59 | -17.8 | 13.24 | 53.7 | 0 | 0 | 120 | 120 | 17.8 | 48.77 | 95 | 61.22 | 0 | 0 | 0 | Normal
2025-05-17 02:00 | 137 | 5 | Autumn | 2 | 0.59 | -25.1 | 6.11 | 38.3 | 0 | 0 | 2.49 | 2.49 | 25.1 | 60.12 | 71.95 | -57.63 | 0 | 0 | 0 | Battery-supported
2025-05-17 03:00 | 137 | 5 | Autumn | 3 | 0.59 | -19.5 | 7.59 | 74.2 | 0 | 0 | 9.58 | 9.58 | 19.5 | 47.67 | 56.71 | -38.09 | 0 | 0 | 0 | Battery-supported
2025-05-17 04:00 | 137 | 5 | Autumn | 4 | 0.59 | -20.5 | 6.81 | 41 | 235.7 | 12.02 | 5.08 | 17.1 | 20.5 | 55.56 | 41.33 | -38.46 | 0 | 0 | 0 | Battery-supported
2025-05-17 05:00 | 137 | 5 | Autumn | 5 | 0.59 | -21.9 | 17.94 | 89.6 | 213.8 | 10.9 | 120 | 130.9 | 21.9 | 56.88 | 68.57 | 74.02 | 0 | 0 | 0 | Normal
2025-05-17 06:00 | 137 | 5 | Autumn | 6 | 0.59 | -18 | 2.48 | 26.7 | 364.8 | 21.89 | 0 | 21.89 | 18 | 55.87 | 54.98 | -33.98 | 0 | 0 | 0 | Battery-supported
2025-05-17 07:00 | 137 | 5 | Autumn | 7 | 0.59 | -21.2 | 8.29 | 55.5 | 0 | 0 | 15.38 | 15.38 | 21.2 | 54.29 | 39.41 | -38.91 | 0 | 0 | 0 | Battery-supported
2025-05-17 08:00 | 137 | 5 | Autumn | 8 | 0.59 | -20.9 | 8.72 | 35.8 | 0 | 0 | 19.91 | 19.91 | 20.9 | 65.03 | 21.36 | -45.12 | 0 | 0 | 0 | Battery-supported
2025-05-17 09:00 | 137 | 5 | Autumn | 9 | 0.59 | -21.3 | 6.65 | 27.5 | 0 | 0 | 4.37 | 4.37 | 21.3 | 62.71 | 15 | -15.91 | 42.43 | 13.718 | 0 | Diesel-backup
2025-05-17 10:00 | 137 | 5 | Autumn | 10 | 0.59 | -24.6 | 4.85 | 88.6 | 0 | 0 | 0.34 | 0.34 | 24.6 | 69.41 | 15 | 0 | 69.07 | 22.102 | 0 | Diesel-backup
2025-05-17 11:00 | 137 | 5 | Autumn | 11 | 0.59 | -22.6 | 1.54 | 70.5 | 188.8 | 9.63 | 0 | 9.63 | 22.6 | 67.16 | 15 | 0 | 57.53 | 18.41 | 0 | Diesel-backup
2025-05-17 12:00 | 137 | 5 | Autumn | 12 | 0.59 | -17.7 | 8.37 | 48.1 | 419.2 | 25.15 | 16.17 | 41.32 | 17.7 | 64.22 | 15 | 0 | 22.9 | 7.976 | 0 | Diesel-backup
2025-05-17 13:00 | 137 | 5 | Autumn | 13 | 0.59 | -24.1 | 12.34 | 67.8 | 197 | 10.05 | 96.69 | 106.74 | 24.1 | 62.41 | 31.31 | 44.33 | 0 | 0 | 0 | Normal
2025-05-17 14:00 | 137 | 5 | Autumn | 14 | 0.59 | -20.7 | 9.3 | 100 | 0 | 0 | 27.31 | 27.31 | 20.7 | 63.33 | 16.91 | -36.02 | 0 | 0 | 0 | Battery-supported
2025-05-17 15:00 | 137 | 5 | Autumn | 15 | 0.59 | -19.6 | 4.85 | 79.6 | 0 | 0 | 0.34 | 0.34 | 19.6 | 63.74 | 15 | -4.76 | 58.64 | 18.764 | 0 | Diesel-backup
2025-05-17 16:00 | 137 | 5 | Autumn | 16 | 0.59 | -14.5 | 8.78 | 7.4 | 0 | 0 | 20.6 | 20.6 | 14.5 | 64.78 | 15 | 0 | 44.18 | 14.184 | 0 | Diesel-backup
2025-05-17 17:00 | 137 | 5 | Autumn | 17 | 0.59 | -16.3 | 20.1 | 21.8 | 0 | 0 | 120 | 120 | 16.3 | 67.23 | 34.42 | 52.77 | 0 | 0 | 0 | Normal
2025-05-17 18:00 | 137 | 5 | Autumn | 18 | 0.59 | -19 | 5.81 | 63.3 | 239.5 | 12.21 | 1.73 | 13.94 | 19 | 56.56 | 17.37 | -42.62 | 0 | 0 | 0 | Battery-supported
2025-05-17 19:00 | 137 | 5 | Autumn | 19 | 0.59 | -14.7 | 10.12 | 45.7 | 428.4 | 25.7 | 40.61 | 66.31 | 14.7 | 55.24 | 21.45 | 11.07 | 0 | 0 | 0 | Normal
2025-05-17 20:00 | 137 | 5 | Autumn | 20 | 0.59 | -19.2 | 10.98 | 20.6 | 287.8 | 14.68 | 58.58 | 73.26 | 19.2 | 52.2 | 29.2 | 21.06 | 0 | 0 | 0 | Normal
2025-05-17 21:00 | 137 | 5 | Autumn | 21 | 0.59 | -15.4 | 3.43 | 63.3 | 0 | 0 | 0 | 0 | 15.4 | 59.18 | 15 | -35.49 | 23.69 | 8.228 | 0 | Diesel-backup
2025-05-17 22:00 | 137 | 5 | Autumn | 22 | 0.59 | -20.8 | 7.36 | 63.4 | 0 | 0 | 8.05 | 8.05 | 20.8 | 57.07 | 15 | 0 | 49.02 | 15.686 | 0 | Diesel-backup
2025-05-17 23:00 | 137 | 5 | Autumn | 23 | 0.59 | -15.6 | 7.42 | 32.2 | 0 | 0 | 8.43 | 8.43 | 15.6 | 52.92 | 15 | 0 | 44.49 | 14.266 | 0 | Diesel-backup
2025-05-18 | 138 | 5 | Autumn | 0 | 0 | -20.1 | 9.1 | 57.5 | 0 | 0 | 24.58 | 24.58 | 20.1 | 53.84 | 15 | 0 | 29.26 | 9.953 | 0 | Diesel-backup
2025-05-18 01:00 | 138 | 5 | Autumn | 1 | 0 | -21.5 | 17.65 | 68.6 | 0 | 0 | 120 | 120 | 21.5 | 56.48 | 38.38 | 63.52 | 0 | 0 | 0 | Normal
2025-05-18 02:00 | 138 | 5 | Autumn | 2 | 0 | -19.7 | 4.02 | 53 | 0 | 0 | 0.02 | 0.02 | 19.7 | 59.22 | 15 | -58.44 | 0.76 | 0.287 | 0 | Diesel-backup
2025-05-18 03:00 | 138 | 5 | Autumn | 3 | 0 | -18.6 | 18.28 | 0.2 | 0 | 0 | 120 | 120 | 18.6 | 49.42 | 40.97 | 70.58 | 0 | 0 | 0 | Normal
2025-05-18 04:00 | 138 | 5 | Autumn | 4 | 0 | -20.3 | 12.92 | 61 | 0 | 0 | 116.99 | 116.99 | 20.3 | 50.78 | 65.34 | 66.21 | 0 | 0 | 0 | Normal
2025-05-18 05:00 | 138 | 5 | Autumn | 5 | 0 | -18 | 25.25 | 45.5 | 0 | 0 | 120 | 120 | 18 | 52.04 | 90.35 | 67.96 | 0 | 0 | 0 | Normal
2025-05-18 06:00 | 138 | 5 | Autumn | 6 | 0 | -20.5 | 1.95 | 64.7 | 0 | 0 | 0 | 0 | 20.5 | 55.54 | 68.13 | -55.54 | 0 | 0 | 0 | Battery-supported
2025-05-18 07:00 | 138 | 5 | Autumn | 7 | 0 | -17.9 | 1.17 | 78.2 | 0 | 0 | 0 | 0 | 17.9 | 55.12 | 46.08 | -55.12 | 0 | 0 | 0 | Battery-supported
2025-05-18 08:00 | 138 | 5 | Autumn | 8 | 0 | -18.3 | 33.05 | 35.2 | 0 | 0 | 0 | 0 | 18.3 | 61.38 | 21.53 | -61.38 | 0 | 0 | 0 | Battery-supported
2025-05-18 09:00 | 138 | 5 | Autumn | 9 | 0 | -19.4 | 3.33 | 52 | 0 | 0 | 0 | 0 | 19.4 | 59.02 | 15 | -16.33 | 42.69 | 13.787 | 0 | Diesel-backup
2025-05-18 10:00 | 138 | 5 | Autumn | 10 | 0 | -20.2 | 5.1 | 36.2 | 0 | 0 | 0.57 | 0.57 | 20.2 | 61.68 | 15 | 0 | 61.11 | 19.555 | 0 | Diesel-backup
2025-05-18 11:00 | 138 | 5 | Autumn | 11 | 0 | -18.9 | 5.14 | 33.7 | 0 | 0 | 0.62 | 0.62 | 18.9 | 62.61 | 15 | 0 | 61.99 | 19.837 | 0 | Diesel-backup
2025-05-18 12:00 | 138 | 5 | Autumn | 12 | 0 | -18 | 12.56 | 51.5 | 0 | 0 | 104.09 | 104.09 | 18 | 63.64 | 29.89 | 40.45 | 0 | 0 | 0 | Normal
2025-05-18 13:00 | 138 | 5 | Autumn | 13 | 0 | -14.7 | 7.79 | 72.7 | 0 | 0 | 11.05 | 11.05 | 14.7 | 61.7 | 15 | -37.21 | 13.44 | 4.842 | 0 | Diesel-backup
2025-05-18 14:00 | 138 | 5 | Autumn | 14 | 0 | -17.2 | 5.65 | 12.1 | 0 | 0 | 1.39 | 1.39 | 17.2 | 59.1 | 15 | 0 | 57.71 | 18.467 | 0 | Diesel-backup
2025-05-18 15:00 | 138 | 5 | Autumn | 15 | 0 | -17.1 | 22.67 | 14.6 | 0 | 0 | 120 | 120 | 17.1 | 57.27 | 38.08 | 62.73 | 0 | 0 | 0 | Normal
2025-05-18 16:00 | 138 | 5 | Autumn | 16 | 0 | -12.4 | 1.69 | 44.5 | 0 | 0 | 0 | 0 | 12.4 | 51.81 | 17.36 | -51.81 | 0 | 0 | 0 | Battery-supported
2025-05-18 17:00 | 138 | 5 | Autumn | 17 | 0 | -18.1 | 15.76 | 45.3 | 0 | 0 | 120 | 120 | 18.1 | 65.77 | 37.32 | 54.23 | 0 | 0 | 0 | Normal
2025-05-18 18:00 | 138 | 5 | Autumn | 18 | 0 | -18.2 | 8.62 | 47.7 | 0 | 0 | 18.79 | 18.79 | 18.2 | 59.45 | 21.05 | -40.66 | 0 | 0 | 0 | Battery-supported
2025-05-18 19:00 | 138 | 5 | Autumn | 19 | 0 | -17.7 | 5.58 | 75.1 | 0 | 0 | 1.26 | 1.26 | 17.7 | 57.65 | 15 | -15.13 | 41.26 | 13.4 | 0 | Diesel-backup
2025-05-18 20:00 | 138 | 5 | Autumn | 20 | 0 | -21.5 | 6.04 | 45 | 0 | 0 | 2.29 | 2.29 | 21.5 | 65.17 | 15 | 0 | 62.88 | 20.122 | 0 | Diesel-backup
2025-05-18 21:00 | 138 | 5 | Autumn | 21 | 0 | -20.2 | 7.3 | 47.2 | 0 | 0 | 7.68 | 7.68 | 20.2 | 61.66 | 15 | 0 | 53.98 | 17.274 | 0 | Diesel-backup
2025-05-18 22:00 | 138 | 5 | Autumn | 22 | 0 | -20.4 | 5.18 | 28.5 | 0 | 0 | 0.66 | 0.66 | 20.4 | 51.7 | 15 | 0 | 51.04 | 16.333 | 0 | Diesel-backup
2025-05-18 23:00 | 138 | 5 | Autumn | 23 | 0 | -17.8 | 14.35 | 24.1 | 0 | 0 | 120 | 120 | 17.8 | 55.17 | 38.86 | 64.83 | 0 | 0 | 0 | Normal
2025-05-19 | 139 | 5 | Autumn | 0 | 0 | -19.8 | 6.93 | 12.9 | 0 | 0 | 5.65 | 5.65 | 19.8 | 52.98 | 19.93 | -47.33 | 0 | 0 | 0 | Battery-supported
2025-05-19 01:00 | 139 | 5 | Autumn | 1 | 0 | -19.1 | 13.21 | 9.7 | 0 | 0 | 120 | 120 | 19.1 | 54.54 | 44.01 | 65.46 | 0 | 0 | 0 | Normal
2025-05-19 02:00 | 139 | 5 | Autumn | 2 | 0 | -17 | 6.12 | 53.7 | 0 | 0 | 2.52 | 2.52 | 17 | 55.24 | 22.93 | -52.72 | 0 | 0 | 0 | Battery-supported
2025-05-19 03:00 | 139 | 5 | Autumn | 3 | 0 | -17.5 | 10.07 | 12.6 | 0 | 0 | 39.69 | 39.69 | 17.5 | 57.36 | 15.86 | -17.67 | 0 | 0 | 0 | Battery-supported
2025-05-19 04:00 | 139 | 5 | Autumn | 4 | 0 | -19.8 | 10.07 | 51.5 | 0 | 0 | 39.69 | 39.69 | 19.8 | 52.68 | 15 | -2.15 | 10.84 | 3.944 | 0 | Diesel-backup
2025-05-19 05:00 | 139 | 5 | Autumn | 5 | 0 | -20.9 | 9.07 | 58.2 | 0 | 0 | 24.19 | 24.19 | 20.9 | 58.9 | 15 | 0 | 34.71 | 11.564 | 0 | Diesel-backup
2025-05-19 06:00 | 139 | 5 | Autumn | 6 | 0 | -16.9 | 18.66 | 76.6 | 0 | 0 | 120 | 120 | 16.9 | 52.85 | 39.71 | 67.15 | 0 | 0 | 0 | Normal
2025-05-19 07:00 | 139 | 5 | Autumn | 7 | 0 | -17.7 | 19.73 | 27.5 | 0 | 0 | 120 | 120 | 17.7 | 54.31 | 63.89 | 65.69 | 0 | 0 | 0 | Normal
2025-05-19 08:00 | 139 | 5 | Autumn | 8 | 0 | -22.9 | 13.95 | 61.8 | 0 | 0 | 120 | 120 | 22.9 | 70.84 | 81.98 | 49.16 | 0 | 0 | 0 | Normal
2025-05-19 09:00 | 139 | 5 | Autumn | 9 | 0 | -20.1 | 16.56 | 90.2 | 0 | 0 | 120 | 120 | 20.1 | 60.26 | 95 | 35.39 | 0 | 0 | 0 | Normal
2025-05-19 10:00 | 139 | 5 | Autumn | 10 | 0 | -19 | 13.51 | 5.4 | 0 | 0 | 120 | 120 | 19 | 65.1 | 95 | 0 | 0 | 0 | 0 | Normal
2025-05-19 11:00 | 139 | 5 | Autumn | 11 | 0 | -17.7 | 6.62 | 77.3 | 0 | 0 | 4.25 | 4.25 | 17.7 | 61.33 | 72.17 | -57.08 | 0 | 0 | 0 | Battery-supported
2025-05-19 12:00 | 139 | 5 | Autumn | 12 | 0 | -17.4 | 8.21 | 10.2 | 0 | 0 | 14.62 | 14.62 | 17.4 | 65.14 | 51.96 | -50.52 | 0 | 0 | 0 | Battery-supported
2025-05-19 13:00 | 139 | 5 | Autumn | 13 | 0 | -18.8 | 1.97 | 59.7 | 0 | 0 | 0 | 0 | 18.8 | 63.44 | 26.58 | -63.44 | 0 | 0 | 0 | Battery-supported
2025-05-19 14:00 | 139 | 5 | Autumn | 14 | 0 | -18.1 | 4.64 | 42.4 | 0 | 0 | 0.21 | 0.21 | 18.1 | 60.5 | 15 | -28.96 | 31.33 | 10.574 | 0 | Diesel-backup
2025-05-19 15:00 | 139 | 5 | Autumn | 15 | 0 | -19.3 | 3.36 | 85.2 | 0 | 0 | 0 | 0 | 19.3 | 65.78 | 15 | 0 | 65.78 | 21.05 | 0 | Diesel-backup
2025-05-19 16:00 | 139 | 5 | Autumn | 16 | 0 | -20.9 | 5.56 | 71 | 0 | 0 | 1.22 | 1.22 | 20.9 | 61.63 | 15 | 0 | 60.41 | 19.331 | 0 | Diesel-backup
2025-05-19 17:00 | 139 | 5 | Autumn | 17 | 0 | -20 | 10.56 | 80.1 | 0 | 0 | 49.25 | 49.25 | 20 | 61.4 | 15 | 0 | 12.15 | 4.399 | 0 | Diesel-backup
2025-05-19 18:00 | 139 | 5 | Autumn | 18 | 0 | -19.4 | 6.46 | 68.9 | 0 | 0 | 3.63 | 3.63 | 19.4 | 59.4 | 15 | 0 | 55.77 | 17.846 | 0 | Diesel-backup
2025-05-19 19:00 | 139 | 5 | Autumn | 19 | 0 | -19.5 | 14.79 | 73 | 0 | 0 | 120 | 120 | 19.5 | 59.99 | 37.08 | 60.01 | 0 | 0 | 0 | Normal
2025-05-19 20:00 | 139 | 5 | Autumn | 20 | 0 | -23.6 | 4.77 | 56.1 | 0 | 0 | 0.29 | 0.29 | 23.6 | 55.66 | 15 | -55.21 | 0.16 | 0.061 | 0 | Diesel-backup
2025-05-19 21:00 | 139 | 5 | Autumn | 21 | 0 | -20.3 | 12.85 | 74.4 | 0 | 0 | 114.41 | 114.41 | 20.3 | 53.26 | 37.5 | 61.15 | 0 | 0 | 0 | Normal
2025-05-19 22:00 | 139 | 5 | Autumn | 22 | 0 | -19.3 | 4.48 | 34.8 | 0 | 0 | 0.13 | 0.13 | 19.3 | 54.01 | 15.95 | -53.88 | 0 | 0 | 0 | Battery-supported
2025-05-19 23:00 | 139 | 5 | Autumn | 23 | 0 | -20 | 17.91 | 54.5 | 0 | 0 | 120 | 120 | 20 | 58.04 | 38.75 | 61.96 | 0 | 0 | 0 | Normal
2025-05-20 | 140 | 5 | Autumn | 0 | 0 | -20.1 | 4.77 | 88.4 | 0 | 0 | 0.29 | 0.29 | 20.1 | 51.42 | 18.3 | -51.13 | 0 | 0 | 0 | Battery-supported
2025-05-20 01:00 | 140 | 5 | Autumn | 1 | 0 | -18.5 | 11.79 | 31.6 | 0 | 0 | 79.74 | 79.74 | 18.5 | 51.5 | 28.69 | 28.24 | 0 | 0 | 0 | Normal
2025-05-20 02:00 | 140 | 5 | Autumn | 2 | 0 | -22 | 5.68 | 25.4 | 0 | 0 | 1.45 | 1.45 | 22 | 56.29 | 15 | -34.23 | 20.61 | 7.238 | 0 | Diesel-backup
2025-05-20 03:00 | 140 | 5 | Autumn | 3 | 0 | -23.2 | 21.48 | 79.9 | 0 | 0 | 120 | 120 | 23.2 | 61.26 | 36.62 | 58.74 | 0 | 0 | 0 | Normal
2025-05-20 04:00 | 140 | 5 | Autumn | 4 | 0 | -20.4 | 20.98 | 88.4 | 0 | 0 | 120 | 120 | 20.4 | 56.12 | 60.12 | 63.88 | 0 | 0 | 0 | Normal
2025-05-20 05:00 | 140 | 5 | Autumn | 5 | 0 | -17.9 | 11.56 | 31.7 | 0 | 0 | 73.29 | 73.29 | 17.9 | 54.4 | 67.08 | 18.89 | 0 | 0 | 0 | Normal
2025-05-20 06:00 | 140 | 5 | Autumn | 6 | 0 | -15.9 | 11.42 | 36.2 | 0 | 0 | 69.53 | 69.53 | 15.9 | 54.43 | 72.63 | 15.1 | 0 | 0 | 0 | Normal
2025-05-20 07:00 | 140 | 5 | Autumn | 7 | 0 | -17.9 | 14.2 | 6.4 | 0 | 0 | 120 | 120 | 17.9 | 54.91 | 95 | 60.78 | 0 | 0 | 0 | Normal
2025-05-20 08:00 | 140 | 5 | Autumn | 8 | 0 | -22.8 | 12.76 | 40.5 | 0 | 0 | 111.13 | 111.13 | 22.8 | 63.39 | 95 | 0 | 0 | 0 | 0 | Normal
2025-05-20 09:00 | 140 | 5 | Autumn | 9 | 0 | -20.1 | 15.31 | 47.3 | 0 | 0 | 120 | 120 | 20.1 | 69.94 | 95 | 0 | 0 | 0 | 0 | Normal
2025-05-20 10:00 | 140 | 5 | Autumn | 10 | 0 | -19 | 4.7 | 84.8 | 0 | 0 | 0.24 | 0.24 | 19 | 54.39 | 73.34 | -54.15 | 0 | 0 | 0 | Battery-supported
2025-05-20 11:00 | 140 | 5 | Autumn | 11 | 0 | -19.2 | 9.1 | 60.1 | 0 | 0 | 24.58 | 24.58 | 19.2 | 65.79 | 56.86 | -41.21 | 0 | 0 | 0 | Battery-supported
2025-05-20 12:00 | 140 | 5 | Autumn | 12 | 0 | -18.4 | 5.97 | 8.7 | 0 | 0 | 2.11 | 2.11 | 18.4 | 63.16 | 32.44 | -61.05 | 0 | 0 | 0 | Battery-supported
2025-05-20 13:00 | 140 | 5 | Autumn | 13 | 0 | -21.6 | 20.79 | 50.2 | 0 | 0 | 120 | 120 | 21.6 | 69.58 | 50.99 | 50.42 | 0 | 0 | 0 | Normal
2025-05-20 14:00 | 140 | 5 | Autumn | 14 | 0 | -19.4 | 3.78 | 65.8 | 0 | 0 | 0 | 0 | 19.4 | 61.47 | 26.4 | -61.47 | 0 | 0 | 0 | Battery-supported
2025-05-20 15:00 | 140 | 5 | Autumn | 15 | 0 | -18.7 | 22.89 | 100 | 0 | 0 | 120 | 120 | 18.7 | 59.71 | 48.59 | 60.29 | 0 | 0 | 0 | Normal
2025-05-20 16:00 | 140 | 5 | Autumn | 16 | 0 | -17.8 | 9.2 | 16 | 0 | 0 | 25.92 | 25.92 | 17.8 | 56.39 | 36.4 | -30.47 | 0 | 0 | 0 | Battery-supported
2025-05-20 17:00 | 140 | 5 | Autumn | 17 | 0 | -21.4 | 15.45 | 29.7 | 0 | 0 | 120 | 120 | 21.4 | 60.15 | 58.43 | 59.85 | 0 | 0 | 0 | Normal
2025-05-20 18:00 | 140 | 5 | Autumn | 18 | 0 | -20.3 | 6.44 | 48.4 | 0 | 0 | 3.56 | 3.56 | 20.3 | 62.63 | 34.8 | -59.07 | 0 | 0 | 0 | Battery-supported
2025-05-20 19:00 | 140 | 5 | Autumn | 19 | 0 | -25.5 | 3.55 | 38.6 | 0 | 0 | 0 | 0 | 25.5 | 65.13 | 15 | -49.5 | 15.63 | 5.591 | 0 | Diesel-backup
2025-05-20 20:00 | 140 | 5 | Autumn | 20 | 0 | -21 | 20.33 | 64.6 | 0 | 0 | 120 | 120 | 21 | 61.15 | 36.66 | 58.85 | 0 | 0 | 0 | Normal
2025-05-20 21:00 | 140 | 5 | Autumn | 21 | 0 | -20.7 | 12.18 | 39.4 | 0 | 0 | 91.53 | 91.53 | 20.7 | 51.46 | 51.4 | 40.07 | 0 | 0 | 0 | Normal
2025-05-20 22:00 | 140 | 5 | Autumn | 22 | 0 | -21.8 | 4.03 | 86.5 | 0 | 0 | 0.02 | 0.02 | 21.8 | 60.94 | 27.03 | -60.92 | 0 | 0 | 0 | Battery-supported
2025-05-20 23:00 | 140 | 5 | Autumn | 23 | 0 | -19.2 | 8.46 | 57.3 | 0 | 0 | 17.08 | 17.08 | 19.2 | 51.31 | 15 | -30.09 | 4.14 | 1.543 | 0 | Diesel-backup
2025-05-21 | 141 | 5 | Autumn | 0 | 0 | -19.9 | 8.09 | 39.6 | 0 | 0 | 13.53 | 13.53 | 19.9 | 56.51 | 15 | 0 | 42.98 | 13.865 | 0 | Diesel-backup
2025-05-21 01:00 | 141 | 5 | Autumn | 1 | 0 | -24.7 | 11.96 | 41.1 | 0 | 0 | 84.75 | 84.75 | 24.7 | 59.2 | 24.4 | 25.55 | 0 | 0 | 0 | Normal
2025-05-21 02:00 | 141 | 5 | Autumn | 2 | 0 | -19.3 | 4.7 | 90.3 | 0 | 0 | 0.24 | 0.24 | 19.3 | 55.69 | 15 | -23.51 | 31.94 | 10.756 | 0 | Diesel-backup
2025-05-21 03:00 | 141 | 5 | Autumn | 3 | 0 | -21.8 | 3.97 | 25.9 | 0 | 0 | 0.01 | 0.01 | 21.8 | 55.75 | 15 | 0 | 55.74 | 17.837 | 0 | Diesel-backup
2025-05-21 04:00 | 141 | 5 | Autumn | 4 | 0 | -18.7 | 9.89 | 53.3 | 0 | 0 | 36.52 | 36.52 | 18.7 | 56.8 | 15 | 0 | 20.28 | 7.131 | 0 | Diesel-backup
2025-05-21 05:00 | 141 | 5 | Autumn | 5 | 0 | -22.6 | 4.89 | 75.2 | 0 | 0 | 0.38 | 0.38 | 22.6 | 60.05 | 15 | 0 | 59.67 | 19.094 | 0 | Diesel-backup
2025-05-21 06:00 | 141 | 5 | Autumn | 6 | 0 | -19.7 | 20.75 | 48 | 0 | 0 | 120 | 120 | 19.7 | 59.54 | 37.25 | 60.46 | 0 | 0 | 0 | Normal
2025-05-21 07:00 | 141 | 5 | Autumn | 7 | 0 | -20.4 | 14.64 | 77 | 0 | 0 | 120 | 120 | 20.4 | 52.76 | 61.99 | 67.24 | 0 | 0 | 0 | Normal
2025-05-21 08:00 | 141 | 5 | Autumn | 8 | 0 | -19.1 | 14.39 | 33.9 | 0 | 0 | 120 | 120 | 19.1 | 58.71 | 84.55 | 61.29 | 0 | 0 | 0 | Normal
2025-05-21 09:00 | 141 | 5 | Autumn | 9 | 0 | -19.5 | 1.94 | 87 | 0 | 0 | 0 | 0 | 19.5 | 60.94 | 60.17 | -60.94 | 0 | 0 | 0 | Battery-supported
2025-05-21 10:00 | 141 | 5 | Autumn | 10 | 0 | -20.3 | 6.63 | 69.4 | 0 | 0 | 4.29 | 4.29 | 20.3 | 63.75 | 36.39 | -59.46 | 0 | 0 | 0 | Battery-supported
2025-05-21 11:00 | 141 | 5 | Autumn | 11 | 0 | -23.1 | 7.54 | 61.5 | 0 | 0 | 9.23 | 9.23 | 23.1 | 68.21 | 15 | -53.47 | 5.51 | 2.041 | 0 | Diesel-backup
2025-05-21 12:00 | 141 | 5 | Autumn | 12 | 0 | -23 | 4.37 | 68.6 | 0 | 0 | 0.09 | 0.09 | 23 | 63.49 | 15 | 0 | 63.4 | 20.288 | 0 | Diesel-backup
2025-05-21 13:00 | 141 | 5 | Autumn | 13 | 0 | -21 | 12.82 | 14.3 | 0 | 0 | 113.31 | 113.31 | 21 | 64.8 | 32.85 | 48.51 | 0 | 0 | 0 | Normal
2025-05-21 14:00 | 141 | 5 | Autumn | 14 | 0 | -19.8 | 11.82 | 85.1 | 0 | 0 | 80.61 | 80.61 | 19.8 | 62.07 | 39.67 | 18.54 | 0 | 0 | 0 | Normal
2025-05-21 15:00 | 141 | 5 | Autumn | 15 | 0 | -21.1 | 14.05 | 80.9 | 0 | 0 | 120 | 120 | 21.1 | 63.04 | 60.64 | 56.96 | 0 | 0 | 0 | Normal
2025-05-21 16:00 | 141 | 5 | Autumn | 16 | 0 | -18.4 | 16.46 | 9.8 | 0 | 0 | 120 | 120 | 18.4 | 61.37 | 82.21 | 58.63 | 0 | 0 | 0 | Normal
2025-05-21 17:00 | 141 | 5 | Autumn | 17 | 0 | -20.4 | 15.98 | 54.9 | 0 | 0 | 120 | 120 | 20.4 | 69.4 | 95 | 34.75 | 0 | 0 | 0 | Normal
2025-05-21 18:00 | 141 | 5 | Autumn | 18 | 0 | -21.9 | 34.93 | 62.1 | 0 | 0 | 0 | 0 | 21.9 | 68.06 | 67.78 | -68.06 | 0 | 0 | 0 | Battery-supported
2025-05-21 19:00 | 141 | 5 | Autumn | 19 | 0 | -20.4 | 8.94 | 53.6 | 0 | 0 | 22.53 | 22.53 | 20.4 | 67.6 | 49.75 | -45.07 | 0 | 0 | 0 | Battery-supported
2025-05-21 20:00 | 141 | 5 | Autumn | 20 | 0 | -19.3 | 8.01 | 54 | 0 | 0 | 12.84 | 12.84 | 19.3 | 63.75 | 29.38 | -50.91 | 0 | 0 | 0 | Battery-supported
2025-05-21 21:00 | 141 | 5 | Autumn | 21 | 0 | -19 | 12.72 | 48.9 | 0 | 0 | 109.7 | 109.7 | 19 | 61.04 | 47.29 | 48.66 | 0 | 0 | 0 | Normal
2025-05-21 22:00 | 141 | 5 | Autumn | 22 | 0 | -15.6 | 18.16 | 28.1 | 0 | 0 | 120 | 120 | 15.6 | 54.16 | 71.52 | 65.84 | 0 | 0 | 0 | Normal
2025-05-21 23:00 | 141 | 5 | Autumn | 23 | 0 | -21.2 | 2.8 | 69.6 | 0 | 0 | 0 | 0 | 21.2 | 50.5 | 51.32 | -50.5 | 0 | 0 | 0 | Battery-supported
2025-05-22 | 142 | 5 | Autumn | 0 | 0 | -20.1 | 5.38 | 80.2 | 0 | 0 | 0.93 | 0.93 | 20.1 | 58.01 | 28.49 | -57.08 | 0 | 0 | 0 | Battery-supported
2025-05-22 01:00 | 142 | 5 | Autumn | 1 | 0 | -19 | 6.24 | 22.9 | 0 | 0 | 2.88 | 2.88 | 19 | 55.35 | 15 | -33.72 | 18.75 | 6.63 | 0 | Diesel-backup
2025-05-22 02:00 | 142 | 5 | Autumn | 2 | 0 | -20 | 9.53 | 60.2 | 0 | 0 | 30.69 | 30.69 | 20 | 57.49 | 15 | 0 | 26.8 | 9.2 | 0 | Diesel-backup
2025-05-22 03:00 | 142 | 5 | Autumn | 3 | 0 | -21 | 6.68 | 32.8 | 0 | 0 | 4.5 | 4.5 | 21 | 50 | 15 | 0 | 45.5 | 14.56 | 0 | Diesel-backup
2025-05-22 04:00 | 142 | 5 | Autumn | 4 | 0 | -23.3 | 16.65 | 67.6 | 0 | 0 | 120 | 120 | 23.3 | 52.45 | 39.86 | 67.55 | 0 | 0 | 0 | Normal
2025-05-22 05:00 | 142 | 5 | Autumn | 5 | 0 | -21.1 | 10.35 | 50.2 | 0 | 0 | 44.99 | 44.99 | 21.1 | 55.72 | 35.57 | -10.73 | 0 | 0 | 0 | Battery-supported
2025-05-22 06:00 | 142 | 5 | Autumn | 6 | 0 | -22.3 | 8.45 | 25.9 | 0 | 0 | 16.98 | 16.98 | 22.3 | 50.28 | 22.25 | -33.3 | 0 | 0 | 0 | Battery-supported
2025-05-22 07:00 | 142 | 5 | Autumn | 7 | 0 | -23.7 | 11.92 | 13.7 | 0 | 0 | 83.55 | 83.55 | 23.7 | 61.51 | 30.36 | 22.04 | 0 | 0 | 0 | Normal
2025-05-22 08:00 | 142 | 5 | Autumn | 8 | 0 | -21.7 | 2.2 | 45.9 | 0 | 0 | 0 | 0 | 21.7 | 65.29 | 15 | -38.39 | 26.9 | 9.23 | 0 | Diesel-backup
2025-05-22 09:00 | 142 | 5 | Autumn | 9 | 0 | -22.2 | 11.58 | 46.7 | 0 | 0 | 73.83 | 73.83 | 22.2 | 72.99 | 15.31 | 0.84 | 0 | 0 | 0 | Normal
2025-05-22 10:00 | 142 | 5 | Autumn | 10 | 0 | -18.6 | 5 | 42.3 | 0 | 0 | 0.47 | 0.47 | 18.6 | 63.1 | 15 | -0.77 | 61.86 | 19.794 | 0 | Diesel-backup
2025-05-22 11:00 | 142 | 5 | Autumn | 11 | 0 | -18.6 | 14.96 | 26.9 | 0 | 0 | 120 | 120 | 18.6 | 64.38 | 35.47 | 55.62 | 0 | 0 | 0 | Normal
2025-05-22 12:00 | 142 | 5 | Autumn | 12 | 0 | -21.9 | 2.5 | 51.1 | 0 | 0 | 0 | 0 | 21.9 | 67.22 | 15 | -51.17 | 16.05 | 5.731 | 0 | Diesel-backup
2025-05-22 13:00 | 142 | 5 | Autumn | 13 | 0 | -20.5 | 12.39 | 36.9 | 0 | 0 | 98.34 | 98.34 | 20.5 | 63.81 | 27.71 | 34.53 | 0 | 0 | 0 | Normal
2025-05-22 14:00 | 142 | 5 | Autumn | 14 | 0 | -24 | 5.1 | 70 | 0 | 0 | 0.57 | 0.57 | 24 | 67.47 | 15 | -31.77 | 35.13 | 11.686 | 0 | Diesel-backup
2025-05-22 15:00 | 142 | 5 | Autumn | 15 | 0 | -21 | 18.41 | 15.7 | 0 | 0 | 120 | 120 | 21 | 63.77 | 35.69 | 56.23 | 0 | 0 | 0 | Normal
2025-05-22 16:00 | 142 | 5 | Autumn | 16 | 0 | -19 | 2.99 | 46.1 | 0 | 0 | 0 | 0 | 19 | 52.45 | 15 | -51.73 | 0.72 | 0.271 | 0 | Diesel-backup
2025-05-22 17:00 | 142 | 5 | Autumn | 17 | 0 | -18.1 | 9.32 | 33.4 | 0 | 0 | 27.59 | 27.59 | 18.1 | 65.59 | 15 | 0 | 38 | 12.5 | 0 | Diesel-backup
2025-05-22 18:00 | 142 | 5 | Autumn | 18 | 0 | -21.5 | 13.71 | 26.1 | 0 | 0 | 120 | 120 | 21.5 | 69.03 | 33.76 | 50.97 | 0 | 0 | 0 | Normal
2025-05-22 19:00 | 142 | 5 | Autumn | 19 | 0 | -17.6 | 11.18 | 71.7 | 0 | 0 | 63.4 | 63.4 | 17.6 | 64.06 | 33.49 | -0.66 | 0 | 0 | 0 | Battery-supported
2025-05-22 20:00 | 142 | 5 | Autumn | 20 | 0 | -23.3 | 11.14 | 64.6 | 0 | 0 | 62.42 | 62.42 | 23.3 | 66.66 | 31.8 | -4.24 | 0 | 0 | 0 | Battery-supported
2025-05-22 21:00 | 142 | 5 | Autumn | 21 | 0 | -22.7 | 3.78 | 39 | 0 | 0 | 0 | 0 | 22.7 | 57.16 | 15 | -41.99 | 15.17 | 5.433 | 0 | Diesel-backup
2025-05-22 22:00 | 142 | 5 | Autumn | 22 | 0 | -18.4 | 3.6 | 88.7 | 0 | 0 | 0 | 0 | 18.4 | 48.86 | 15 | 0 | 48.86 | 15.635 | 0 | Diesel-backup
2025-05-22 23:00 | 142 | 5 | Autumn | 23 | 0 | -16.3 | 10.88 | 30.2 | 0 | 0 | 56.26 | 56.26 | 16.3 | 46.29 | 18.67 | 9.97 | 0 | 0 | 0 | Normal
2025-05-23 | 143 | 5 | Autumn | 0 | 0 | -19 | 9.92 | 98.1 | 0 | 0 | 37.04 | 37.04 | 19 | 51.62 | 15 | -9.17 | 5.41 | 2.004 | 0 | Diesel-backup
2025-05-23 01:00 | 143 | 5 | Autumn | 1 | 0 | -20.2 | 4.54 | 65.8 | 0 | 0 | 0.16 | 0.16 | 20.2 | 56.01 | 15 | 0 | 55.85 | 17.872 | 0 | Diesel-backup
2025-05-23 02:00 | 143 | 5 | Autumn | 2 | 0 | -24.9 | 4.36 | 44.5 | 0 | 0 | 0.09 | 0.09 | 24.9 | 61.39 | 15 | 0 | 61.3 | 19.616 | 0 | Diesel-backup
2025-05-23 03:00 | 143 | 5 | Autumn | 3 | 0 | -24.5 | 8.55 | 17.3 | 0 | 0 | 18.03 | 18.03 | 24.5 | 57.44 | 15 | 0 | 39.41 | 12.893 | 0 | Diesel-backup
2025-05-23 04:00 | 143 | 5 | Autumn | 4 | 0 | -19.8 | 7.14 | 5.5 | 0 | 0 | 6.75 | 6.75 | 19.8 | 49.59 | 15 | 0 | 42.84 | 13.827 | 0 | Diesel-backup
2025-05-23 05:00 | 143 | 5 | Autumn | 5 | 0 | -20.9 | 25.09 | 74.4 | 0 | 0 | 120 | 120 | 20.9 | 53.23 | 39.57 | 66.77 | 0 | 0 | 0 | Normal
2025-05-23 06:00 | 143 | 5 | Autumn | 6 | 0 | -22.5 | 19.09 | 53.2 | 0 | 0 | 120 | 120 | 22.5 | 57.02 | 62.75 | 62.98 | 0 | 0 | 0 | Normal
2025-05-23 07:00 | 143 | 5 | Autumn | 7 | 0 | -20 | 14.68 | 22.3 | 0 | 0 | 120 | 120 | 20 | 48.75 | 88.97 | 71.25 | 0 | 0 | 0 | Normal
2025-05-23 08:00 | 143 | 5 | Autumn | 8 | 0 | -19.8 | 20.44 | 89.8 | 0 | 0 | 120 | 120 | 19.8 | 63.53 | 95 | 16.39 | 0 | 0 | 0 | Normal
2025-05-23 09:00 | 143 | 5 | Autumn | 9 | 0 | -18 | 5.95 | 21.8 | 0 | 0 | 2.06 | 2.06 | 18 | 67.45 | 68.84 | -65.39 | 0 | 0 | 0 | Battery-supported
2025-05-23 10:00 | 143 | 5 | Autumn | 10 | 0 | -19.8 | 6.55 | 46.6 | 0 | 0 | 3.97 | 3.97 | 19.8 | 59.59 | 46.6 | -55.62 | 0 | 0 | 0 | Battery-supported
2025-05-23 11:00 | 143 | 5 | Autumn | 11 | 0 | -17.4 | 17.52 | 77.2 | 0 | 0 | 120 | 120 | 17.4 | 68.88 | 65.41 | 51.12 | 0 | 0 | 0 | Normal
2025-05-23 12:00 | 143 | 5 | Autumn | 12 | 0 | -20.1 | 9.32 | 92.3 | 0 | 0 | 27.59 | 27.59 | 20.1 | 60.28 | 52.33 | -32.69 | 0 | 0 | 0 | Battery-supported
2025-05-23 13:00 | 143 | 5 | Autumn | 13 | 0 | -20.3 | 9.68 | 45 | 0 | 0 | 33.04 | 33.04 | 20.3 | 62.41 | 40.58 | -29.37 | 0 | 0 | 0 | Battery-supported
2025-05-23 14:00 | 143 | 5 | Autumn | 14 | 0 | -17.8 | 4.15 | 24.7 | 0 | 0 | 0.04 | 0.04 | 17.8 | 62.73 | 15.51 | -62.69 | 0 | 0 | 0 | Battery-supported
2025-05-23 15:00 | 143 | 5 | Autumn | 15 | 0 | -22.2 | 17.06 | 21.1 | 0 | 0 | 120 | 120 | 22.2 | 65.01 | 35.74 | 54.99 | 0 | 0 | 0 | Normal
2025-05-23 16:00 | 143 | 5 | Autumn | 16 | 0 | -13.9 | 12.77 | 79.2 | 0 | 0 | 111.49 | 111.49 | 13.9 | 50.12 | 58.33 | 61.37 | 0 | 0 | 0 | Normal
2025-05-23 17:00 | 143 | 5 | Autumn | 17 | 0 | -19.3 | 7.67 | 60.3 | 0 | 0 | 10.15 | 10.15 | 19.3 | 63.3 | 37.07 | -53.15 | 0 | 0 | 0 | Battery-supported
2025-05-23 18:00 | 143 | 5 | Autumn | 18 | 0 | -19.3 | 6.58 | 23.6 | 0 | 0 | 4.09 | 4.09 | 19.3 | 62.61 | 15 | -55.17 | 3.35 | 1.25 | 0 | Diesel-backup
2025-05-23 19:00 | 143 | 5 | Autumn | 19 | 0 | -18.9 | 18.65 | 40.8 | 0 | 0 | 120 | 120 | 18.9 | 60.85 | 36.77 | 59.15 | 0 | 0 | 0 | Normal
2025-05-23 20:00 | 143 | 5 | Autumn | 20 | 0 | -16 | 6 | 14.9 | 0 | 0 | 2.19 | 2.19 | 16 | 59.29 | 15 | -54.42 | 2.68 | 1.004 | 0 | Diesel-backup
2025-05-23 21:00 | 143 | 5 | Autumn | 21 | 0 | -18.4 | 3.26 | 62.3 | 0 | 0 | 0 | 0 | 18.4 | 55.17 | 15 | 0 | 55.17 | 17.654 | 0 | Diesel-backup
2025-05-23 22:00 | 143 | 5 | Autumn | 22 | 0 | -23.6 | 19.25 | 38.6 | 0 | 0 | 120 | 120 | 23.6 | 55.05 | 38.9 | 64.95 | 0 | 0 | 0 | Normal
2025-05-23 23:00 | 143 | 5 | Autumn | 23 | 0 | -17 | 19.47 | 81.8 | 0 | 0 | 120 | 120 | 17 | 54.14 | 63.14 | 65.86 | 0 | 0 | 0 | Normal
2025-05-24 | 144 | 5 | Autumn | 0 | 0 | -21 | 6 | 83.8 | 0 | 0 | 2.19 | 2.19 | 21 | 53.56 | 42.59 | -51.37 | 0 | 0 | 0 | Battery-supported
2025-05-24 01:00 | 144 | 5 | Autumn | 1 | 0 | -20 | 27.93 | 37.3 | 0 | 0 | 120 | 120 | 20 | 61.14 | 64.25 | 58.86 | 0 | 0 | 0 | Normal
2025-05-24 02:00 | 144 | 5 | Autumn | 2 | 0 | -23.1 | 8.71 | 40.8 | 0 | 0 | 19.79 | 19.79 | 23.1 | 62.26 | 47.26 | -42.47 | 0 | 0 | 0 | Battery-supported
2025-05-24 03:00 | 144 | 5 | Autumn | 3 | 0 | -19.1 | 6.05 | 59.4 | 0 | 0 | 2.32 | 2.32 | 19.1 | 50.11 | 28.15 | -47.79 | 0 | 0 | 0 | Battery-supported
2025-05-24 04:00 | 144 | 5 | Autumn | 4 | 0 | -21.7 | 12.56 | 56.2 | 0 | 0 | 104.09 | 104.09 | 21.7 | 61.62 | 43.78 | 42.47 | 0 | 0 | 0 | Normal
2025-05-24 05:00 | 144 | 5 | Autumn | 5 | 0 | -20 | 3.73 | 51.2 | 0 | 0 | 0 | 0 | 20 | 56.63 | 21.12 | -56.63 | 0 | 0 | 0 | Battery-supported
2025-05-24 06:00 | 144 | 5 | Autumn | 6 | 0 | -20.9 | 4.91 | 54.2 | 0 | 0 | 0.39 | 0.39 | 20.9 | 58.02 | 15 | -15.31 | 42.32 | 13.688 | 0 | Diesel-backup
2025-05-24 07:00 | 144 | 5 | Autumn | 7 | 0 | -16 | 10.98 | 20.5 | 0 | 0 | 58.58 | 58.58 | 16 | 50.27 | 18.06 | 8.31 | 0 | 0 | 0 | Normal
2025-05-24 08:00 | 144 | 5 | Autumn | 8 | 0 | -15.9 | 9.83 | 59 | 0 | 0 | 35.5 | 35.5 | 15.9 | 57.53 | 15 | -7.65 | 14.38 | 5.167 | 0 | Diesel-backup
2025-05-24 09:00 | 144 | 5 | Autumn | 9 | 0 | -20.2 | 15.57 | 76.8 | 0 | 0 | 120 | 120 | 20.2 | 62.12 | 36.3 | 57.88 | 0 | 0 | 0 | Normal
2025-05-24 10:00 | 144 | 5 | Autumn | 10 | 0 | -20.1 | 4.13 | 29.5 | 0 | 0 | 0.03 | 0.03 | 20.1 | 59.29 | 15 | -53.25 | 6.01 | 2.223 | 0 | Diesel-backup
2025-05-24 11:00 | 144 | 5 | Autumn | 11 | 0 | -21.1 | 25.25 | 74.6 | 0 | 0 | 120 | 120 | 21.1 | 56.62 | 38.32 | 63.38 | 0 | 0 | 0 | Normal
2025-05-24 12:00 | 144 | 5 | Autumn | 12 | 0 | -17.8 | 7.07 | 4.7 | 0 | 0 | 6.37 | 6.37 | 17.8 | 58.25 | 17.57 | -51.88 | 0 | 0 | 0 | Battery-supported
2025-05-24 13:00 | 144 | 5 | Autumn | 13 | 0 | -21 | 9.62 | 36.7 | 0 | 0 | 32.08 | 32.08 | 21 | 61.43 | 15 | -6.43 | 22.92 | 7.982 | 0 | Diesel-backup
2025-05-24 14:00 | 144 | 5 | Autumn | 14 | 0 | -21.2 | 6.87 | 26.5 | 0 | 0 | 5.36 | 5.36 | 21.2 | 59.84 | 15 | 0 | 54.48 | 17.434 | 0 | Diesel-backup
2025-05-24 15:00 | 144 | 5 | Autumn | 15 | 0 | -18.1 | 3.7 | 0 | 0 | 0 | 0 | 0 | 18.1 | 63.43 | 15 | 0 | 63.43 | 20.298 | 0 | Diesel-backup
2025-05-24 16:00 | 144 | 5 | Autumn | 16 | 0 | -21.4 | 8.99 | 65.6 | 0 | 0 | 23.16 | 23.16 | 21.4 | 65.38 | 15 | 0 | 42.22 | 13.661 | 0 | Diesel-backup
2025-05-24 17:00 | 144 | 5 | Autumn | 17 | 0 | -20.3 | 13.67 | 59.9 | 0 | 0 | 120 | 120 | 20.3 | 60.93 | 36.74 | 59.07 | 0 | 0 | 0 | Normal
2025-05-24 18:00 | 144 | 5 | Autumn | 18 | 0 | -23.7 | 8.18 | 79.6 | 0 | 0 | 14.35 | 14.35 | 23.7 | 65.45 | 16.3 | -51.1 | 0 | 0 | 0 | Battery-supported
2025-05-24 19:00 | 144 | 5 | Autumn | 19 | 0 | -18.7 | 5.28 | 35.1 | 0 | 0 | 0.79 | 0.79 | 18.7 | 62.59 | 15 | -3.24 | 58.56 | 18.738 | 0 | Diesel-backup
2025-05-24 20:00 | 144 | 5 | Autumn | 20 | 0 | -16 | 15.87 | 67.4 | 0 | 0 | 120 | 120 | 16 | 56.09 | 38.52 | 63.91 | 0 | 0 | 0 | Normal
2025-05-24 21:00 | 144 | 5 | Autumn | 21 | 0 | -18.7 | 16.22 | 59.2 | 0 | 0 | 120 | 120 | 18.7 | 45 | 66.12 | 75 | 0 | 0 | 0 | Normal
2025-05-24 22:00 | 144 | 5 | Autumn | 22 | 0 | -17 | 7.91 | 30.3 | 0 | 0 | 12 | 12 | 17 | 56.79 | 48.2 | -44.79 | 0 | 0 | 0 | Battery-supported
2025-05-24 23:00 | 144 | 5 | Autumn | 23 | 0 | -22.1 | 11.39 | 71.2 | 0 | 0 | 68.75 | 68.75 | 22.1 | 56.64 | 52.66 | 12.11 | 0 | 0 | 0 | Normal
2025-05-25 | 145 | 5 | Autumn | 0 | 0 | -19.9 | 15.85 | 85.8 | 0 | 0 | 120 | 120 | 19.9 | 55.98 | 76.22 | 64.02 | 0 | 0 | 0 | Normal
2025-05-25 01:00 | 145 | 5 | Autumn | 1 | 0 | -22.5 | 13.62 | 16.6 | 0 | 0 | 120 | 120 | 22.5 | 58.19 | 95 | 51.04 | 0 | 0 | 0 | Normal
2025-05-25 02:00 | 145 | 5 | Autumn | 2 | 0 | -20.9 | 11.23 | 0 | 0 | 0 | 64.65 | 64.65 | 20.9 | 50.13 | 95 | 0 | 0 | 0 | 0 | Normal
2025-05-25 03:00 | 145 | 5 | Autumn | 3 | 0 | -18.7 | 13.29 | 44.5 | 0 | 0 | 120 | 120 | 18.7 | 50.95 | 95 | 0 | 0 | 0 | 0 | Normal
2025-05-25 04:00 | 145 | 5 | Autumn | 4 | 0 | -20.2 | 11.88 | 80.6 | 0 | 0 | 82.36 | 82.36 | 20.2 | 55.15 | 95 | 0 | 0 | 0 | 0 | Normal
2025-05-25 05:00 | 145 | 5 | Autumn | 5 | 0 | -23.5 | 9.33 | 82.1 | 0 | 0 | 27.73 | 27.73 | 23.5 | 57.7 | 83.01 | -29.97 | 0 | 0 | 0 | Battery-supported
2025-05-25 06:00 | 145 | 5 | Autumn | 6 | 0 | -23.3 | 4.08 | 57.2 | 0 | 0 | 0.03 | 0.03 | 23.3 | 53.76 | 61.52 | -53.73 | 0 | 0 | 0 | Battery-supported
2025-05-25 07:00 | 145 | 5 | Autumn | 7 | 0 | -23.5 | 4.78 | 43.6 | 0 | 0 | 0.29 | 0.29 | 23.5 | 59.87 | 37.69 | -59.58 | 0 | 0 | 0 | Battery-supported
2025-05-25 08:00 | 145 | 5 | Autumn | 8 | 0 | -19.3 | 12.19 | 61.9 | 0 | 0 | 91.85 | 91.85 | 19.3 | 64.58 | 47.72 | 27.27 | 0 | 0 | 0 | Normal
2025-05-25 09:00 | 145 | 5 | Autumn | 9 | 0 | -15.9 | 6.84 | 83.8 | 0 | 0 | 5.21 | 5.21 | 15.9 | 57.38 | 26.86 | -52.17 | 0 | 0 | 0 | Battery-supported
2025-05-25 10:00 | 145 | 5 | Autumn | 10 | 0 | -17.4 | 11.93 | 87.5 | 0 | 0 | 83.85 | 83.85 | 17.4 | 64.41 | 34.01 | 19.44 | 0 | 0 | 0 | Normal
2025-05-25 11:00 | 145 | 5 | Autumn | 11 | 0 | -24.6 | 4.01 | 66.3 | 0 | 0 | 0.02 | 0.02 | 24.6 | 69.73 | 15 | -47.52 | 22.19 | 7.748 | 0 | Diesel-backup
2025-05-25 12:00 | 145 | 5 | Autumn | 12 | 0 | -17.3 | 5.63 | 18.5 | 0 | 0 | 1.35 | 1.35 | 17.3 | 61.85 | 15 | 0 | 60.5 | 19.36 | 0 | Diesel-backup
2025-05-25 13:00 | 145 | 5 | Autumn | 13 | 0 | -18.4 | 8.2 | 49.6 | 0 | 0 | 14.53 | 14.53 | 18.4 | 59.4 | 15 | 0 | 44.87 | 14.366 | 0 | Diesel-backup
2025-05-25 14:00 | 145 | 5 | Autumn | 14 | 0 | -23.8 | 1.66 | 46.9 | 0 | 0 | 0 | 0 | 23.8 | 66.12 | 15 | 0 | 66.12 | 21.158 | 0 | Diesel-backup
2025-05-25 15:00 | 145 | 5 | Autumn | 15 | 0 | -21.1 | 5.15 | 43.4 | 0 | 0 | 0.63 | 0.63 | 21.1 | 67.43 | 15 | 0 | 66.8 | 21.376 | 0 | Diesel-backup
2025-05-25 16:00 | 145 | 5 | Autumn | 16 | 0 | -18 | 6.11 | 69.1 | 0 | 0 | 2.49 | 2.49 | 18 | 55.2 | 15 | 0 | 52.71 | 16.867 | 0 | Diesel-backup
2025-05-25 17:00 | 145 | 5 | Autumn | 17 | 0 | -19.2 | 10.29 | 62.2 | 0 | 0 | 43.81 | 43.81 | 19.2 | 56.66 | 15 | 0 | 12.85 | 4.641 | 0 | Diesel-backup
2025-05-25 18:00 | 145 | 5 | Autumn | 18 | 0 | -23.3 | 7.89 | 71.8 | 0 | 0 | 11.84 | 11.84 | 23.3 | 64.67 | 15 | 0 | 52.83 | 16.906 | 0 | Diesel-backup
2025-05-25 19:00 | 145 | 5 | Autumn | 19 | 0 | -19.1 | 10.62 | 44.6 | 0 | 0 | 50.52 | 50.52 | 19.1 | 62.02 | 15 | 0 | 11.5 | 4.173 | 0 | Diesel-backup
2025-05-25 20:00 | 145 | 5 | Autumn | 20 | 0 | -25.1 | 9.54 | 61.1 | 0 | 0 | 30.84 | 30.84 | 25.1 | 67.71 | 15 | 0 | 36.87 | 12.182 | 0 | Diesel-backup
2025-05-25 21:00 | 145 | 5 | Autumn | 21 | 0 | -20.9 | 7.69 | 39.8 | 0 | 0 | 10.3 | 10.3 | 20.9 | 57.99 | 15 | 0 | 47.69 | 15.261 | 0 | Diesel-backup
2025-05-25 22:00 | 145 | 5 | Autumn | 22 | 0 | -17.9 | 6.14 | 54 | 0 | 0 | 2.58 | 2.58 | 17.9 | 53.87 | 15 | 0 | 51.29 | 16.413 | 0 | Diesel-backup
2025-05-25 23:00 | 145 | 5 | Autumn | 23 | 0 | -20.4 | 9.73 | 32.1 | 0 | 0 | 33.84 | 33.84 | 20.4 | 55.48 | 15 | 0 | 21.64 | 7.572 | 0 | Diesel-backup
2025-05-26 | 146 | 5 | Autumn | 0 | 0 | -21.7 | 18.41 | 11.7 | 0 | 0 | 120 | 120 | 21.7 | 55.49 | 38.74 | 64.51 | 0 | 0 | 0 | Normal
2025-05-26 01:00 | 146 | 5 | Autumn | 1 | 0 | -18.6 | 6.13 | 54.7 | 0 | 0 | 2.55 | 2.55 | 18.6 | 56.87 | 17.01 | -54.32 | 0 | 0 | 0 | Battery-supported
2025-05-26 02:00 | 146 | 5 | Autumn | 2 | 0 | -18.4 | 24.8 | 25.2 | 0 | 0 | 120 | 120 | 18.4 | 58.2 | 39.75 | 61.8 | 0 | 0 | 0 | Normal
2025-05-26 03:00 | 146 | 5 | Autumn | 3 | 0 | -17.7 | 9.87 | 73 | 0 | 0 | 36.18 | 36.18 | 17.7 | 51.52 | 33.62 | -15.34 | 0 | 0 | 0 | Battery-supported
2025-05-26 04:00 | 146 | 5 | Autumn | 4 | 0 | -18.7 | 15.2 | 72.8 | 0 | 0 | 120 | 120 | 18.7 | 55.26 | 57.44 | 64.74 | 0 | 0 | 0 | Normal
2025-05-26 05:00 | 146 | 5 | Autumn | 5 | 0 | -18.2 | 11.52 | 41.6 | 0 | 0 | 72.2 | 72.2 | 18.2 | 52.17 | 64.81 | 20.03 | 0 | 0 | 0 | Normal
2025-05-26 06:00 | 146 | 5 | Autumn | 6 | 0 | -19 | 12.52 | 79 | 0 | 0 | 102.71 | 102.71 | 19 | 49.16 | 84.52 | 53.55 | 0 | 0 | 0 | Normal
2025-05-26 07:00 | 146 | 5 | Autumn | 7 | 0 | -20 | 5.13 | 6.4 | 0 | 0 | 0.61 | 0.61 | 20 | 48.33 | 65.43 | -47.72 | 0 | 0 | 0 | Battery-supported
2025-05-26 08:00 | 146 | 5 | Autumn | 8 | 0 | -20.4 | 6.82 | 23.8 | 0 | 0 | 5.12 | 5.12 | 20.4 | 68.1 | 40.24 | -62.98 | 0 | 0 | 0 | Battery-supported
2025-05-26 09:00 | 146 | 5 | Autumn | 9 | 0 | -21.1 | 2.79 | 86 | 0 | 0 | 0 | 0 | 21.1 | 67.3 | 15 | -63.1 | 4.2 | 1.563 | 0 | Diesel-backup
2025-05-26 10:00 | 146 | 5 | Autumn | 10 | 0 | -23.3 | 8.1 | 86.1 | 0 | 0 | 13.62 | 13.62 | 23.3 | 67.91 | 15 | 0 | 54.29 | 17.373 | 0 | Diesel-backup
2025-05-26 11:00 | 146 | 5 | Autumn | 11 | 0 | -22.7 | 13.21 | 68.5 | 0 | 0 | 120 | 120 | 22.7 | 69.69 | 33.51 | 50.31 | 0 | 0 | 0 | Normal
2025-05-26 12:00 | 146 | 5 | Autumn | 12 | 0 | -21.2 | 8.14 | 81.1 | 0 | 0 | 13.98 | 13.98 | 21.2 | 61 | 15 | -46.29 | 0.73 | 0.277 | 0 | Diesel-backup
2025-05-26 13:00 | 146 | 5 | Autumn | 13 | 0 | -20.1 | 15.68 | 44 | 0 | 0 | 120 | 120 | 20.1 | 66.66 | 34.63 | 53.34 | 0 | 0 | 0 | Normal
2025-05-26 14:00 | 146 | 5 | Autumn | 14 | 0 | -17.4 | 7.24 | 80.7 | 0 | 0 | 7.32 | 7.32 | 17.4 | 61.79 | 15 | -49.07 | 5.4 | 2.001 | 0 | Diesel-backup
2025-05-26 15:00 | 146 | 5 | Autumn | 15 | 0 | -20.7 | 5.88 | 76 | 0 | 0 | 1.89 | 1.89 | 20.7 | 61.98 | 15 | 0 | 60.09 | 19.229 | 0 | Diesel-backup
2025-05-26 16:00 | 146 | 5 | Autumn | 16 | 0 | -18.4 | 6.64 | 71.1 | 0 | 0 | 4.33 | 4.33 | 18.4 | 52.18 | 15 | 0 | 47.85 | 15.312 | 0 | Diesel-backup
2025-05-26 17:00 | 146 | 5 | Autumn | 17 | 0 | -18.2 | 13.95 | 60 | 0 | 0 | 120 | 120 | 18.2 | 55.48 | 38.74 | 64.52 | 0 | 0 | 0 | Normal
2025-05-26 18:00 | 146 | 5 | Autumn | 18 | 0 | -21.1 | 21.79 | 80.8 | 0 | 0 | 120 | 120 | 21.1 | 70.98 | 56.78 | 49.02 | 0 | 0 | 0 | Normal
2025-05-26 19:00 | 146 | 5 | Autumn | 19 | 0 | -19.3 | 26.22 | 66.3 | 0 | 0 | 120 | 120 | 19.3 | 69.04 | 75.54 | 50.96 | 0 | 0 | 0 | Normal
2025-05-26 20:00 | 146 | 5 | Autumn | 20 | 0 | -21.1 | 13.12 | 10.9 | 0 | 0 | 120 | 120 | 21.1 | 58.43 | 95 | 52.89 | 0 | 0 | 0 | Normal
2025-05-26 21:00 | 146 | 5 | Autumn | 21 | 0 | -17.7 | 15.27 | 59.1 | 0 | 0 | 120 | 120 | 17.7 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-05-26 22:00 | 146 | 5 | Autumn | 22 | 0 | -19.2 | 3.28 | 69.7 | 0 | 0 | 0 | 0 | 19.2 | 59.41 | 71.24 | -59.41 | 0 | 0 | 0 | Battery-supported
2025-05-26 23:00 | 146 | 5 | Autumn | 23 | 0 | -23.2 | 3.96 | 41.5 | 0 | 0 | 0.01 | 0.01 | 23.2 | 57.88 | 48.09 | -57.87 | 0 | 0 | 0 | Battery-supported
2025-05-27 | 147 | 5 | Autumn | 0 | 0 | -20.4 | 5.29 | 67.3 | 0 | 0 | 0.8 | 0.8 | 20.4 | 52.52 | 27.4 | -51.72 | 0 | 0 | 0 | Battery-supported
2025-05-27 01:00 | 147 | 5 | Autumn | 1 | 0 | -17.1 | 19.09 | 83.3 | 0 | 0 | 120 | 120 | 17.1 | 47.16 | 54.21 | 72.84 | 0 | 0 | 0 | Normal
2025-05-27 02:00 | 147 | 5 | Autumn | 2 | 0 | -21.1 | 18.93 | 58.1 | 0 | 0 | 120 | 120 | 21.1 | 51.13 | 79.55 | 68.87 | 0 | 0 | 0 | Normal
2025-05-27 03:00 | 147 | 5 | Autumn | 3 | 0 | -19.8 | 29.61 | 79.8 | 0 | 0 | 0 | 0 | 19.8 | 60.02 | 55.54 | -60.02 | 0 | 0 | 0 | Battery-supported
2025-05-27 04:00 | 147 | 5 | Autumn | 4 | 0 | -19.5 | 5.21 | 79.7 | 0 | 0 | 0.7 | 0.7 | 19.5 | 55.5 | 33.62 | -54.8 | 0 | 0 | 0 | Battery-supported
2025-05-27 05:00 | 147 | 5 | Autumn | 5 | 0 | -23 | 8.72 | 73.3 | 0 | 0 | 19.91 | 19.91 | 23 | 50.83 | 21.25 | -30.92 | 0 | 0 | 0 | Battery-supported
2025-05-27 06:00 | 147 | 5 | Autumn | 6 | 0 | -19.6 | 2.78 | 3.1 | 0 | 0 | 0 | 0 | 19.6 | 51.79 | 15 | -15.63 | 36.16 | 11.979 | 0 | Diesel-backup
2025-05-27 07:00 | 147 | 5 | Autumn | 7 | 0 | -23.8 | 3.54 | 49.7 | 0 | 0 | 0 | 0 | 23.8 | 65.13 | 15 | 0 | 65.13 | 20.842 | 0 | Diesel-backup
2025-05-27 08:00 | 147 | 5 | Autumn | 8 | 0 | -22.1 | 7.71 | 78.3 | 0 | 0 | 10.44 | 10.44 | 22.1 | 66.31 | 15 | 0 | 55.87 | 17.878 | 0 | Diesel-backup
2025-05-27 09:00 | 147 | 5 | Autumn | 9 | 0 | -18.4 | 5.37 | 39.5 | 0 | 0 | 0.92 | 0.92 | 18.4 | 55.81 | 15 | 0 | 54.89 | 17.565 | 0 | Diesel-backup
2025-05-27 10:00 | 147 | 5 | Autumn | 10 | 0 | -20 | 5.41 | 10.8 | 0 | 0 | 0.98 | 0.98 | 20 | 60.4 | 15 | 0 | 59.42 | 19.014 | 0 | Diesel-backup
2025-05-27 11:00 | 147 | 5 | Autumn | 11 | 0 | -21.4 | 6.33 | 13.3 | 0 | 0 | 3.17 | 3.17 | 21.4 | 63.96 | 15 | 0 | 60.79 | 19.453 | 0 | Diesel-backup
2025-05-27 12:00 | 147 | 5 | Autumn | 12 | 0 | -19.8 | 20.32 | 54.8 | 0 | 0 | 120 | 120 | 19.8 | 66.6 | 34.65 | 53.4 | 0 | 0 | 0 | Normal
2025-05-27 13:00 | 147 | 5 | Autumn | 13 | 0 | -20.9 | 16.97 | 70.7 | 0 | 0 | 120 | 120 | 20.9 | 63.51 | 55.44 | 56.49 | 0 | 0 | 0 | Normal
2025-05-27 14:00 | 147 | 5 | Autumn | 14 | 0 | -20.7 | 4.77 | 14.4 | 0 | 0 | 0.29 | 0.29 | 20.7 | 69.21 | 27.87 | -68.92 | 0 | 0 | 0 | Battery-supported
2025-05-27 15:00 | 147 | 5 | Autumn | 15 | 0 | -19.3 | 16.7 | 36.6 | 0 | 0 | 120 | 120 | 19.3 | 63.35 | 48.72 | 56.65 | 0 | 0 | 0 | Normal
2025-05-27 16:00 | 147 | 5 | Autumn | 16 | 0 | -22.3 | 5.66 | 56 | 0 | 0 | 1.41 | 1.41 | 22.3 | 56.13 | 26.83 | -54.72 | 0 | 0 | 0 | Battery-supported
2025-05-27 17:00 | 147 | 5 | Autumn | 17 | 0 | -20.7 | 3.26 | 59.6 | 0 | 0 | 0 | 0 | 20.7 | 65.84 | 15 | -29.58 | 36.26 | 12.01 | 0 | Diesel-backup
2025-05-27 18:00 | 147 | 5 | Autumn | 18 | 0 | -21.4 | 6.18 | 31.4 | 0 | 0 | 2.69 | 2.69 | 21.4 | 63.67 | 15 | 0 | 60.98 | 19.514 | 0 | Diesel-backup
2025-05-27 19:00 | 147 | 5 | Autumn | 19 | 0 | -24.2 | 10.94 | 71.8 | 0 | 0 | 57.64 | 57.64 | 24.2 | 65.18 | 15 | 0 | 7.54 | 2.774 | 0 | Diesel-backup
2025-05-27 20:00 | 147 | 5 | Autumn | 20 | 0 | -22.8 | 5.13 | 45.5 | 0 | 0 | 0.61 | 0.61 | 22.8 | 67.38 | 15 | 0 | 66.77 | 21.366 | 0 | Diesel-backup
2025-05-27 21:00 | 147 | 5 | Autumn | 21 | 0 | -17.3 | 13.01 | 53.3 | 0 | 0 | 120 | 120 | 17.3 | 51.31 | 40.28 | 68.69 | 0 | 0 | 0 | Normal
2025-05-27 22:00 | 147 | 5 | Autumn | 22 | 0 | -19.9 | 6.47 | 64.3 | 0 | 0 | 3.67 | 3.67 | 19.9 | 55.7 | 19.47 | -52.03 | 0 | 0 | 0 | Battery-supported
2025-05-27 23:00 | 147 | 5 | Autumn | 23 | 0 | -23.7 | 11.4 | 42.8 | 0 | 0 | 69.01 | 69.01 | 23.7 | 56.61 | 24.03 | 12.4 | 0 | 0 | 0 | Normal
2025-05-28 | 148 | 5 | Autumn | 0 | 0 | -24.3 | 4.74 | 52.6 | 0 | 0 | 0.27 | 0.27 | 24.3 | 57.05 | 15 | -22.57 | 34.21 | 11.419 | 0 | Diesel-backup
2025-05-28 01:00 | 148 | 5 | Autumn | 1 | 0 | -21.1 | 9.27 | 61 | 0 | 0 | 26.89 | 26.89 | 21.1 | 60.53 | 15 | 0 | 33.64 | 11.254 | 0 | Diesel-backup
2025-05-28 02:00 | 148 | 5 | Autumn | 2 | 0 | -17.5 | 5.25 | 16.3 | 0 | 0 | 0.75 | 0.75 | 17.5 | 52.96 | 15 | 0 | 52.21 | 16.707 | 0 | Diesel-backup
2025-05-28 03:00 | 148 | 5 | Autumn | 3 | 0 | -21.3 | 7.87 | 16.2 | 0 | 0 | 11.68 | 11.68 | 21.3 | 57.94 | 15 | 0 | 46.26 | 14.803 | 0 | Diesel-backup
2025-05-28 04:00 | 148 | 5 | Autumn | 4 | 0 | -18 | 25.13 | 64.3 | 0 | 0 | 120 | 120 | 18 | 50.69 | 40.51 | 69.31 | 0 | 0 | 0 | Normal
2025-05-28 05:00 | 148 | 5 | Autumn | 5 | 0 | -20.1 | 7.03 | 64.1 | 0 | 0 | 6.16 | 6.16 | 20.1 | 59.36 | 19.23 | -53.2 | 0 | 0 | 0 | Battery-supported
2025-05-28 06:00 | 148 | 5 | Autumn | 6 | 0 | -19.9 | 3.91 | 70.8 | 0 | 0 | 0.01 | 0.01 | 19.9 | 55.72 | 15 | -10.57 | 45.14 | 14.446 | 0 | Diesel-backup
2025-05-28 07:00 | 148 | 5 | Autumn | 7 | 0 | -23.8 | 9.62 | 54.3 | 0 | 0 | 32.08 | 32.08 | 23.8 | 57.45 | 15 | 0 | 25.37 | 8.756 | 0 | Diesel-backup
2025-05-28 08:00 | 148 | 5 | Autumn | 8 | 0 | -18.8 | 9.72 | 68.1 | 0 | 0 | 33.68 | 33.68 | 18.8 | 66.87 | 15 | 0 | 33.19 | 11.123 | 0 | Diesel-backup
2025-05-28 09:00 | 148 | 5 | Autumn | 9 | 0 | -21.6 | 9.68 | 96.7 | 0 | 0 | 33.04 | 33.04 | 21.6 | 63.25 | 15 | 0 | 30.21 | 10.239 | 0 | Diesel-backup
2025-05-28 10:00 | 148 | 5 | Autumn | 10 | 0 | -19 | 12.61 | 60.5 | 0 | 0 | 105.82 | 105.82 | 19 | 62.72 | 30.86 | 43.1 | 0 | 0 | 0 | Normal
2025-05-28 11:00 | 148 | 5 | Autumn | 11 | 0 | -22.7 | 6.83 | 66.4 | 0 | 0 | 5.17 | 5.17 | 22.7 | 60.89 | 15 | -39.65 | 16.07 | 5.737 | 0 | Diesel-backup
2025-05-28 12:00 | 148 | 5 | Autumn | 12 | 0 | -20.5 | 13.33 | 85.4 | 0 | 0 | 120 | 120 | 20.5 | 61 | 36.71 | 59 | 0 | 0 | 0 | Normal
2025-05-28 13:00 | 148 | 5 | Autumn | 13 | 0 | -20.1 | 9.04 | 62.4 | 0 | 0 | 23.8 | 23.8 | 20.1 | 66.21 | 19.75 | -42.41 | 0 | 0 | 0 | Battery-supported
2025-05-28 14:00 | 148 | 5 | Autumn | 14 | 0 | -21.2 | 3.76 | 39.2 | 0 | 0 | 0 | 0 | 21.2 | 64 | 15 | -11.87 | 52.13 | 16.682 | 0 | Diesel-backup
2025-05-28 15:00 | 148 | 5 | Autumn | 15 | 0 | -20 | 14.41 | 61.8 | 0 | 0 | 120 | 120 | 20 | 63.37 | 35.84 | 56.63 | 0 | 0 | 0 | Normal
2025-05-28 16:00 | 148 | 5 | Autumn | 16 | 0 | -21.5 | 10.18 | 60.9 | 0 | 0 | 41.72 | 41.72 | 21.5 | 64.14 | 26.87 | -22.42 | 0 | 0 | 0 | Battery-supported
2025-05-28 17:00 | 148 | 5 | Autumn | 17 | 0 | -22.3 | 12.93 | 18.8 | 0 | 0 | 117.37 | 117.37 | 22.3 | 65.1 | 46.11 | 52.27 | 0 | 0 | 0 | Normal
2025-05-28 18:00 | 148 | 5 | Autumn | 18 | 0 | -17.4 | 4.07 | 57.8 | 0 | 0 | 0.03 | 0.03 | 17.4 | 58.24 | 22.82 | -58.21 | 0 | 0 | 0 | Battery-supported
2025-05-28 19:00 | 148 | 5 | Autumn | 19 | 0 | -18.6 | 14.9 | 66.5 | 0 | 0 | 120 | 120 | 18.6 | 59.72 | 45.01 | 60.28 | 0 | 0 | 0 | Normal
2025-05-28 20:00 | 148 | 5 | Autumn | 20 | 0 | -22.6 | 28.85 | 51.6 | 0 | 0 | 0 | 0 | 22.6 | 64.42 | 19.24 | -64.42 | 0 | 0 | 0 | Battery-supported
2025-05-28 21:00 | 148 | 5 | Autumn | 21 | 0 | -19.7 | 3.86 | 47.1 | 0 | 0 | 0.01 | 0.01 | 19.7 | 53.54 | 15 | -10.6 | 42.93 | 13.853 | 0 | Diesel-backup
2025-05-28 22:00 | 148 | 5 | Autumn | 22 | 0 | -22.5 | 16.1 | 36.3 | 0 | 0 | 120 | 120 | 22.5 | 59.35 | 37.32 | 60.65 | 0 | 0 | 0 | Normal
2025-05-28 23:00 | 148 | 5 | Autumn | 23 | 0 | -23.5 | 10.2 | 27.1 | 0 | 0 | 42.1 | 42.1 | 23.5 | 60.22 | 30.07 | -18.12 | 0 | 0 | 0 | Battery-supported
2025-05-29 | 149 | 5 | Autumn | 0 | 0 | -18.8 | 9.12 | 32.9 | 0 | 0 | 24.84 | 24.84 | 18.8 | 59.07 | 16.38 | -34.23 | 0 | 0 | 0 | Battery-supported
2025-05-29 01:00 | 149 | 5 | Autumn | 1 | 0 | -24.8 | 15.03 | 35.2 | 0 | 0 | 120 | 120 | 24.8 | 62.57 | 37.51 | 57.43 | 0 | 0 | 0 | Normal
2025-05-29 02:00 | 149 | 5 | Autumn | 2 | 0 | -19 | 14.11 | 58.9 | 0 | 0 | 120 | 120 | 19 | 50.46 | 63.1 | 69.54 | 0 | 0 | 0 | Normal
2025-05-29 03:00 | 149 | 5 | Autumn | 3 | 0 | -21.6 | 18.43 | 43.6 | 0 | 0 | 120 | 120 | 21.6 | 53.92 | 87.42 | 66.08 | 0 | 0 | 0 | Normal
2025-05-29 04:00 | 149 | 5 | Autumn | 4 | 0 | -21.5 | 4.19 | 44.8 | 0 | 0 | 0.05 | 0.05 | 21.5 | 60.22 | 63.35 | -60.17 | 0 | 0 | 0 | Battery-supported
2025-05-29 05:00 | 149 | 5 | Autumn | 5 | 0 | -20.2 | 18.83 | 17.5 | 0 | 0 | 120 | 120 | 20.2 | 57.84 | 86.23 | 62.16 | 0 | 0 | 0 | Normal
2025-05-29 06:00 | 149 | 5 | Autumn | 6 | 0 | -19.8 | 11.39 | 29.4 | 0 | 0 | 68.75 | 68.75 | 19.8 | 58.96 | 89.83 | 9.79 | 0 | 0 | 0 | Normal
2025-05-29 07:00 | 149 | 5 | Autumn | 7 | 0 | -22.9 | 2.85 | 49.6 | 0 | 0 | 0 | 0 | 22.9 | 57.88 | 66.68 | -57.88 | 0 | 0 | 0 | Battery-supported
2025-05-29 08:00 | 149 | 5 | Autumn | 8 | 0 | -19.5 | 7.09 | 28 | 0 | 0 | 6.48 | 6.48 | 19.5 | 61.46 | 44.69 | -54.98 | 0 | 0 | 0 | Battery-supported
2025-05-29 09:00 | 149 | 5 | Autumn | 9 | 0 | -20.8 | 10.37 | 74 | 0 | 0 | 45.38 | 45.38 | 20.8 | 65.17 | 36.77 | -19.79 | 0 | 0 | 0 | Battery-supported
2025-05-29 10:00 | 149 | 5 | Autumn | 10 | 0 | -23.8 | 6.99 | 33.3 | 0 | 0 | 5.95 | 5.95 | 23.8 | 61.3 | 15 | -54.43 | 0.92 | 0.347 | 0 | Diesel-backup
2025-05-29 11:00 | 149 | 5 | Autumn | 11 | 0 | -21.4 | 8.45 | 66.3 | 0 | 0 | 16.98 | 16.98 | 21.4 | 63.61 | 15 | 0 | 46.63 | 14.922 | 0 | Diesel-backup
2025-05-29 12:00 | 149 | 5 | Autumn | 12 | 0 | -18 | 6.39 | 91.7 | 0 | 0 | 3.38 | 3.38 | 18 | 68.84 | 15 | 0 | 65.46 | 20.947 | 0 | Diesel-backup
2025-05-29 13:00 | 149 | 5 | Autumn | 13 | 0 | -17.4 | 37.42 | 39.5 | 0 | 0 | 0 | 0 | 17.4 | 59.08 | 15 | 0 | 59.08 | 18.906 | 0 | Diesel-backup
2025-05-29 14:00 | 149 | 5 | Autumn | 14 | 0 | -19.5 | 13.48 | 78 | 0 | 0 | 120 | 120 | 19.5 | 62.44 | 36.18 | 57.56 | 0 | 0 | 0 | Normal
2025-05-29 15:00 | 149 | 5 | Autumn | 15 | 0 | -23.7 | 9.62 | 38.8 | 0 | 0 | 32.08 | 32.08 | 23.7 | 65.89 | 22.66 | -33.81 | 0 | 0 | 0 | Battery-supported
2025-05-29 16:00 | 149 | 5 | Autumn | 16 | 0 | -20 | 4.68 | 38.1 | 0 | 0 | 0.23 | 0.23 | 20 | 69.01 | 15 | -19.15 | 49.63 | 15.883 | 0 | Diesel-backup
2025-05-29 17:00 | 149 | 5 | Autumn | 17 | 0 | -19.2 | 18.46 | 64.2 | 0 | 0 | 120 | 120 | 19.2 | 57.46 | 38.01 | 62.54 | 0 | 0 | 0 | Normal
2025-05-29 18:00 | 149 | 5 | Autumn | 18 | 0 | -19.5 | 12.48 | 70.2 | 0 | 0 | 101.35 | 101.35 | 19.5 | 65.2 | 51.32 | 36.15 | 0 | 0 | 0 | Normal
2025-05-29 19:00 | 149 | 5 | Autumn | 19 | 0 | -19.3 | 5.01 | 70.5 | 0 | 0 | 0.48 | 0.48 | 19.3 | 60.7 | 27.23 | -60.22 | 0 | 0 | 0 | Battery-supported
2025-05-29 20:00 | 149 | 5 | Autumn | 20 | 0 | -20.3 | 5.03 | 68.1 | 0 | 0 | 0.5 | 0.5 | 20.3 | 60.7 | 15 | -30.57 | 29.63 | 10.063 | 0 | Diesel-backup
2025-05-29 21:00 | 149 | 5 | Autumn | 21 | 0 | -21.2 | 8.58 | 80.5 | 0 | 0 | 18.35 | 18.35 | 21.2 | 49.5 | 15 | 0 | 31.15 | 10.52 | 0 | Diesel-backup
2025-05-29 22:00 | 149 | 5 | Autumn | 22 | 0 | -22.4 | 9.68 | 43.9 | 0 | 0 | 33.04 | 33.04 | 22.4 | 64.26 | 15 | 0 | 31.22 | 10.541 | 0 | Diesel-backup
2025-05-29 23:00 | 149 | 5 | Autumn | 23 | 0 | -25.2 | 13.3 | 36.8 | 0 | 0 | 120 | 120 | 25.2 | 63.09 | 35.94 | 56.91 | 0 | 0 | 0 | Normal
2025-05-30 | 150 | 5 | Autumn | 0 | 0 | -20.5 | 8.95 | 61.7 | 0 | 0 | 22.66 | 22.66 | 20.5 | 50.19 | 24.93 | -27.53 | 0 | 0 | 0 | Battery-supported
2025-05-30 01:00 | 150 | 5 | Autumn | 1 | 0 | -20.8 | 13.99 | 73.3 | 0 | 0 | 120 | 120 | 20.8 | 50.76 | 50.41 | 69.24 | 0 | 0 | 0 | Normal
2025-05-30 02:00 | 150 | 5 | Autumn | 2 | 0 | -20 | 7.01 | 31.8 | 0 | 0 | 6.05 | 6.05 | 20 | 52.42 | 31.86 | -46.37 | 0 | 0 | 0 | Battery-supported
2025-05-30 03:00 | 150 | 5 | Autumn | 3 | 0 | -24.1 | 8.96 | 51.8 | 0 | 0 | 22.78 | 22.78 | 24.1 | 61.1 | 16.54 | -38.32 | 0 | 0 | 0 | Battery-supported
2025-05-30 04:00 | 150 | 5 | Autumn | 4 | 0 | -19.8 | 18.89 | 58.4 | 0 | 0 | 120 | 120 | 19.8 | 54.29 | 40.72 | 65.71 | 0 | 0 | 0 | Normal
2025-05-30 05:00 | 150 | 5 | Autumn | 5 | 0 | -16.7 | 14.35 | 42.5 | 0 | 0 | 120 | 120 | 16.7 | 48.05 | 67.19 | 71.95 | 0 | 0 | 0 | Normal
2025-05-30 06:00 | 150 | 5 | Autumn | 6 | 0 | -21 | 9.29 | 67.4 | 0 | 0 | 27.17 | 27.17 | 21 | 55.68 | 55.79 | -28.51 | 0 | 0 | 0 | Battery-supported
2025-05-30 07:00 | 150 | 5 | Autumn | 7 | 0 | -21.3 | 11.18 | 76.1 | 0 | 0 | 63.4 | 63.4 | 21.3 | 61.37 | 56.54 | 2.03 | 0 | 0 | 0 | Normal
2025-05-30 08:00 | 150 | 5 | Autumn | 8 | 0 | -20.5 | 8.98 | 87.7 | 0 | 0 | 23.03 | 23.03 | 20.5 | 65.88 | 39.4 | -42.85 | 0 | 0 | 0 | Battery-supported
2025-05-30 09:00 | 150 | 5 | Autumn | 9 | 0 | -16.7 | 3.59 | 50.5 | 0 | 0 | 0 | 0 | 16.7 | 52.47 | 18.41 | -52.47 | 0 | 0 | 0 | Battery-supported
2025-05-30 10:00 | 150 | 5 | Autumn | 10 | 0 | -23.5 | 1.17 | 24.4 | 0 | 0 | 0 | 0 | 23.5 | 62.29 | 15 | -8.52 | 53.77 | 17.206 | 0 | Diesel-backup
2025-05-30 11:00 | 150 | 5 | Autumn | 11 | 0 | -20.8 | 22.55 | 11.6 | 0 | 0 | 120 | 120 | 20.8 | 63.28 | 35.87 | 56.72 | 0 | 0 | 0 | Normal
2025-05-30 12:00 | 150 | 5 | Autumn | 12 | 0 | -23 | 5.24 | 18.3 | 0 | 0 | 0.74 | 0.74 | 23 | 66.54 | 15 | -52.18 | 13.62 | 4.905 | 0 | Diesel-backup
2025-05-30 13:00 | 150 | 5 | Autumn | 13 | 0 | -22.4 | 7.36 | 23.8 | 0 | 0 | 8.05 | 8.05 | 22.4 | 70.64 | 15 | 0 | 62.59 | 20.029 | 0 | Diesel-backup
2025-05-30 14:00 | 150 | 5 | Autumn | 14 | 0 | -21.3 | 33.89 | 28.5 | 0 | 0 | 0 | 0 | 21.3 | 64.26 | 15 | 0 | 64.26 | 20.563 | 0 | Diesel-backup
2025-05-30 15:00 | 150 | 5 | Autumn | 15 | 0 | -18.2 | 4.56 | 58.3 | 0 | 0 | 0.17 | 0.17 | 18.2 | 63.36 | 15 | 0 | 63.19 | 20.221 | 0 | Diesel-backup
2025-05-30 16:00 | 150 | 5 | Autumn | 16 | 0 | -17.2 | 8.67 | 22.7 | 0 | 0 | 19.34 | 19.34 | 17.2 | 51.45 | 15 | 0 | 32.11 | 10.805 | 0 | Diesel-backup
2025-05-30 17:00 | 150 | 5 | Autumn | 17 | 0 | -20.2 | 19.59 | 68.6 | 0 | 0 | 120 | 120 | 20.2 | 61.61 | 36.49 | 58.39 | 0 | 0 | 0 | Normal
2025-05-30 18:00 | 150 | 5 | Autumn | 18 | 0 | -22 | 25.32 | 78.6 | 0 | 0 | 120 | 120 | 22 | 67.8 | 55.7 | 52.2 | 0 | 0 | 0 | Normal
2025-05-30 19:00 | 150 | 5 | Autumn | 19 | 0 | -15.7 | 12.41 | 73.9 | 0 | 0 | 99 | 99 | 15.7 | 66.25 | 67.75 | 32.75 | 0 | 0 | 0 | Normal
2025-05-30 20:00 | 150 | 5 | Autumn | 20 | 0 | -22.1 | 18.6 | 46.2 | 0 | 0 | 120 | 120 | 22.1 | 59.74 | 89.92 | 60.26 | 0 | 0 | 0 | Normal
2025-05-30 21:00 | 150 | 5 | Autumn | 21 | 0 | -22.5 | 8.14 | 27 | 0 | 0 | 13.98 | 13.98 | 22.5 | 56.81 | 72.79 | -42.83 | 0 | 0 | 0 | Battery-supported
2025-05-30 22:00 | 150 | 5 | Autumn | 22 | 0 | -25.1 | 1.16 | 24.2 | 0 | 0 | 0 | 0 | 25.1 | 53.05 | 51.57 | -53.05 | 0 | 0 | 0 | Battery-supported
2025-05-30 23:00 | 150 | 5 | Autumn | 23 | 0 | -18.1 | 17.66 | 62.2 | 0 | 0 | 120 | 120 | 18.1 | 52.28 | 76.49 | 67.72 | 0 | 0 | 0 | Normal
2025-05-31 | 151 | 5 | Autumn | 0 | 0 | -19.2 | 9.18 | 37.8 | 0 | 0 | 25.65 | 25.65 | 19.2 | 58.37 | 63.41 | -32.72 | 0 | 0 | 0 | Battery-supported
2025-05-31 01:00 | 151 | 5 | Autumn | 1 | 0 | -16 | 7.58 | 74.6 | 0 | 0 | 9.51 | 9.51 | 16 | 54.69 | 45.33 | -45.18 | 0 | 0 | 0 | Battery-supported
2025-05-31 02:00 | 151 | 5 | Autumn | 2 | 0 | -24.4 | 7.16 | 42.3 | 0 | 0 | 6.86 | 6.86 | 24.4 | 59.2 | 24.4 | -52.34 | 0 | 0 | 0 | Battery-supported
2025-05-31 03:00 | 151 | 5 | Autumn | 3 | 0 | -18.1 | 13.86 | 58.3 | 0 | 0 | 120 | 120 | 18.1 | 52.07 | 49.4 | 67.93 | 0 | 0 | 0 | Normal
2025-05-31 04:00 | 151 | 5 | Autumn | 4 | 0 | -21.2 | 13.77 | 25.3 | 0 | 0 | 120 | 120 | 21.2 | 66.6 | 69.05 | 53.4 | 0 | 0 | 0 | Normal
2025-05-31 05:00 | 151 | 5 | Autumn | 5 | 0 | -19.6 | 9.34 | 69.2 | 0 | 0 | 27.88 | 27.88 | 19.6 | 53.73 | 58.71 | -25.85 | 0 | 0 | 0 | Battery-supported
2025-05-31 06:00 | 151 | 5 | Autumn | 6 | 0 | -25 | 12.09 | 71.6 | 0 | 0 | 88.71 | 88.71 | 25 | 57.8 | 70.08 | 30.91 | 0 | 0 | 0 | Normal
2025-05-31 07:00 | 151 | 5 | Autumn | 7 | 0 | -18.1 | 4.51 | 28.9 | 0 | 0 | 0.14 | 0.14 | 18.1 | 50.84 | 49.8 | -50.7 | 0 | 0 | 0 | Battery-supported
2025-05-31 08:00 | 151 | 5 | Autumn | 8 | 0 | -19.6 | 8.23 | 67.1 | 0 | 0 | 14.81 | 14.81 | 19.6 | 56.72 | 33.04 | -41.91 | 0 | 0 | 0 | Battery-supported
2025-05-31 09:00 | 151 | 5 | Autumn | 9 | 0 | -21.4 | 4.66 | 43.4 | 0 | 0 | 0.22 | 0.22 | 21.4 | 66.15 | 15 | -45.1 | 20.83 | 7.312 | 0 | Diesel-backup
2025-05-31 10:00 | 151 | 5 | Autumn | 10 | 0 | -19.9 | 4.55 | 74.5 | 0 | 0 | 0.16 | 0.16 | 19.9 | 65.49 | 15 | 0 | 65.33 | 20.906 | 0 | Diesel-backup
2025-05-31 11:00 | 151 | 5 | Autumn | 11 | 0 | -23 | 11.42 | 15.4 | 0 | 0 | 69.53 | 69.53 | 23 | 68.45 | 15.4 | 1.08 | 0 | 0 | 0 | Normal
2025-05-31 12:00 | 151 | 5 | Autumn | 12 | 0 | -22.6 | 9.65 | 35.5 | 0 | 0 | 32.56 | 32.56 | 22.6 | 68.69 | 15 | -0.99 | 35.14 | 11.687 | 0 | Diesel-backup
2025-05-31 13:00 | 151 | 5 | Autumn | 13 | 0 | -22.4 | 7.04 | 36 | 0 | 0 | 6.21 | 6.21 | 22.4 | 63.01 | 15 | 0 | 56.8 | 18.176 | 0 | Diesel-backup
2025-05-31 14:00 | 151 | 5 | Autumn | 14 | 0 | -25.4 | 7.98 | 26.7 | 0 | 0 | 12.58 | 12.58 | 25.4 | 67.74 | 15 | 0 | 55.16 | 17.651 | 0 | Diesel-backup
2025-05-31 15:00 | 151 | 5 | Autumn | 15 | 0 | -19.5 | 11.99 | 31.1 | 0 | 0 | 85.65 | 85.65 | 19.5 | 67.1 | 21.83 | 18.55 | 0 | 0 | 0 | Normal
2025-05-31 16:00 | 151 | 5 | Autumn | 16 | 0 | -18.7 | 14.03 | 21.9 | 0 | 0 | 120 | 120 | 18.7 | 59.81 | 43.98 | 60.19 | 0 | 0 | 0 | Normal
2025-05-31 17:00 | 151 | 5 | Autumn | 17 | 0 | -22.9 | 12.74 | 83.4 | 0 | 0 | 110.41 | 110.41 | 22.9 | 63.65 | 61.18 | 46.76 | 0 | 0 | 0 | Normal
2025-05-31 18:00 | 151 | 5 | Autumn | 18 | 0 | -20.6 | 2.77 | 55.7 | 0 | 0 | 0 | 0 | 20.6 | 67.57 | 34.16 | -67.57 | 0 | 0 | 0 | Battery-supported
2025-05-31 19:00 | 151 | 5 | Autumn | 19 | 0 | -21.9 | 1.6 | 73 | 0 | 0 | 0 | 0 | 21.9 | 61.71 | 15 | -47.89 | 13.82 | 4.974 | 0 | Diesel-backup
2025-05-31 20:00 | 151 | 5 | Autumn | 20 | 0 | -20.6 | 5.59 | 53.9 | 0 | 0 | 1.28 | 1.28 | 20.6 | 59.02 | 15 | 0 | 57.74 | 18.477 | 0 | Diesel-backup
2025-05-31 21:00 | 151 | 5 | Autumn | 21 | 0 | -22.7 | 1.61 | 63.2 | 0 | 0 | 0 | 0 | 22.7 | 53.5 | 15 | 0 | 53.5 | 17.12 | 0 | Diesel-backup
2025-05-31 22:00 | 151 | 5 | Autumn | 22 | 0 | -23.3 | 21.12 | 81 | 0 | 0 | 120 | 120 | 23.3 | 69.1 | 33.73 | 50.9 | 0 | 0 | 0 | Normal
2025-05-31 23:00 | 151 | 5 | Autumn | 23 | 0 | -19 | 7.82 | 86.8 | 0 | 0 | 11.28 | 11.28 | 19 | 58.02 | 15.04 | -46.74 | 0 | 0 | 0 | Battery-supported
2025-06-01 | 152 | 6 | Winter | 0 | 0 | -21.6 | 3.78 | 78.7 | 0 | 0 | 0 | 0 | 21.6 | 59.08 | 15 | -0.09 | 58.99 | 18.877 | 0 | Diesel-backup
2025-06-01 01:00 | 152 | 6 | Winter | 1 | 0 | -17.1 | 7.78 | 55 | 0 | 0 | 10.97 | 10.97 | 17.1 | 48.34 | 15 | 0 | 37.37 | 12.323 | 0 | Diesel-backup
2025-06-01 02:00 | 152 | 6 | Winter | 2 | 0 | -21.4 | 2.3 | 45.1 | 0 | 0 | 0 | 0 | 21.4 | 58.39 | 15 | 0 | 58.39 | 18.685 | 0 | Diesel-backup
2025-06-01 03:00 | 152 | 6 | Winter | 3 | 0 | -23.5 | 3.84 | 40.1 | 0 | 0 | 0.01 | 0.01 | 23.5 | 65.27 | 15 | 0 | 65.26 | 20.883 | 0 | Diesel-backup
2025-06-01 04:00 | 152 | 6 | Winter | 4 | 0 | -18.8 | 7.42 | 62.3 | 0 | 0 | 8.43 | 8.43 | 18.8 | 55.24 | 15 | 0 | 46.81 | 14.979 | 0 | Diesel-backup
2025-06-01 05:00 | 152 | 6 | Winter | 5 | 0 | -20.1 | 6.66 | 26.2 | 0 | 0 | 4.42 | 4.42 | 20.1 | 50.67 | 15 | 0 | 46.25 | 14.8 | 0 | Diesel-backup
2025-06-01 06:00 | 152 | 6 | Winter | 6 | 0 | -19.9 | 7.38 | 11.1 | 0 | 0 | 8.18 | 8.18 | 19.9 | 57.04 | 15 | 0 | 48.86 | 15.635 | 0 | Diesel-backup
2025-06-01 07:00 | 152 | 6 | Winter | 7 | 0 | -18.9 | 12.24 | 4.3 | 0 | 0 | 93.44 | 93.44 | 18.9 | 53.26 | 29.79 | 40.18 | 0 | 0 | 0 | Normal
2025-06-01 08:00 | 152 | 6 | Winter | 8 | 0 | -22.9 | 16.08 | 35.1 | 0 | 0 | 120 | 120 | 22.9 | 66.45 | 49.49 | 53.55 | 0 | 0 | 0 | Normal
2025-06-01 09:00 | 152 | 6 | Winter | 9 | 0 | -21.8 | 10.04 | 70.2 | 0 | 0 | 39.15 | 39.15 | 21.8 | 60.94 | 40.78 | -21.79 | 0 | 0 | 0 | Battery-supported
2025-06-01 10:00 | 152 | 6 | Winter | 10 | 0 | -21.9 | 16.57 | 37.2 | 0 | 0 | 120 | 120 | 21.9 | 61.85 | 62.18 | 58.15 | 0 | 0 | 0 | Normal
2025-06-01 11:00 | 152 | 6 | Winter | 11 | 0 | -24.3 | 6.76 | 54.6 | 0 | 0 | 4.85 | 4.85 | 24.3 | 65.41 | 37.95 | -60.56 | 0 | 0 | 0 | Battery-supported
2025-06-01 12:00 | 152 | 6 | Winter | 12 | 0 | -22.1 | 17.86 | 52.1 | 0 | 0 | 120 | 120 | 22.1 | 61.99 | 59.3 | 58.01 | 0 | 0 | 0 | Normal
2025-06-01 13:00 | 152 | 6 | Winter | 13 | 0 | -18.6 | 10.14 | 45.6 | 0 | 0 | 40.97 | 40.97 | 18.6 | 61.36 | 51.14 | -20.39 | 0 | 0 | 0 | Battery-supported
2025-06-01 14:00 | 152 | 6 | Winter | 14 | 0 | -21 | 15.29 | 64.2 | 0 | 0 | 120 | 120 | 21 | 61.26 | 72.76 | 58.74 | 0 | 0 | 0 | Normal
2025-06-01 15:00 | 152 | 6 | Winter | 15 | 0 | -24.5 | 6.84 | 42.6 | 0 | 0 | 5.21 | 5.21 | 24.5 | 74.05 | 45.22 | -68.84 | 0 | 0 | 0 | Battery-supported
2025-06-01 16:00 | 152 | 6 | Winter | 16 | 0 | -24.9 | 9.86 | 25.6 | 0 | 0 | 36.01 | 36.01 | 24.9 | 69.87 | 31.68 | -33.86 | 0 | 0 | 0 | Battery-supported
2025-06-01 17:00 | 152 | 6 | Winter | 17 | 0 | -17.8 | 27.35 | 84 | 0 | 0 | 120 | 120 | 17.8 | 63.83 | 52.35 | 56.17 | 0 | 0 | 0 | Normal
2025-06-01 18:00 | 152 | 6 | Winter | 18 | 0 | -21.7 | 9.82 | 38.7 | 0 | 0 | 35.33 | 35.33 | 21.7 | 64.14 | 40.83 | -28.81 | 0 | 0 | 0 | Battery-supported
2025-06-01 19:00 | 152 | 6 | Winter | 19 | 0 | -22.9 | 16 | 36.4 | 0 | 0 | 120 | 120 | 22.9 | 57.88 | 63.69 | 62.12 | 0 | 0 | 0 | Normal
2025-06-01 20:00 | 152 | 6 | Winter | 20 | 0 | -22.1 | 17.14 | 78.5 | 0 | 0 | 120 | 120 | 22.1 | 68.46 | 82.65 | 51.54 | 0 | 0 | 0 | Normal
2025-06-01 21:00 | 152 | 6 | Winter | 21 | 0 | -24.8 | 13.34 | 44.8 | 0 | 0 | 120 | 120 | 24.8 | 59.36 | 95 | 33.55 | 0 | 0 | 0 | Normal
2025-06-01 22:00 | 152 | 6 | Winter | 22 | 0 | -18.4 | 14.72 | 69 | 0 | 0 | 120 | 120 | 18.4 | 55.07 | 95 | 0 | 0 | 0 | 0 | Normal
2025-06-01 23:00 | 152 | 6 | Winter | 23 | 0 | -22.4 | 6.86 | 31.1 | 0 | 0 | 5.31 | 5.31 | 22.4 | 57.11 | 74.28 | -51.8 | 0 | 0 | 0 | Battery-supported
2025-06-02 | 153 | 6 | Winter | 0 | 0 | -18.6 | 5.49 | 76.6 | 0 | 0 | 1.1 | 1.1 | 18.6 | 45 | 56.72 | -43.9 | 0 | 0 | 0 | Battery-supported
2025-06-02 01:00 | 153 | 6 | Winter | 1 | 0 | -21.5 | 4.72 | 46.6 | 0 | 0 | 0.25 | 0.25 | 21.5 | 54.78 | 34.91 | -54.53 | 0 | 0 | 0 | Battery-supported
2025-06-02 02:00 | 153 | 6 | Winter | 2 | 0 | -18.5 | 11.93 | 40.5 | 0 | 0 | 83.85 | 83.85 | 18.5 | 50.19 | 47.29 | 33.66 | 0 | 0 | 0 | Normal
2025-06-02 03:00 | 153 | 6 | Winter | 3 | 0 | -21.1 | 9.67 | 31.6 | 0 | 0 | 32.88 | 32.88 | 21.1 | 56.93 | 37.67 | -24.05 | 0 | 0 | 0 | Battery-supported
2025-06-02 04:00 | 153 | 6 | Winter | 4 | 0 | -19.8 | 11.45 | 19.3 | 0 | 0 | 70.33 | 70.33 | 19.8 | 56.63 | 42.72 | 13.7 | 0 | 0 | 0 | Normal
2025-06-02 05:00 | 153 | 6 | Winter | 5 | 0 | -20.1 | 4.19 | 17.4 | 0 | 0 | 0.05 | 0.05 | 20.1 | 63.72 | 17.25 | -63.67 | 0 | 0 | 0 | Battery-supported
2025-06-02 06:00 | 153 | 6 | Winter | 6 | 0 | -20.3 | 6.07 | 61.5 | 0 | 0 | 2.38 | 2.38 | 20.3 | 57.17 | 15 | -5.62 | 49.17 | 15.734 | 0 | Diesel-backup
2025-06-02 07:00 | 153 | 6 | Winter | 7 | 0 | -20.9 | 15.78 | 86.2 | 0 | 0 | 120 | 120 | 20.9 | 53.66 | 39.41 | 66.34 | 0 | 0 | 0 | Normal
2025-06-02 08:00 | 153 | 6 | Winter | 8 | 0 | -22.2 | 10.59 | 78.9 | 0 | 0 | 49.88 | 49.88 | 22.2 | 63.51 | 33.96 | -13.63 | 0 | 0 | 0 | Battery-supported
2025-06-02 09:00 | 153 | 6 | Winter | 9 | 0 | -17.4 | 10.21 | 88 | 0 | 0 | 42.28 | 42.28 | 17.4 | 62.46 | 25.89 | -20.18 | 0 | 0 | 0 | Battery-supported
2025-06-02 10:00 | 153 | 6 | Winter | 10 | 0 | -23.6 | 8.23 | 45.7 | 0 | 0 | 14.81 | 14.81 | 23.6 | 69.98 | 15 | -27.22 | 27.95 | 9.553 | 0 | Diesel-backup
2025-06-02 11:00 | 153 | 6 | Winter | 11 | 0 | -21.6 | 5.71 | 14 | 0 | 0 | 1.51 | 1.51 | 21.6 | 59.62 | 15 | 0 | 58.11 | 18.595 | 0 | Diesel-backup
2025-06-02 12:00 | 153 | 6 | Winter | 12 | 0 | -21.6 | 18.24 | 36 | 0 | 0 | 120 | 120 | 21.6 | 63.61 | 35.75 | 56.39 | 0 | 0 | 0 | Normal
2025-06-02 13:00 | 153 | 6 | Winter | 13 | 0 | -20.8 | 19.97 | 18.9 | 0 | 0 | 120 | 120 | 20.8 | 63.18 | 56.66 | 56.82 | 0 | 0 | 0 | Normal
2025-06-02 14:00 | 153 | 6 | Winter | 14 | 0 | -22.6 | 9.92 | 49.7 | 0 | 0 | 37.04 | 37.04 | 22.6 | 59.14 | 47.82 | -22.1 | 0 | 0 | 0 | Battery-supported
2025-06-02 15:00 | 153 | 6 | Winter | 15 | 0 | -21 | 2.44 | 47 | 0 | 0 | 0 | 0 | 21 | 66.88 | 21.07 | -66.88 | 0 | 0 | 0 | Battery-supported
2025-06-02 16:00 | 153 | 6 | Winter | 16 | 0 | -22 | 8.76 | 29.7 | 0 | 0 | 20.37 | 20.37 | 22 | 65.9 | 15 | -15.17 | 30.36 | 10.283 | 0 | Diesel-backup
2025-06-02 17:00 | 153 | 6 | Winter | 17 | 0 | -25.1 | 20.79 | 36.1 | 0 | 0 | 120 | 120 | 25.1 | 67.31 | 34.39 | 52.69 | 0 | 0 | 0 | Normal
2025-06-02 18:00 | 153 | 6 | Winter | 18 | 0 | -21.6 | 6.18 | 60.4 | 0 | 0 | 2.69 | 2.69 | 21.6 | 65.57 | 15 | -48.47 | 14.41 | 5.174 | 0 | Diesel-backup
2025-06-02 19:00 | 153 | 6 | Winter | 19 | 0 | -24.1 | 7.15 | 41.4 | 0 | 0 | 6.81 | 6.81 | 24.1 | 69.71 | 15 | 0 | 62.9 | 20.128 | 0 | Diesel-backup
2025-06-02 20:00 | 153 | 6 | Winter | 20 | 0 | -25.5 | 15.36 | 61 | 0 | 0 | 120 | 120 | 25.5 | 76.24 | 31.1 | 43.76 | 0 | 0 | 0 | Normal
2025-06-02 21:00 | 153 | 6 | Winter | 21 | 0 | -21.3 | 7.08 | 81.4 | 0 | 0 | 6.42 | 6.42 | 21.3 | 58.92 | 15 | -40.26 | 12.24 | 4.43 | 0 | Diesel-backup
2025-06-02 22:00 | 153 | 6 | Winter | 22 | 0 | -20.6 | 9.58 | 39.9 | 0 | 0 | 31.46 | 31.46 | 20.6 | 51.02 | 15 | 0 | 19.56 | 6.896 | 0 | Diesel-backup
2025-06-02 23:00 | 153 | 6 | Winter | 23 | 0 | -20.5 | 1.94 | 19.5 | 0 | 0 | 0 | 0 | 20.5 | 66.78 | 15 | 0 | 66.78 | 21.37 | 0 | Diesel-backup
2025-06-03 | 154 | 6 | Winter | 0 | 0 | -20.5 | 20.28 | 8.4 | 0 | 0 | 120 | 120 | 20.5 | 51.01 | 40.39 | 68.99 | 0 | 0 | 0 | Normal
2025-06-03 01:00 | 154 | 6 | Winter | 1 | 0 | -26 | 14.66 | 22.5 | 0 | 0 | 120 | 120 | 26 | 62.56 | 61.53 | 57.44 | 0 | 0 | 0 | Normal
2025-06-03 02:00 | 154 | 6 | Winter | 2 | 0 | -24.8 | 17.56 | 91.7 | 0 | 0 | 120 | 120 | 24.8 | 58.97 | 83.99 | 61.03 | 0 | 0 | 0 | Normal
2025-06-03 03:00 | 154 | 6 | Winter | 3 | 0 | -17.4 | 5.18 | 63.2 | 0 | 0 | 0.66 | 0.66 | 17.4 | 51.93 | 63.48 | -51.27 | 0 | 0 | 0 | Battery-supported
2025-06-03 04:00 | 154 | 6 | Winter | 4 | 0 | -24.1 | 22.77 | 44.2 | 0 | 0 | 120 | 120 | 24.1 | 60.62 | 85.33 | 59.38 | 0 | 0 | 0 | Normal
2025-06-03 05:00 | 154 | 6 | Winter | 5 | 0 | -20.4 | 9.07 | 89.9 | 0 | 0 | 24.19 | 24.19 | 20.4 | 57.22 | 72.12 | -33.03 | 0 | 0 | 0 | Battery-supported
2025-06-03 06:00 | 154 | 6 | Winter | 6 | 0 | -23.3 | 18.43 | 27.9 | 0 | 0 | 120 | 120 | 23.3 | 63.82 | 92.79 | 56.18 | 0 | 0 | 0 | Normal
2025-06-03 07:00 | 154 | 6 | Winter | 7 | 0 | -21.6 | 11.77 | 17.1 | 0 | 0 | 79.16 | 79.16 | 21.6 | 53.97 | 95 | 6 | 0 | 0 | 0 | Normal
2025-06-03 08:00 | 154 | 6 | Winter | 8 | 0 | -23.2 | 15.04 | 58.9 | 0 | 0 | 120 | 120 | 23.2 | 67.8 | 95 | 0 | 0 | 0 | 0 | Normal
2025-06-03 09:00 | 154 | 6 | Winter | 9 | 0 | -20.6 | 12.3 | 44.7 | 0 | 0 | 95.38 | 95.38 | 20.6 | 66.03 | 95 | 0 | 0 | 0 | 0 | Normal
2025-06-03 10:00 | 154 | 6 | Winter | 10 | 0 | -21.5 | 7.06 | 52.6 | 0 | 0 | 6.31 | 6.31 | 21.5 | 73.91 | 67.96 | -67.6 | 0 | 0 | 0 | Battery-supported
2025-06-03 11:00 | 154 | 6 | Winter | 11 | 0 | -22.8 | 3.1 | 30.4 | 0 | 0 | 0 | 0 | 22.8 | 67.8 | 40.84 | -67.8 | 0 | 0 | 0 | Battery-supported
2025-06-03 12:00 | 154 | 6 | Winter | 12 | 0 | -24.1 | 19.24 | 47.9 | 0 | 0 | 120 | 120 | 24.1 | 62.5 | 62 | 57.5 | 0 | 0 | 0 | Normal
2025-06-03 13:00 | 154 | 6 | Winter | 13 | 0 | -21.2 | 1.27 | 34.6 | 0 | 0 | 0 | 0 | 21.2 | 69.7 | 34.12 | -69.7 | 0 | 0 | 0 | Battery-supported
2025-06-03 14:00 | 154 | 6 | Winter | 14 | 0 | -24.5 | 16 | 9.4 | 0 | 0 | 120 | 120 | 24.5 | 65.73 | 54.09 | 54.27 | 0 | 0 | 0 | Normal
2025-06-03 15:00 | 154 | 6 | Winter | 15 | 0 | -20.8 | 19.23 | 48.8 | 0 | 0 | 120 | 120 | 20.8 | 60.36 | 76.04 | 59.64 | 0 | 0 | 0 | Normal
2025-06-03 16:00 | 154 | 6 | Winter | 16 | 0 | -16 | 3.68 | 73.6 | 0 | 0 | 0 | 0 | 16 | 64.31 | 50.31 | -64.31 | 0 | 0 | 0 | Battery-supported
2025-06-03 17:00 | 154 | 6 | Winter | 17 | 0 | -18.8 | 7.31 | 21.2 | 0 | 0 | 7.74 | 7.74 | 18.8 | 62.33 | 28.48 | -54.59 | 0 | 0 | 0 | Battery-supported
2025-06-03 18:00 | 154 | 6 | Winter | 18 | 0 | -20.2 | 3.39 | 50.8 | 0 | 0 | 0 | 0 | 20.2 | 62.4 | 15 | -33.7 | 28.7 | 9.784 | 0 | Diesel-backup
2025-06-03 19:00 | 154 | 6 | Winter | 19 | 0 | -22 | 6.4 | 92.9 | 0 | 0 | 3.41 | 3.41 | 22 | 71.74 | 15 | 0 | 68.33 | 21.866 | 0 | Diesel-backup
2025-06-03 20:00 | 154 | 6 | Winter | 20 | 0 | -26.1 | 17.4 | 76.1 | 0 | 0 | 120 | 120 | 26.1 | 67.05 | 34.49 | 52.95 | 0 | 0 | 0 | Normal
2025-06-03 21:00 | 154 | 6 | Winter | 21 | 0 | -24.7 | 14.95 | 36.6 | 0 | 0 | 120 | 120 | 24.7 | 57.62 | 57.44 | 62.38 | 0 | 0 | 0 | Normal
2025-06-03 22:00 | 154 | 6 | Winter | 22 | 0 | -19 | 13.81 | 88.4 | 0 | 0 | 120 | 120 | 19 | 55.99 | 81 | 64.01 | 0 | 0 | 0 | Normal
2025-06-03 23:00 | 154 | 6 | Winter | 23 | 0 | -23.5 | 7.34 | 26.3 | 0 | 0 | 7.93 | 7.93 | 23.5 | 49.47 | 64.38 | -41.54 | 0 | 0 | 0 | Battery-supported
2025-06-04 | 155 | 6 | Winter | 0 | 0 | -23.5 | 1.41 | 12.8 | 0 | 0 | 0 | 0 | 23.5 | 59.14 | 40.73 | -59.14 | 0 | 0 | 0 | Battery-supported
2025-06-04 01:00 | 155 | 6 | Winter | 1 | 0 | -22.3 | 4.08 | 84.7 | 0 | 0 | 0.03 | 0.03 | 22.3 | 57.62 | 17.69 | -57.59 | 0 | 0 | 0 | Battery-supported
2025-06-04 02:00 | 155 | 6 | Winter | 2 | 0 | -24.3 | 8.27 | 68.8 | 0 | 0 | 15.19 | 15.19 | 24.3 | 55.88 | 15 | -6.72 | 33.97 | 11.349 | 0 | Diesel-backup
2025-06-04 03:00 | 155 | 6 | Winter | 3 | 0 | -24.6 | 4.72 | 39.4 | 0 | 0 | 0.25 | 0.25 | 24.6 | 59.53 | 15 | 0 | 59.28 | 18.97 | 0 | Diesel-backup
2025-06-04 04:00 | 155 | 6 | Winter | 4 | 0 | -22 | 16.14 | 32.7 | 0 | 0 | 120 | 120 | 22 | 58.04 | 37.8 | 61.96 | 0 | 0 | 0 | Normal
2025-06-04 05:00 | 155 | 6 | Winter | 5 | 0 | -23.9 | 23.22 | 37.2 | 0 | 0 | 120 | 120 | 23.9 | 58.73 | 60.35 | 61.27 | 0 | 0 | 0 | Normal
2025-06-04 06:00 | 155 | 6 | Winter | 6 | 0 | -23.6 | 11.74 | 67 | 0 | 0 | 78.31 | 78.31 | 23.6 | 61.87 | 66.4 | 16.44 | 0 | 0 | 0 | Normal
2025-06-04 07:00 | 155 | 6 | Winter | 7 | 0 | -23.6 | 3.66 | 27.4 | 0 | 0 | 0 | 0 | 23.6 | 59.68 | 42.53 | -59.68 | 0 | 0 | 0 | Battery-supported
2025-06-04 08:00 | 155 | 6 | Winter | 8 | 0 | -20.8 | 19.68 | 21.1 | 0 | 0 | 120 | 120 | 20.8 | 63.12 | 63.46 | 56.88 | 0 | 0 | 0 | Normal
2025-06-04 09:00 | 155 | 6 | Winter | 9 | 0 | -22.4 | 10.25 | 47 | 0 | 0 | 43.04 | 43.04 | 22.4 | 68.21 | 53.39 | -25.17 | 0 | 0 | 0 | Battery-supported
2025-06-04 10:00 | 155 | 6 | Winter | 10 | 0 | -22.3 | 9.43 | 71.6 | 0 | 0 | 29.19 | 29.19 | 22.3 | 66.37 | 38.52 | -37.18 | 0 | 0 | 0 | Battery-supported
2025-06-04 11:00 | 155 | 6 | Winter | 11 | 0 | -20.6 | 13.17 | 0 | 0 | 0 | 120 | 120 | 20.6 | 75.61 | 54.85 | 44.39 | 0 | 0 | 0 | Normal
2025-06-04 12:00 | 155 | 6 | Winter | 12 | 0 | -22.2 | 4.2 | 42.2 | 0 | 0 | 0.05 | 0.05 | 22.2 | 69.29 | 27.16 | -69.24 | 0 | 0 | 0 | Battery-supported
2025-06-04 13:00 | 155 | 6 | Winter | 13 | 0 | -22.5 | 7.44 | 55.1 | 0 | 0 | 8.56 | 8.56 | 22.5 | 63.38 | 15 | -30.39 | 24.43 | 8.459 | 0 | Diesel-backup
2025-06-04 14:00 | 155 | 6 | Winter | 14 | 0 | -20.9 | 9.04 | 25.3 | 0 | 0 | 23.8 | 23.8 | 20.9 | 57.02 | 15 | 0 | 33.22 | 11.131 | 0 | Diesel-backup
2025-06-04 15:00 | 155 | 6 | Winter | 15 | 0 | -20.5 | 11.14 | 48.1 | 0 | 0 | 62.42 | 62.42 | 20.5 | 60.79 | 15.6 | 1.63 | 0 | 0 | 0 | Normal
2025-06-04 16:00 | 155 | 6 | Winter | 16 | 0 | -22.3 | 11.82 | 53.2 | 0 | 0 | 80.61 | 80.61 | 22.3 | 57.13 | 24.24 | 23.48 | 0 | 0 | 0 | Normal
2025-06-04 17:00 | 155 | 6 | Winter | 17 | 0 | -21.8 | 13.16 | 80.5 | 0 | 0 | 120 | 120 | 21.8 | 67.46 | 43.58 | 52.54 | 0 | 0 | 0 | Normal
2025-06-04 18:00 | 155 | 6 | Winter | 18 | 0 | -23.6 | 6.53 | 52.6 | 0 | 0 | 3.89 | 3.89 | 23.6 | 65.44 | 18.96 | -61.55 | 0 | 0 | 0 | Battery-supported
2025-06-04 19:00 | 155 | 6 | Winter | 19 | 0 | -23.8 | 2.66 | 38.7 | 0 | 0 | 0 | 0 | 23.8 | 63.73 | 15 | -9.89 | 53.84 | 17.229 | 0 | Diesel-backup
2025-06-04 20:00 | 155 | 6 | Winter | 20 | 0 | -20.2 | 8.21 | 45.6 | 0 | 0 | 14.62 | 14.62 | 20.2 | 65.59 | 15 | 0 | 50.97 | 16.31 | 0 | Diesel-backup
2025-06-04 21:00 | 155 | 6 | Winter | 21 | 0 | -21 | 8.86 | 57.7 | 0 | 0 | 21.55 | 21.55 | 21 | 54.52 | 15 | 0 | 32.97 | 11.058 | 0 | Diesel-backup
2025-06-04 22:00 | 155 | 6 | Winter | 22 | 0 | -20.9 | 2.56 | 82.6 | 0 | 0 | 0 | 0 | 20.9 | 57.48 | 15 | 0 | 57.48 | 18.394 | 0 | Diesel-backup
2025-06-04 23:00 | 155 | 6 | Winter | 23 | 0 | -21.3 | 6.3 | 32.5 | 0 | 0 | 3.07 | 3.07 | 21.3 | 55.24 | 15 | 0 | 52.17 | 16.694 | 0 | Diesel-backup
2025-06-05 | 156 | 6 | Winter | 0 | 0 | -22 | 10.57 | 44.3 | 0 | 0 | 49.46 | 49.46 | 22 | 57.31 | 15 | 0 | 7.85 | 2.885 | 0 | Diesel-backup
2025-06-05 01:00 | 156 | 6 | Winter | 1 | 0 | -20.5 | 6.96 | 61.1 | 0 | 0 | 5.8 | 5.8 | 20.5 | 60.66 | 15 | 0 | 54.86 | 17.555 | 0 | Diesel-backup
2025-06-05 02:00 | 156 | 6 | Winter | 2 | 0 | -20 | 10.31 | 5.9 | 0 | 0 | 44.2 | 44.2 | 20 | 58.66 | 15 | 0 | 14.46 | 5.192 | 0 | Diesel-backup
2025-06-05 03:00 | 156 | 6 | Winter | 3 | 0 | -20.1 | 6.77 | 53.7 | 0 | 0 | 4.89 | 4.89 | 20.1 | 60.83 | 15 | 0 | 55.94 | 17.901 | 0 | Diesel-backup
2025-06-05 04:00 | 156 | 6 | Winter | 4 | 0 | -22.3 | 13.75 | 38.5 | 0 | 0 | 120 | 120 | 22.3 | 58.68 | 37.57 | 61.32 | 0 | 0 | 0 | Normal
2025-06-05 05:00 | 156 | 6 | Winter | 5 | 0 | -19 | 4.99 | 92.6 | 0 | 0 | 0.46 | 0.46 | 19 | 46.76 | 19.05 | -46.3 | 0 | 0 | 0 | Battery-supported
2025-06-05 06:00 | 156 | 6 | Winter | 6 | 0 | -21.6 | 9.52 | 35.4 | 0 | 0 | 30.54 | 30.54 | 21.6 | 53.86 | 15 | -10.11 | 13.21 | 4.763 | 0 | Diesel-backup
2025-06-05 07:00 | 156 | 6 | Winter | 7 | 0 | -20.7 | 9.81 | 4.9 | 0 | 0 | 35.16 | 35.16 | 20.7 | 49.24 | 15 | 0 | 14.08 | 5.063 | 0 | Diesel-backup
2025-06-05 08:00 | 156 | 6 | Winter | 8 | 0 | -21.4 | 15.81 | 13.5 | 0 | 0 | 120 | 120 | 21.4 | 68.07 | 34.11 | 51.93 | 0 | 0 | 0 | Normal
2025-06-05 09:00 | 156 | 6 | Winter | 9 | 0 | -21.5 | 7.7 | 19.5 | 0 | 0 | 10.37 | 10.37 | 21.5 | 64.56 | 15 | -47.78 | 6.41 | 2.369 | 0 | Diesel-backup
2025-06-05 10:00 | 156 | 6 | Winter | 10 | 0 | -23.7 | 23.09 | 35.4 | 0 | 0 | 120 | 120 | 23.7 | 71.74 | 32.76 | 48.26 | 0 | 0 | 0 | Normal
2025-06-05 11:00 | 156 | 6 | Winter | 11 | 0 | -20.5 | 22.59 | 42.4 | 0 | 0 | 120 | 120 | 20.5 | 67.65 | 52.02 | 52.35 | 0 | 0 | 0 | Normal
2025-06-05 12:00 | 156 | 6 | Winter | 12 | 0 | -15.8 | 5.21 | 60.2 | 0 | 0 | 0.7 | 0.7 | 15.8 | 58.3 | 28.98 | -57.6 | 0 | 0 | 0 | Battery-supported
2025-06-05 13:00 | 156 | 6 | Winter | 13 | 0 | -22.9 | 9.35 | 13.4 | 0 | 0 | 28.02 | 28.02 | 22.9 | 72.88 | 15 | -34.96 | 9.9 | 3.612 | 0 | Diesel-backup
2025-06-05 14:00 | 156 | 6 | Winter | 14 | 0 | -21.9 | 3.94 | 79.6 | 0 | 0 | 0.01 | 0.01 | 21.9 | 68.74 | 15 | 0 | 68.73 | 21.994 | 0 | Diesel-backup
2025-06-05 15:00 | 156 | 6 | Winter | 15 | 0 | -23 | 12.59 | 47.4 | 0 | 0 | 105.12 | 105.12 | 23 | 66.33 | 29.27 | 38.79 | 0 | 0 | 0 | Normal
2025-06-05 16:00 | 156 | 6 | Winter | 16 | 0 | -23.1 | 6.9 | 0 | 0 | 0 | 5.5 | 5.5 | 23.1 | 67.84 | 15 | -35.69 | 26.65 | 9.155 | 0 | Diesel-backup
2025-06-05 17:00 | 156 | 6 | Winter | 17 | 0 | -18.7 | 10.19 | 36.9 | 0 | 0 | 41.91 | 41.91 | 18.7 | 67.36 | 15 | 0 | 25.45 | 8.781 | 0 | Diesel-backup
2025-06-05 18:00 | 156 | 6 | Winter | 18 | 0 | -23.5 | 8.1 | 13.1 | 0 | 0 | 13.62 | 13.62 | 23.5 | 68.29 | 15 | 0 | 54.67 | 17.494 | 0 | Diesel-backup
2025-06-05 19:00 | 156 | 6 | Winter | 19 | 0 | -23.1 | 37.2 | 44.5 | 0 | 0 | 0 | 0 | 23.1 | 63.44 | 15 | 0 | 63.44 | 20.301 | 0 | Diesel-backup
2025-06-05 20:00 | 156 | 6 | Winter | 20 | 0 | -25.6 | 8.69 | 76.5 | 0 | 0 | 19.57 | 19.57 | 25.6 | 63.89 | 15 | 0 | 44.32 | 14.221 | 0 | Diesel-backup
2025-06-05 21:00 | 156 | 6 | Winter | 21 | 0 | -23.7 | 8.22 | 37.6 | 0 | 0 | 14.72 | 14.72 | 23.7 | 57.64 | 15 | 0 | 42.92 | 13.849 | 0 | Diesel-backup
2025-06-05 22:00 | 156 | 6 | Winter | 22 | 0 | -25.8 | 16.41 | 31.1 | 0 | 0 | 120 | 120 | 25.8 | 58.08 | 37.79 | 61.92 | 0 | 0 | 0 | Normal
2025-06-05 23:00 | 156 | 6 | Winter | 23 | 0 | -20.7 | 17.77 | 77.4 | 0 | 0 | 120 | 120 | 20.7 | 56.52 | 61.15 | 63.48 | 0 | 0 | 0 | Normal
2025-06-06 | 157 | 6 | Winter | 0 | 0 | -16 | 11.11 | 57.4 | 0 | 0 | 61.68 | 61.68 | 16 | 48.94 | 65.84 | 12.74 | 0 | 0 | 0 | Normal
2025-06-06 01:00 | 157 | 6 | Winter | 1 | 0 | -23 | 18.09 | 27.8 | 0 | 0 | 120 | 120 | 23 | 56.47 | 89.21 | 63.53 | 0 | 0 | 0 | Normal
2025-06-06 02:00 | 157 | 6 | Winter | 2 | 0 | -25.9 | 33.76 | 68.1 | 0 | 0 | 0 | 0 | 25.9 | 65.75 | 62.91 | -65.75 | 0 | 0 | 0 | Battery-supported
2025-06-06 03:00 | 157 | 6 | Winter | 3 | 0 | -20.2 | 7.85 | 45.8 | 0 | 0 | 11.52 | 11.52 | 20.2 | 61.82 | 42.79 | -50.3 | 0 | 0 | 0 | Battery-supported
2025-06-06 04:00 | 157 | 6 | Winter | 4 | 0 | -23.8 | 4.28 | 48.6 | 0 | 0 | 0.07 | 0.07 | 23.8 | 55.69 | 20.55 | -55.62 | 0 | 0 | 0 | Battery-supported
2025-06-06 05:00 | 157 | 6 | Winter | 5 | 0 | -19.3 | 12.04 | 86.1 | 0 | 0 | 87.17 | 87.17 | 19.3 | 52.86 | 33.17 | 34.31 | 0 | 0 | 0 | Normal
2025-06-06 06:00 | 157 | 6 | Winter | 6 | 0 | -22.8 | 17.12 | 45.7 | 0 | 0 | 120 | 120 | 22.8 | 56.88 | 56.4 | 63.12 | 0 | 0 | 0 | Normal
2025-06-06 07:00 | 157 | 6 | Winter | 7 | 0 | -23.6 | 22.07 | 75.8 | 0 | 0 | 120 | 120 | 23.6 | 59.86 | 78.53 | 60.14 | 0 | 0 | 0 | Normal
2025-06-06 08:00 | 157 | 6 | Winter | 8 | 0 | -22.6 | 13.34 | 37.3 | 0 | 0 | 120 | 120 | 22.6 | 66.98 | 95 | 44.75 | 0 | 0 | 0 | Normal
2025-06-06 09:00 | 157 | 6 | Winter | 9 | 0 | -20.5 | 9.69 | 99.6 | 0 | 0 | 33.2 | 33.2 | 20.5 | 61.47 | 83.69 | -28.27 | 0 | 0 | 0 | Battery-supported
2025-06-06 10:00 | 157 | 6 | Winter | 10 | 0 | -22.7 | 5.75 | 14.5 | 0 | 0 | 1.59 | 1.59 | 22.7 | 67.74 | 57.23 | -66.15 | 0 | 0 | 0 | Battery-supported
2025-06-06 11:00 | 157 | 6 | Winter | 11 | 0 | -23.3 | 19.41 | 42.6 | 0 | 0 | 120 | 120 | 23.3 | 64.45 | 77.67 | 55.55 | 0 | 0 | 0 | Normal
2025-06-06 12:00 | 157 | 6 | Winter | 12 | 0 | -22.6 | 11.46 | 20.1 | 0 | 0 | 70.59 | 70.59 | 22.6 | 64.11 | 80.06 | 6.48 | 0 | 0 | 0 | Normal
2025-06-06 13:00 | 157 | 6 | Winter | 13 | 0 | -25 | 2.72 | 18.9 | 0 | 0 | 0 | 0 | 25 | 64.36 | 54.32 | -64.36 | 0 | 0 | 0 | Battery-supported
2025-06-06 14:00 | 157 | 6 | Winter | 14 | 0 | -21.3 | 27.6 | 10.3 | 0 | 0 | 120 | 120 | 21.3 | 68.44 | 73.29 | 51.56 | 0 | 0 | 0 | Normal
2025-06-06 15:00 | 157 | 6 | Winter | 15 | 0 | -26.1 | 4.47 | 89 | 0 | 0 | 0.13 | 0.13 | 26.1 | 72.74 | 44.25 | -72.61 | 0 | 0 | 0 | Battery-supported
2025-06-06 16:00 | 157 | 6 | Winter | 16 | 0 | -23.2 | 17.31 | 51.8 | 0 | 0 | 120 | 120 | 23.2 | 67.59 | 63.53 | 52.41 | 0 | 0 | 0 | Normal
2025-06-06 17:00 | 157 | 6 | Winter | 17 | 0 | -20.5 | 10.9 | 58.2 | 0 | 0 | 56.72 | 56.72 | 20.5 | 66.15 | 59.76 | -9.43 | 0 | 0 | 0 | Battery-supported
2025-06-06 18:00 | 157 | 6 | Winter | 18 | 0 | -21.5 | 2.88 | 33.4 | 0 | 0 | 0 | 0 | 21.5 | 68.93 | 32.19 | -68.93 | 0 | 0 | 0 | Battery-supported
2025-06-06 19:00 | 157 | 6 | Winter | 19 | 0 | -20.9 | 9.01 | 82.2 | 0 | 0 | 23.41 | 23.41 | 20.9 | 66.91 | 15 | -42.97 | 0.53 | 0.2 | 0 | Diesel-backup
2025-06-06 20:00 | 157 | 6 | Winter | 20 | 0 | -22.3 | 7.86 | 3.9 | 0 | 0 | 11.6 | 11.6 | 22.3 | 68.21 | 15 | 0 | 56.61 | 18.115 | 0 | Diesel-backup
2025-06-06 21:00 | 157 | 6 | Winter | 21 | 0 | -19.6 | 3.41 | 56.4 | 0 | 0 | 0 | 0 | 19.6 | 52.88 | 15 | 0 | 52.88 | 16.922 | 0 | Diesel-backup
2025-06-06 22:00 | 157 | 6 | Winter | 22 | 0 | -20.2 | 12.59 | 14.5 | 0 | 0 | 105.12 | 105.12 | 20.2 | 49.19 | 35.58 | 55.93 | 0 | 0 | 0 | Normal
2025-06-06 23:00 | 157 | 6 | Winter | 23 | 0 | -21.2 | 15.93 | 51.1 | 0 | 0 | 120 | 120 | 21.2 | 53.04 | 60.22 | 66.96 | 0 | 0 | 0 | Normal
2025-06-07 | 158 | 6 | Winter | 0 | 0 | -20.3 | 9.42 | 53.3 | 0 | 0 | 29.04 | 29.04 | 20.3 | 64.08 | 46.21 | -35.04 | 0 | 0 | 0 | Battery-supported
2025-06-07 01:00 | 158 | 6 | Winter | 1 | 0 | -20.7 | 7.74 | 64.1 | 0 | 0 | 10.67 | 10.67 | 20.7 | 54.75 | 28.58 | -44.08 | 0 | 0 | 0 | Battery-supported
2025-06-07 02:00 | 158 | 6 | Winter | 2 | 0 | -23.3 | 13.19 | 38.8 | 0 | 0 | 120 | 120 | 23.3 | 64.7 | 48.93 | 55.3 | 0 | 0 | 0 | Normal
2025-06-07 03:00 | 158 | 6 | Winter | 3 | 0 | -25.3 | 1 | 51 | 0 | 0 | 0 | 0 | 25.3 | 62.47 | 23.94 | -62.47 | 0 | 0 | 0 | Battery-supported
2025-06-07 04:00 | 158 | 6 | Winter | 4 | 0 | -21.4 | 7.2 | 78.1 | 0 | 0 | 7.09 | 7.09 | 21.4 | 56.28 | 15 | -22.34 | 26.85 | 9.214 | 0 | Diesel-backup
2025-06-07 05:00 | 158 | 6 | Winter | 5 | 0 | -21.1 | 7.54 | 65.9 | 0 | 0 | 9.23 | 9.23 | 21.1 | 52.49 | 15 | 0 | 43.26 | 13.94 | 0 | Diesel-backup
2025-06-07 06:00 | 158 | 6 | Winter | 6 | 0 | -19.9 | 9.6 | 19.5 | 0 | 0 | 31.77 | 31.77 | 19.9 | 52.09 | 15 | 0 | 20.32 | 7.144 | 0 | Diesel-backup
2025-06-07 07:00 | 158 | 6 | Winter | 7 | 0 | -24.4 | 3.26 | 44.5 | 0 | 0 | 0 | 0 | 24.4 | 58.87 | 15 | 0 | 58.87 | 18.838 | 0 | Diesel-backup
2025-06-07 08:00 | 158 | 6 | Winter | 8 | 0 | -24.3 | 2.17 | 57.6 | 0 | 0 | 0 | 0 | 24.3 | 66.76 | 15 | 0 | 66.76 | 21.363 | 0 | Diesel-backup
2025-06-07 09:00 | 158 | 6 | Winter | 9 | 0 | -21.3 | 4.78 | 61.3 | 0 | 0 | 0.29 | 0.29 | 21.3 | 66.49 | 15 | 0 | 66.2 | 21.184 | 0 | Diesel-backup
2025-06-07 10:00 | 158 | 6 | Winter | 10 | 0 | -22.5 | 12.5 | 85.5 | 0 | 0 | 102.03 | 102.03 | 22.5 | 62.79 | 29.44 | 39.24 | 0 | 0 | 0 | Normal
2025-06-07 11:00 | 158 | 6 | Winter | 11 | 0 | -26.5 | 7.46 | 35.9 | 0 | 0 | 8.69 | 8.69 | 26.5 | 66.93 | 15 | -36.1 | 22.14 | 7.732 | 0 | Diesel-backup
2025-06-07 12:00 | 158 | 6 | Winter | 12 | 0 | -21.5 | 4.76 | 27 | 0 | 0 | 0.28 | 0.28 | 21.5 | 67.99 | 15 | 0 | 67.71 | 21.667 | 0 | Diesel-backup
2025-06-07 13:00 | 158 | 6 | Winter | 13 | 0 | -26.4 | 25.24 | 29.1 | 0 | 0 | 120 | 120 | 26.4 | 76.99 | 30.83 | 43.01 | 0 | 0 | 0 | Normal
2025-06-07 14:00 | 158 | 6 | Winter | 14 | 0 | -24.4 | 7.74 | 26.8 | 0 | 0 | 10.67 | 10.67 | 24.4 | 67.74 | 15 | -39.57 | 17.5 | 6.216 | 0 | Diesel-backup
2025-06-07 15:00 | 158 | 6 | Winter | 15 | 0 | -19.4 | 9.64 | 62.9 | 0 | 0 | 32.4 | 32.4 | 19.4 | 64.17 | 15 | 0 | 31.77 | 10.704 | 0 | Diesel-backup
2025-06-07 16:00 | 158 | 6 | Winter | 16 | 0 | -18.3 | 19.28 | 59.1 | 0 | 0 | 120 | 120 | 18.3 | 60.71 | 36.82 | 59.29 | 0 | 0 | 0 | Normal
2025-06-07 17:00 | 158 | 6 | Winter | 17 | 0 | -25 | 10.5 | 23.3 | 0 | 0 | 48.01 | 48.01 | 25 | 67.74 | 28.93 | -19.73 | 0 | 0 | 0 | Battery-supported
2025-06-07 18:00 | 158 | 6 | Winter | 18 | 0 | -23.1 | 13.11 | 50.2 | 0 | 0 | 120 | 120 | 23.1 | 65.25 | 49.07 | 54.75 | 0 | 0 | 0 | Normal
2025-06-07 19:00 | 158 | 6 | Winter | 19 | 0 | -22.2 | 5.57 | 1.9 | 0 | 0 | 1.24 | 1.24 | 22.2 | 63.8 | 24.05 | -62.56 | 0 | 0 | 0 | Battery-supported
2025-06-07 20:00 | 158 | 6 | Winter | 20 | 0 | -18.4 | 9.96 | 11 | 0 | 0 | 37.73 | 37.73 | 18.4 | 63.62 | 15 | -22.63 | 3.26 | 1.219 | 0 | Diesel-backup
2025-06-07 21:00 | 158 | 6 | Winter | 21 | 0 | -23.4 | 23.43 | 72.4 | 0 | 0 | 120 | 120 | 23.4 | 60.87 | 36.76 | 59.13 | 0 | 0 | 0 | Normal
2025-06-07 22:00 | 158 | 6 | Winter | 22 | 0 | -23.4 | 12.15 | 97.7 | 0 | 0 | 90.59 | 90.59 | 23.4 | 57.42 | 48.97 | 33.17 | 0 | 0 | 0 | Normal
2025-06-07 23:00 | 158 | 6 | Winter | 23 | 0 | -18.9 | 11.13 | 38.1 | 0 | 0 | 62.17 | 62.17 | 18.9 | 51.6 | 52.86 | 10.57 | 0 | 0 | 0 | Normal
2025-06-08 | 159 | 6 | Winter | 0 | 0 | -23.3 | 8.25 | 37.2 | 0 | 0 | 15 | 15 | 23.3 | 56.39 | 36.3 | -41.39 | 0 | 0 | 0 | Battery-supported
2025-06-08 01:00 | 159 | 6 | Winter | 1 | 0 | -20.9 | 3.92 | 76 | 0 | 0 | 0.01 | 0.01 | 20.9 | 58.51 | 15 | -53.25 | 5.25 | 1.947 | 0 | Diesel-backup
2025-06-08 02:00 | 159 | 6 | Winter | 2 | 0 | -25.7 | 18.14 | 36.4 | 0 | 0 | 120 | 120 | 25.7 | 57.49 | 38 | 62.51 | 0 | 0 | 0 | Normal
2025-06-08 03:00 | 159 | 6 | Winter | 3 | 0 | -22.8 | 9.2 | 21.8 | 0 | 0 | 25.92 | 25.92 | 22.8 | 53.73 | 26.88 | -27.81 | 0 | 0 | 0 | Battery-supported
2025-06-08 04:00 | 159 | 6 | Winter | 4 | 0 | -26.1 | 6.13 | 66.9 | 0 | 0 | 2.55 | 2.55 | 26.1 | 62.23 | 15 | -29.7 | 29.98 | 10.17 | 0 | Diesel-backup
2025-06-08 05:00 | 159 | 6 | Winter | 5 | 0 | -24.8 | 3.62 | 45.8 | 0 | 0 | 0 | 0 | 24.8 | 59.53 | 15 | 0 | 59.53 | 19.05 | 0 | Diesel-backup
2025-06-08 06:00 | 159 | 6 | Winter | 6 | 0 | -20.6 | 11.49 | 43.6 | 0 | 0 | 71.39 | 71.39 | 20.6 | 55.04 | 21.02 | 16.35 | 0 | 0 | 0 | Normal
2025-06-08 07:00 | 159 | 6 | Winter | 7 | 0 | -22.6 | 4.38 | 51.7 | 0 | 0 | 0.1 | 0.1 | 22.6 | 60.93 | 15 | -15.04 | 45.79 | 14.652 | 0 | Diesel-backup
2025-06-08 08:00 | 159 | 6 | Winter | 8 | 0 | -23.2 | 18.23 | 62.7 | 0 | 0 | 120 | 120 | 23.2 | 65.99 | 34.88 | 54.01 | 0 | 0 | 0 | Normal
2025-06-08 09:00 | 159 | 6 | Winter | 9 | 0 | -24.1 | 6.37 | 54.5 | 0 | 0 | 3.31 | 3.31 | 24.1 | 64.48 | 15 | -49.69 | 11.48 | 4.166 | 0 | Diesel-backup
2025-06-08 10:00 | 159 | 6 | Winter | 10 | 0 | -22.9 | 10.11 | 24.7 | 0 | 0 | 40.42 | 40.42 | 22.9 | 66.58 | 15 | 0 | 26.16 | 9.002 | 0 | Diesel-backup
2025-06-08 11:00 | 159 | 6 | Winter | 11 | 0 | -21.8 | 12.03 | 12.6 | 0 | 0 | 86.87 | 86.87 | 21.8 | 62.19 | 24.08 | 24.68 | 0 | 0 | 0 | Normal
2025-06-08 12:00 | 159 | 6 | Winter | 12 | 0 | -20.3 | 11.22 | 38.8 | 0 | 0 | 64.4 | 64.4 | 20.3 | 66.84 | 23.11 | -2.44 | 0 | 0 | 0 | Battery-supported
2025-06-08 13:00 | 159 | 6 | Winter | 13 | 0 | -28.2 | 16.02 | 45.5 | 0 | 0 | 120 | 120 | 28.2 | 71.29 | 41.03 | 48.71 | 0 | 0 | 0 | Normal
2025-06-08 14:00 | 159 | 6 | Winter | 14 | 0 | -24.3 | 6.76 | 58.1 | 0 | 0 | 4.85 | 4.85 | 24.3 | 63.19 | 17.7 | -58.34 | 0 | 0 | 0 | Battery-supported
2025-06-08 15:00 | 159 | 6 | Winter | 15 | 0 | -22.1 | 9.7 | 79.2 | 0 | 0 | 33.36 | 33.36 | 22.1 | 65.72 | 15 | -6.74 | 25.62 | 8.834 | 0 | Diesel-backup
2025-06-08 16:00 | 159 | 6 | Winter | 16 | 0 | -22.7 | 13.56 | 86 | 0 | 0 | 120 | 120 | 22.7 | 62.52 | 36.15 | 57.48 | 0 | 0 | 0 | Normal
2025-06-08 17:00 | 159 | 6 | Winter | 17 | 0 | -21.6 | 22.2 | 54.4 | 0 | 0 | 120 | 120 | 21.6 | 68.71 | 55.03 | 51.29 | 0 | 0 | 0 | Normal
2025-06-08 18:00 | 159 | 6 | Winter | 18 | 0 | -21.9 | 15.36 | 16.3 | 0 | 0 | 120 | 120 | 21.9 | 64.5 | 75.45 | 55.5 | 0 | 0 | 0 | Normal
2025-06-08 19:00 | 159 | 6 | Winter | 19 | 0 | -23.1 | 17.04 | 23.8 | 0 | 0 | 120 | 120 | 23.1 | 68.62 | 94.36 | 51.38 | 0 | 0 | 0 | Normal
2025-06-08 20:00 | 159 | 6 | Winter | 20 | 0 | -23.6 | 7.88 | 33.7 | 0 | 0 | 11.76 | 11.76 | 23.6 | 64.13 | 73.41 | -52.37 | 0 | 0 | 0 | Battery-supported
2025-06-08 21:00 | 159 | 6 | Winter | 21 | 0 | -23 | 12.17 | 52.3 | 0 | 0 | 91.22 | 91.22 | 23 | 57.23 | 85.92 | 33.99 | 0 | 0 | 0 | Normal
2025-06-08 22:00 | 159 | 6 | Winter | 22 | 0 | -19.9 | 20.39 | 52.7 | 0 | 0 | 120 | 120 | 19.9 | 56.56 | 95 | 24.68 | 0 | 0 | 0 | Normal
2025-06-08 23:00 | 159 | 6 | Winter | 23 | 0 | -24.1 | 9.41 | 11.6 | 0 | 0 | 28.89 | 28.89 | 24.1 | 58.47 | 83.17 | -29.58 | 0 | 0 | 0 | Battery-supported
2025-06-09 | 160 | 6 | Winter | 0 | 0 | -22.7 | 12.23 | 64.5 | 0 | 0 | 93.12 | 93.12 | 22.7 | 54.13 | 95 | 32.15 | 0 | 0 | 0 | Normal
2025-06-09 01:00 | 160 | 6 | Winter | 1 | 0 | -22.2 | 3.03 | 52.2 | 0 | 0 | 0 | 0 | 22.2 | 60.07 | 70.97 | -60.07 | 0 | 0 | 0 | Battery-supported
2025-06-09 02:00 | 160 | 6 | Winter | 2 | 0 | -19.2 | 14.35 | 91.7 | 0 | 0 | 120 | 120 | 19.2 | 55.33 | 94.77 | 64.67 | 0 | 0 | 0 | Normal
2025-06-09 03:00 | 160 | 6 | Winter | 3 | 0 | -23.2 | 11.1 | 41.6 | 0 | 0 | 61.44 | 61.44 | 23.2 | 53.9 | 95 | 0.62 | 0 | 0 | 0 | Normal
2025-06-09 04:00 | 160 | 6 | Winter | 4 | 0 | -20.5 | 13.81 | 18.3 | 0 | 0 | 120 | 120 | 20.5 | 54.05 | 95 | 0 | 0 | 0 | 0 | Normal
2025-06-09 05:00 | 160 | 6 | Winter | 5 | 0 | -19.9 | 8.02 | 49.8 | 0 | 0 | 12.92 | 12.92 | 19.9 | 51.62 | 79.52 | -38.7 | 0 | 0 | 0 | Battery-supported
2025-06-09 06:00 | 160 | 6 | Winter | 6 | 0 | -22.7 | 2.5 | 81.8 | 0 | 0 | 0 | 0 | 22.7 | 55.76 | 57.22 | -55.76 | 0 | 0 | 0 | Battery-supported
2025-06-09 07:00 | 160 | 6 | Winter | 7 | 0 | -23 | 14.75 | 79.2 | 0 | 0 | 120 | 120 | 23 | 56.19 | 80.7 | 63.81 | 0 | 0 | 0 | Normal
2025-06-09 08:00 | 160 | 6 | Winter | 8 | 0 | -23.3 | 6.1 | 38.9 | 0 | 0 | 2.46 | 2.46 | 23.3 | 65.35 | 55.54 | -62.89 | 0 | 0 | 0 | Battery-supported
2025-06-09 09:00 | 160 | 6 | Winter | 9 | 0 | -23.1 | 3.29 | 63.8 | 0 | 0 | 0 | 0 | 23.1 | 60.42 | 31.37 | -60.42 | 0 | 0 | 0 | Battery-supported
2025-06-09 10:00 | 160 | 6 | Winter | 10 | 0 | -20.7 | 10.65 | 66 | 0 | 0 | 51.16 | 51.16 | 20.7 | 62.04 | 27.02 | -10.88 | 0 | 0 | 0 | Battery-supported
2025-06-09 11:00 | 160 | 6 | Winter | 11 | 0 | -22.1 | 23.88 | 44.3 | 0 | 0 | 120 | 120 | 22.1 | 68.95 | 45.81 | 51.05 | 0 | 0 | 0 | Normal
2025-06-09 12:00 | 160 | 6 | Winter | 12 | 0 | -22.1 | 5.5 | 14.3 | 0 | 0 | 1.12 | 1.12 | 22.1 | 72 | 17.46 | -70.88 | 0 | 0 | 0 | Battery-supported
2025-06-09 13:00 | 160 | 6 | Winter | 13 | 0 | -25.1 | 6.27 | 64 | 0 | 0 | 2.97 | 2.97 | 25.1 | 63.54 | 15 | -6.14 | 54.43 | 17.417 | 0 | Diesel-backup
2025-06-09 14:00 | 160 | 6 | Winter | 14 | 0 | -24.7 | 15.18 | 45.9 | 0 | 0 | 120 | 120 | 24.7 | 72.01 | 32.66 | 47.99 | 0 | 0 | 0 | Normal
2025-06-09 15:00 | 160 | 6 | Winter | 15 | 0 | -17.9 | 8.49 | 44.9 | 0 | 0 | 17.39 | 17.39 | 17.9 | 69.84 | 15 | -44.15 | 8.3 | 3.046 | 0 | Diesel-backup
2025-06-09 16:00 | 160 | 6 | Winter | 16 | 0 | -23 | 14.72 | 27.8 | 0 | 0 | 120 | 120 | 23 | 65.22 | 35.16 | 54.78 | 0 | 0 | 0 | Normal
2025-06-09 17:00 | 160 | 6 | Winter | 17 | 0 | -24.3 | 8.21 | 86.2 | 0 | 0 | 14.62 | 14.62 | 24.3 | 69.34 | 15 | -50.4 | 4.32 | 1.608 | 0 | Diesel-backup
2025-06-09 18:00 | 160 | 6 | Winter | 18 | 0 | -19.4 | 7.4 | 51.9 | 0 | 0 | 8.3 | 8.3 | 19.4 | 66.46 | 15 | 0 | 58.16 | 18.611 | 0 | Diesel-backup
2025-06-09 19:00 | 160 | 6 | Winter | 19 | 0 | -22 | 5.69 | 45.8 | 0 | 0 | 1.47 | 1.47 | 22 | 63.26 | 15 | 0 | 61.79 | 19.773 | 0 | Diesel-backup
2025-06-09 20:00 | 160 | 6 | Winter | 20 | 0 | -21.3 | 11.69 | 19.1 | 0 | 0 | 76.89 | 76.89 | 21.3 | 68.1 | 18.23 | 8.79 | 0 | 0 | 0 | Normal
2025-06-09 21:00 | 160 | 6 | Winter | 21 | 0 | -22.9 | 5.66 | 93.9 | 0 | 0 | 1.41 | 1.41 | 22.9 | 57.14 | 15 | -8.09 | 47.64 | 15.246 | 0 | Diesel-backup
2025-06-09 22:00 | 160 | 6 | Winter | 22 | 0 | -23.3 | 7.12 | 49 | 0 | 0 | 6.64 | 6.64 | 23.3 | 62.13 | 15 | 0 | 55.49 | 17.757 | 0 | Diesel-backup
2025-06-09 23:00 | 160 | 6 | Winter | 23 | 0 | -23 | 18.1 | 38.1 | 0 | 0 | 120 | 120 | 23 | 64.07 | 35.58 | 55.93 | 0 | 0 | 0 | Normal
2025-06-10 | 161 | 6 | Winter | 0 | 0 | -25.8 | 29.74 | 38.9 | 0 | 0 | 0 | 0 | 25.8 | 65.83 | 15 | -51.46 | 14.37 | 5.163 | 0 | Diesel-backup
2025-06-10 01:00 | 161 | 6 | Winter | 1 | 0 | -22.9 | 12.59 | 26.3 | 0 | 0 | 105.12 | 105.12 | 22.9 | 56.65 | 32.84 | 48.47 | 0 | 0 | 0 | Normal
2025-06-10 02:00 | 161 | 6 | Winter | 2 | 0 | -22.1 | 18.53 | 45.1 | 0 | 0 | 120 | 120 | 22.1 | 59.49 | 55.1 | 60.51 | 0 | 0 | 0 | Normal
2025-06-10 03:00 | 161 | 6 | Winter | 3 | 0 | -18.6 | 7.68 | 50.3 | 0 | 0 | 10.22 | 10.22 | 18.6 | 51.73 | 38.5 | -41.51 | 0 | 0 | 0 | Battery-supported
2025-06-10 04:00 | 161 | 6 | Winter | 4 | 0 | -22.5 | 8.35 | 47.4 | 0 | 0 | 15.97 | 15.97 | 22.5 | 52.94 | 23.71 | -36.97 | 0 | 0 | 0 | Battery-supported
2025-06-10 05:00 | 161 | 6 | Winter | 5 | 0 | -27.8 | 10.97 | 60.6 | 0 | 0 | 58.34 | 58.34 | 27.8 | 61.92 | 22.28 | -3.58 | 0 | 0 | 0 | Battery-supported
2025-06-10 06:00 | 161 | 6 | Winter | 6 | 0 | -22.9 | 6.17 | 37.7 | 0 | 0 | 2.66 | 2.66 | 22.9 | 61.17 | 15 | -18.2 | 40.31 | 13.141 | 0 | Diesel-backup
2025-06-10 07:00 | 161 | 6 | Winter | 7 | 0 | -16.7 | 7.35 | 90.2 | 0 | 0 | 7.99 | 7.99 | 16.7 | 50.61 | 15 | 0 | 42.62 | 13.768 | 0 | Diesel-backup
2025-06-10 08:00 | 161 | 6 | Winter | 8 | 0 | -20.8 | 14.46 | 75.9 | 0 | 0 | 120 | 120 | 20.8 | 69.62 | 33.54 | 50.38 | 0 | 0 | 0 | Normal
2025-06-10 09:00 | 161 | 6 | Winter | 9 | 0 | -24.5 | 9.87 | 28.3 | 0 | 0 | 36.18 | 36.18 | 24.5 | 67.81 | 20.89 | -31.63 | 0 | 0 | 0 | Battery-supported
2025-06-10 10:00 | 161 | 6 | Winter | 10 | 0 | -21.4 | 8.9 | 77.3 | 0 | 0 | 22.04 | 22.04 | 21.4 | 60.12 | 15 | -14.72 | 23.36 | 8.122 | 0 | Diesel-backup
2025-06-10 11:00 | 161 | 6 | Winter | 11 | 0 | -24.3 | 8.63 | 28.5 | 0 | 0 | 18.9 | 18.9 | 24.3 | 66.2 | 15 | 0 | 47.3 | 15.136 | 0 | Diesel-backup
2025-06-10 12:00 | 161 | 6 | Winter | 12 | 0 | -25.7 | 4.83 | 35.9 | 0 | 0 | 0.33 | 0.33 | 25.7 | 66.14 | 15 | 0 | 65.81 | 21.059 | 0 | Diesel-backup
2025-06-10 13:00 | 161 | 6 | Winter | 13 | 0 | -23.5 | 10.72 | 81.6 | 0 | 0 | 52.68 | 52.68 | 23.5 | 71.77 | 15 | 0 | 19.09 | 6.742 | 0 | Diesel-backup
2025-06-10 14:00 | 161 | 6 | Winter | 14 | 0 | -22.5 | 6.18 | 59.4 | 0 | 0 | 2.69 | 2.69 | 22.5 | 67.52 | 15 | 0 | 64.83 | 20.746 | 0 | Diesel-backup
2025-06-10 15:00 | 161 | 6 | Winter | 15 | 0 | -26.8 | 3.01 | 65.1 | 0 | 0 | 0 | 0 | 26.8 | 69.55 | 15 | 0 | 69.55 | 22.256 | 0 | Diesel-backup
2025-06-10 16:00 | 161 | 6 | Winter | 16 | 0 | -25.2 | 4.37 | 14.1 | 0 | 0 | 0.09 | 0.09 | 25.2 | 71.18 | 15 | 0 | 71.09 | 22.749 | 0 | Diesel-backup
2025-06-10 17:00 | 161 | 6 | Winter | 17 | 0 | -22.7 | 8.73 | 47.9 | 0 | 0 | 20.02 | 20.02 | 22.7 | 62.61 | 15 | 0 | 42.59 | 13.76 | 0 | Diesel-backup
2025-06-10 18:00 | 161 | 6 | Winter | 18 | 0 | -23.6 | 13.78 | 56.3 | 0 | 0 | 120 | 120 | 23.6 | 62.06 | 36.32 | 57.94 | 0 | 0 | 0 | Normal
2025-06-10 19:00 | 161 | 6 | Winter | 19 | 0 | -21.8 | 15.9 | 68.1 | 0 | 0 | 120 | 120 | 21.8 | 59.78 | 58.48 | 60.22 | 0 | 0 | 0 | Normal
2025-06-10 20:00 | 161 | 6 | Winter | 20 | 0 | -25.4 | 3.66 | 62.3 | 0 | 0 | 0 | 0 | 25.4 | 61.09 | 34.05 | -61.09 | 0 | 0 | 0 | Battery-supported
2025-06-10 21:00 | 161 | 6 | Winter | 21 | 0 | -21.1 | 12.99 | 41 | 0 | 0 | 119.62 | 119.62 | 21.1 | 51.86 | 58.98 | 67.76 | 0 | 0 | 0 | Normal
2025-06-10 22:00 | 161 | 6 | Winter | 22 | 0 | -25.3 | 24.74 | 26.3 | 0 | 0 | 120 | 120 | 25.3 | 62.56 | 80.12 | 57.44 | 0 | 0 | 0 | Normal
2025-06-10 23:00 | 161 | 6 | Winter | 23 | 0 | -19.1 | 16.36 | 61.2 | 0 | 0 | 120 | 120 | 19.1 | 57.02 | 95 | 40.43 | 0 | 0 | 0 | Normal
2025-06-11 | 162 | 6 | Winter | 0 | 0 | -26.6 | 10.5 | 51.3 | 0 | 0 | 48.01 | 48.01 | 26.6 | 58.13 | 90.95 | -10.12 | 0 | 0 | 0 | Battery-supported
2025-06-11 01:00 | 162 | 6 | Winter | 1 | 0 | -25.2 | 11.02 | 57.7 | 0 | 0 | 59.52 | 59.52 | 25.2 | 52.16 | 93.66 | 7.36 | 0 | 0 | 0 | Normal
2025-06-11 02:00 | 162 | 6 | Winter | 2 | 0 | -21.9 | 10.32 | 19.2 | 0 | 0 | 44.4 | 44.4 | 21.9 | 55.28 | 89.31 | -10.88 | 0 | 0 | 0 | Battery-supported
2025-06-11 03:00 | 162 | 6 | Winter | 3 | 0 | -19.2 | 7.02 | 56.9 | 0 | 0 | 6.1 | 6.1 | 19.2 | 56.2 | 69.27 | -50.1 | 0 | 0 | 0 | Battery-supported
2025-06-11 04:00 | 162 | 6 | Winter | 4 | 0 | -22.1 | 16.85 | 62.8 | 0 | 0 | 120 | 120 | 22.1 | 60.43 | 91.19 | 59.57 | 0 | 0 | 0 | Normal
2025-06-11 05:00 | 162 | 6 | Winter | 5 | 0 | -21.6 | 5.13 | 76.3 | 0 | 0 | 0.61 | 0.61 | 21.6 | 57.57 | 68.41 | -56.96 | 0 | 0 | 0 | Battery-supported
2025-06-11 06:00 | 162 | 6 | Winter | 6 | 0 | -22.8 | 10.83 | 26.7 | 0 | 0 | 55.12 | 55.12 | 22.8 | 53.77 | 68.9 | 1.35 | 0 | 0 | 0 | Normal
2025-06-11 07:00 | 162 | 6 | Winter | 7 | 0 | -25.1 | 2.97 | 46.6 | 0 | 0 | 0 | 0 | 25.1 | 63.01 | 43.7 | -63.01 | 0 | 0 | 0 | Battery-supported
2025-06-11 08:00 | 162 | 6 | Winter | 8 | 0 | -23.9 | 17.73 | 70.8 | 0 | 0 | 120 | 120 | 23.9 | 68.48 | 62.66 | 51.52 | 0 | 0 | 0 | Normal
2025-06-11 09:00 | 162 | 6 | Winter | 9 | 0 | -25.5 | 10.57 | 45 | 0 | 0 | 49.46 | 49.46 | 25.5 | 71.46 | 53.86 | -22 | 0 | 0 | 0 | Battery-supported
2025-06-11 10:00 | 162 | 6 | Winter | 10 | 0 | -25.6 | 3.48 | 97.4 | 0 | 0 | 0 | 0 | 25.6 | 65.04 | 27.84 | -65.04 | 0 | 0 | 0 | Battery-supported
2025-06-11 11:00 | 162 | 6 | Winter | 11 | 0 | -21.9 | 21.13 | 27.2 | 0 | 0 | 120 | 120 | 21.9 | 66.95 | 47.36 | 53.05 | 0 | 0 | 0 | Normal
2025-06-11 12:00 | 162 | 6 | Winter | 12 | 0 | -25.3 | 9.16 | 39.1 | 0 | 0 | 25.38 | 25.38 | 25.3 | 71.77 | 28.81 | -46.39 | 0 | 0 | 0 | Battery-supported
2025-06-11 13:00 | 162 | 6 | Winter | 13 | 0 | -22.1 | 4.06 | 66.4 | 0 | 0 | 0.02 | 0.02 | 22.1 | 59.7 | 15 | -34.52 | 25.16 | 8.69 | 0 | Diesel-backup
2025-06-11 14:00 | 162 | 6 | Winter | 14 | 0 | -25.7 | 26.04 | 63 | 0 | 0 | 120 | 120 | 25.7 | 66.24 | 34.78 | 53.76 | 0 | 0 | 0 | Normal
2025-06-11 15:00 | 162 | 6 | Winter | 15 | 0 | -22.2 | 8.25 | 61.6 | 0 | 0 | 15 | 15 | 22.2 | 59.12 | 17.14 | -44.12 | 0 | 0 | 0 | Battery-supported
2025-06-11 16:00 | 162 | 6 | Winter | 16 | 0 | -23.9 | 5.77 | 61.5 | 0 | 0 | 1.64 | 1.64 | 23.9 | 63.65 | 15 | -5.34 | 56.67 | 18.135 | 0 | Diesel-backup
2025-06-11 17:00 | 162 | 6 | Winter | 17 | 0 | -19.7 | 11.15 | 49.2 | 0 | 0 | 62.66 | 62.66 | 19.7 | 62.29 | 15.14 | 0.37 | 0 | 0 | 0 | Normal
2025-06-11 18:00 | 162 | 6 | Winter | 18 | 0 | -22.1 | 4.4 | 33.6 | 0 | 0 | 0.1 | 0.1 | 22.1 | 59.31 | 15 | -0.34 | 58.87 | 18.838 | 0 | Diesel-backup
2025-06-11 19:00 | 162 | 6 | Winter | 19 | 0 | -20.1 | 7.02 | 69.8 | 0 | 0 | 6.1 | 6.1 | 20.1 | 67.55 | 15 | 0 | 61.45 | 19.664 | 0 | Diesel-backup
2025-06-11 20:00 | 162 | 6 | Winter | 20 | 0 | -24.5 | 19.74 | 21.7 | 0 | 0 | 120 | 120 | 24.5 | 72.01 | 32.66 | 47.99 | 0 | 0 | 0 | Normal
2025-06-11 21:00 | 162 | 6 | Winter | 21 | 0 | -22.7 | 26.97 | 80.5 | 0 | 0 | 120 | 120 | 22.7 | 57.18 | 55.78 | 62.82 | 0 | 0 | 0 | Normal
2025-06-11 22:00 | 162 | 6 | Winter | 22 | 0 | -25 | 8.38 | 10.7 | 0 | 0 | 16.27 | 16.27 | 25 | 57.37 | 39.34 | -41.1 | 0 | 0 | 0 | Battery-supported
2025-06-11 23:00 | 162 | 6 | Winter | 23 | 0 | -23.7 | 12.57 | 44 | 0 | 0 | 104.43 | 104.43 | 23.7 | 58.52 | 56.23 | 45.91 | 0 | 0 | 0 | Normal
2025-06-12 | 163 | 6 | Winter | 0 | 0 | -23.5 | 20.28 | 63 | 0 | 0 | 120 | 120 | 23.5 | 64.34 | 76.72 | 55.66 | 0 | 0 | 0 | Normal
2025-06-12 01:00 | 163 | 6 | Winter | 1 | 0 | -24.5 | 8.23 | 44.8 | 0 | 0 | 14.81 | 14.81 | 24.5 | 62 | 57.84 | -47.19 | 0 | 0 | 0 | Battery-supported
2025-06-12 02:00 | 163 | 6 | Winter | 2 | 0 | -25.6 | 5.62 | 75.2 | 0 | 0 | 1.33 | 1.33 | 25.6 | 53.4 | 37.01 | -52.07 | 0 | 0 | 0 | Battery-supported
2025-06-12 03:00 | 163 | 6 | Winter | 3 | 0 | -26.1 | 13.98 | 76.2 | 0 | 0 | 120 | 120 | 26.1 | 52.08 | 62.01 | 67.92 | 0 | 0 | 0 | Normal
2025-06-12 04:00 | 163 | 6 | Winter | 4 | 0 | -28.1 | 3.95 | 72.7 | 0 | 0 | 0.01 | 0.01 | 28.1 | 59.48 | 38.22 | -59.47 | 0 | 0 | 0 | Battery-supported
2025-06-12 05:00 | 163 | 6 | Winter | 5 | 0 | -25.3 | 5.21 | 73.4 | 0 | 0 | 0.7 | 0.7 | 25.3 | 60.13 | 15 | -58.05 | 1.38 | 0.52 | 0 | Diesel-backup
2025-06-12 06:00 | 163 | 6 | Winter | 6 | 0 | -21.6 | 3.41 | 11.7 | 0 | 0 | 0 | 0 | 21.6 | 49.79 | 15 | 0 | 49.79 | 15.933 | 0 | Diesel-backup
2025-06-12 07:00 | 163 | 6 | Winter | 7 | 0 | -26.5 | 19.45 | 25.8 | 0 | 0 | 120 | 120 | 26.5 | 60.68 | 36.83 | 59.32 | 0 | 0 | 0 | Normal
2025-06-12 08:00 | 163 | 6 | Winter | 8 | 0 | -26 | 10.11 | 55.3 | 0 | 0 | 40.42 | 40.42 | 26 | 62.29 | 28.08 | -21.87 | 0 | 0 | 0 | Battery-supported
2025-06-12 09:00 | 163 | 6 | Winter | 9 | 0 | -19 | 14.28 | 50.5 | 0 | 0 | 120 | 120 | 19 | 62.03 | 49.41 | 57.97 | 0 | 0 | 0 | Normal
2025-06-12 10:00 | 163 | 6 | Winter | 10 | 0 | -24.3 | 5.44 | 80.7 | 0 | 0 | 1.02 | 1.02 | 24.3 | 68.17 | 22.55 | -67.15 | 0 | 0 | 0 | Battery-supported
2025-06-12 11:00 | 163 | 6 | Winter | 11 | 0 | -22.2 | 12.3 | 63.6 | 0 | 0 | 95.38 | 95.38 | 22.2 | 72.02 | 31.15 | 23.36 | 0 | 0 | 0 | Normal
2025-06-12 12:00 | 163 | 6 | Winter | 12 | 0 | -21.5 | 12.55 | 56.4 | 0 | 0 | 103.74 | 103.74 | 21.5 | 63.97 | 45.79 | 39.77 | 0 | 0 | 0 | Normal
2025-06-12 13:00 | 163 | 6 | Winter | 13 | 0 | -21.5 | 26.01 | 32.1 | 0 | 0 | 120 | 120 | 21.5 | 63.08 | 66.73 | 56.92 | 0 | 0 | 0 | Normal
2025-06-12 14:00 | 163 | 6 | Winter | 14 | 0 | -26.3 | 13.58 | 16.3 | 0 | 0 | 120 | 120 | 26.3 | 74.63 | 83.43 | 45.37 | 0 | 0 | 0 | Normal
2025-06-12 15:00 | 163 | 6 | Winter | 15 | 0 | -23.5 | 15.94 | 15.2 | 0 | 0 | 120 | 120 | 23.5 | 69.11 | 95 | 31.44 | 0 | 0 | 0 | Normal
2025-06-12 16:00 | 163 | 6 | Winter | 16 | 0 | -26.5 | 10.59 | 42.5 | 0 | 0 | 49.88 | 49.88 | 26.5 | 69.67 | 87.08 | -19.79 | 0 | 0 | 0 | Battery-supported
2025-06-12 17:00 | 163 | 6 | Winter | 17 | 0 | -17.6 | 1.16 | 22.4 | 0 | 0 | 0 | 0 | 17.6 | 59.38 | 63.33 | -59.38 | 0 | 0 | 0 | Battery-supported
2025-06-12 18:00 | 163 | 6 | Winter | 18 | 0 | -26.5 | 11.66 | 25 | 0 | 0 | 76.05 | 76.05 | 26.5 | 76.3 | 63.23 | -0.25 | 0 | 0 | 0 | Battery-supported
2025-06-12 19:00 | 163 | 6 | Winter | 19 | 0 | -25.3 | 8.73 | 34.2 | 0 | 0 | 20.02 | 20.02 | 25.3 | 65.37 | 45.09 | -45.35 | 0 | 0 | 0 | Battery-supported
2025-06-12 20:00 | 163 | 6 | Winter | 20 | 0 | -25.2 | 8.46 | 42.5 | 0 | 0 | 17.08 | 17.08 | 25.2 | 62.29 | 27.01 | -45.21 | 0 | 0 | 0 | Battery-supported
2025-06-12 21:00 | 163 | 6 | Winter | 21 | 0 | -26.2 | 7.24 | 85.9 | 0 | 0 | 7.32 | 7.32 | 26.2 | 60.43 | 15 | -30.02 | 23.09 | 8.036 | 0 | Diesel-backup
2025-06-12 22:00 | 163 | 6 | Winter | 22 | 0 | -20 | 8.46 | 61.1 | 0 | 0 | 17.08 | 17.08 | 20 | 53.73 | 15 | 0 | 36.65 | 12.12 | 0 | Diesel-backup
2025-06-12 23:00 | 163 | 6 | Winter | 23 | 0 | -17.6 | 6.38 | 77.5 | 0 | 0 | 3.34 | 3.34 | 17.6 | 57.42 | 15 | 0 | 54.08 | 17.306 | 0 | Diesel-backup
2025-06-13 | 164 | 6 | Winter | 0 | 0 | -24.1 | 15.1 | 38.6 | 0 | 0 | 120 | 120 | 24.1 | 59.72 | 37.18 | 60.28 | 0 | 0 | 0 | Normal
2025-06-13 01:00 | 164 | 6 | Winter | 1 | 0 | -26 | 4.9 | 78.5 | 0 | 0 | 0.38 | 0.38 | 26 | 64.66 | 15 | -55.46 | 8.82 | 3.232 | 0 | Diesel-backup
2025-06-13 02:00 | 164 | 6 | Winter | 2 | 0 | -28 | 24.13 | 87.2 | 0 | 0 | 120 | 120 | 28 | 52.76 | 39.74 | 67.24 | 0 | 0 | 0 | Normal
2025-06-13 03:00 | 164 | 6 | Winter | 3 | 0 | -23.6 | 14.37 | 57.4 | 0 | 0 | 120 | 120 | 23.6 | 57.26 | 62.83 | 62.74 | 0 | 0 | 0 | Normal
2025-06-13 04:00 | 164 | 6 | Winter | 4 | 0 | -23.8 | 17.42 | 47.2 | 0 | 0 | 120 | 120 | 23.8 | 64.7 | 83.18 | 55.3 | 0 | 0 | 0 | Normal
2025-06-13 05:00 | 164 | 6 | Winter | 5 | 0 | -24.5 | 5.15 | 59.6 | 0 | 0 | 0.63 | 0.63 | 24.5 | 55.18 | 61.36 | -54.55 | 0 | 0 | 0 | Battery-supported
2025-06-13 06:00 | 164 | 6 | Winter | 6 | 0 | -22.6 | 6.93 | 79.6 | 0 | 0 | 5.65 | 5.65 | 22.6 | 56.48 | 41.03 | -50.83 | 0 | 0 | 0 | Battery-supported
2025-06-13 07:00 | 164 | 6 | Winter | 7 | 0 | -22.2 | 10.36 | 34.9 | 0 | 0 | 45.18 | 45.18 | 22.2 | 60.56 | 34.88 | -15.38 | 0 | 0 | 0 | Battery-supported
2025-06-13 08:00 | 164 | 6 | Winter | 8 | 0 | -22.3 | 9.77 | 39.3 | 0 | 0 | 34.5 | 34.5 | 22.3 | 63.28 | 23.37 | -28.78 | 0 | 0 | 0 | Battery-supported
2025-06-13 09:00 | 164 | 6 | Winter | 9 | 0 | -23.8 | 14.39 | 73.6 | 0 | 0 | 120 | 120 | 23.8 | 69.93 | 41.79 | 50.07 | 0 | 0 | 0 | Normal
2025-06-13 10:00 | 164 | 6 | Winter | 10 | 0 | -25.5 | 9.79 | 74 | 0 | 0 | 34.83 | 34.83 | 25.5 | 66.08 | 29.29 | -31.25 | 0 | 0 | 0 | Battery-supported
2025-06-13 11:00 | 164 | 6 | Winter | 11 | 0 | -21.6 | 24.86 | 73.9 | 0 | 0 | 120 | 120 | 21.6 | 64.45 | 49.74 | 55.55 | 0 | 0 | 0 | Normal
2025-06-13 12:00 | 164 | 6 | Winter | 12 | 0 | -23 | 5.23 | 71.9 | 0 | 0 | 0.72 | 0.72 | 23 | 68.68 | 22.55 | -67.96 | 0 | 0 | 0 | Battery-supported
2025-06-13 13:00 | 164 | 6 | Winter | 13 | 0 | -21.1 | 4.51 | 77.4 | 0 | 0 | 0.14 | 0.14 | 21.1 | 59.73 | 15 | -18.88 | 40.71 | 13.251 | 0 | Diesel-backup
2025-06-13 14:00 | 164 | 6 | Winter | 14 | 0 | -21.3 | 6.72 | 68.8 | 0 | 0 | 4.67 | 4.67 | 21.3 | 61.04 | 15 | 0 | 56.37 | 18.038 | 0 | Diesel-backup
2025-06-13 15:00 | 164 | 6 | Winter | 15 | 0 | -26.2 | 8.49 | 61.1 | 0 | 0 | 17.39 | 17.39 | 26.2 | 72.86 | 15 | 0 | 55.47 | 17.75 | 0 | Diesel-backup
2025-06-13 16:00 | 164 | 6 | Winter | 16 | 0 | -26.2 | 18.29 | 97.9 | 0 | 0 | 120 | 120 | 26.2 | 66.05 | 34.85 | 53.95 | 0 | 0 | 0 | Normal
2025-06-13 17:00 | 164 | 6 | Winter | 17 | 0 | -24.7 | 12.12 | 65.2 | 0 | 0 | 89.65 | 89.65 | 24.7 | 68.21 | 42.74 | 21.44 | 0 | 0 | 0 | Normal
2025-06-13 18:00 | 164 | 6 | Winter | 18 | 0 | -25.4 | 1.39 | 13.5 | 0 | 0 | 0 | 0 | 25.4 | 72.3 | 15 | -69.36 | 2.94 | 1.1 | 0 | Diesel-backup
2025-06-13 19:00 | 164 | 6 | Winter | 19 | 0 | -21.4 | 1.52 | 53.5 | 0 | 0 | 0 | 0 | 21.4 | 64.77 | 15 | 0 | 64.77 | 20.726 | 0 | Diesel-backup
2025-06-13 20:00 | 164 | 6 | Winter | 20 | 0 | -22.3 | 8.98 | 36.9 | 0 | 0 | 23.03 | 23.03 | 22.3 | 66.39 | 15 | 0 | 43.36 | 13.966 | 0 | Diesel-backup
2025-06-13 21:00 | 164 | 6 | Winter | 21 | 0 | -20.6 | 7.44 | 33 | 0 | 0 | 8.56 | 8.56 | 20.6 | 61.8 | 15 | 0 | 53.24 | 17.037 | 0 | Diesel-backup
2025-06-13 22:00 | 164 | 6 | Winter | 22 | 0 | -22.2 | 9.15 | 49.4 | 0 | 0 | 25.24 | 25.24 | 22.2 | 66.4 | 15 | 0 | 41.16 | 13.374 | 0 | Diesel-backup
2025-06-13 23:00 | 164 | 6 | Winter | 23 | 0 | -22.6 | 8.49 | 54.2 | 0 | 0 | 17.39 | 17.39 | 22.6 | 58.14 | 15 | 0 | 40.75 | 13.262 | 0 | Diesel-backup
2025-06-14 | 165 | 6 | Winter | 0 | 0 | -20.5 | 22.86 | 11.8 | 0 | 0 | 120 | 120 | 20.5 | 53.8 | 39.36 | 66.2 | 0 | 0 | 0 | Normal
2025-06-14 01:00 | 165 | 6 | Winter | 1 | 0 | -22.1 | 16.76 | 6.4 | 0 | 0 | 120 | 120 | 22.1 | 60.43 | 61.28 | 59.57 | 0 | 0 | 0 | Normal
2025-06-14 02:00 | 165 | 6 | Winter | 2 | 0 | -23 | 6.96 | 62.9 | 0 | 0 | 5.8 | 5.8 | 23 | 54.89 | 41.65 | -49.09 | 0 | 0 | 0 | Battery-supported
2025-06-14 03:00 | 165 | 6 | Winter | 3 | 0 | -19.9 | 9.69 | 14.4 | 0 | 0 | 33.2 | 33.2 | 19.9 | 60.15 | 30.87 | -26.95 | 0 | 0 | 0 | Battery-supported
2025-06-14 04:00 | 165 | 6 | Winter | 4 | 0 | -22.9 | 8.08 | 47.7 | 0 | 0 | 13.45 | 13.45 | 22.9 | 55.71 | 15 | -39.67 | 2.59 | 0.97 | 0 | Diesel-backup
2025-06-14 05:00 | 165 | 6 | Winter | 5 | 0 | -23.8 | 2.1 | 44.4 | 0 | 0 | 0 | 0 | 23.8 | 57.11 | 15 | 0 | 57.11 | 18.275 | 0 | Diesel-backup
2025-06-14 06:00 | 165 | 6 | Winter | 6 | 0 | -25 | 7.17 | 33.1 | 0 | 0 | 6.92 | 6.92 | 25 | 55.9 | 15 | 0 | 48.98 | 15.674 | 0 | Diesel-backup
2025-06-14 07:00 | 165 | 6 | Winter | 7 | 0 | -21.6 | 7.23 | 60.2 | 0 | 0 | 7.26 | 7.26 | 21.6 | 53.2 | 15 | 0 | 45.94 | 14.701 | 0 | Diesel-backup
2025-06-14 08:00 | 165 | 6 | Winter | 8 | 0 | -20.4 | 6.24 | 68.4 | 0 | 0 | 2.88 | 2.88 | 20.4 | 68.12 | 15 | 0 | 65.24 | 20.877 | 0 | Diesel-backup
2025-06-14 09:00 | 165 | 6 | Winter | 9 | 0 | -23.3 | 7.04 | 80.7 | 0 | 0 | 6.21 | 6.21 | 23.3 | 67.67 | 15 | 0 | 61.46 | 19.667 | 0 | Diesel-backup
2025-06-14 10:00 | 165 | 6 | Winter | 10 | 0 | -20.3 | 8.18 | 65.5 | 0 | 0 | 14.35 | 14.35 | 20.3 | 63.09 | 15 | 0 | 48.74 | 15.597 | 0 | Diesel-backup
2025-06-14 11:00 | 165 | 6 | Winter | 11 | 0 | -27.5 | 12.73 | 44.9 | 0 | 0 | 110.06 | 110.06 | 27.5 | 78.7 | 26.54 | 31.36 | 0 | 0 | 0 | Normal
2025-06-14 12:00 | 165 | 6 | Winter | 12 | 0 | -23.3 | 6.57 | 71.7 | 0 | 0 | 4.05 | 4.05 | 23.3 | 66.77 | 15 | -28.85 | 33.87 | 11.321 | 0 | Diesel-backup
2025-06-14 13:00 | 165 | 6 | Winter | 13 | 0 | -23.3 | 19.89 | 75.7 | 0 | 0 | 120 | 120 | 23.3 | 66.23 | 34.79 | 53.77 | 0 | 0 | 0 | Normal
2025-06-14 14:00 | 165 | 6 | Winter | 14 | 0 | -24.8 | 5.19 | 47.9 | 0 | 0 | 0.68 | 0.68 | 24.8 | 63.35 | 15 | -49.47 | 13.2 | 4.762 | 0 | Diesel-backup
2025-06-14 15:00 | 165 | 6 | Winter | 15 | 0 | -17.9 | 17.98 | 51.3 | 0 | 0 | 120 | 120 | 17.9 | 57.66 | 37.94 | 62.34 | 0 | 0 | 0 | Normal
2025-06-14 16:00 | 165 | 6 | Winter | 16 | 0 | -23.3 | 11.56 | 87.3 | 0 | 0 | 73.29 | 73.29 | 23.3 | 62.56 | 41.89 | 10.73 | 0 | 0 | 0 | Normal
2025-06-14 17:00 | 165 | 6 | Winter | 17 | 0 | -24.1 | 4.25 | 21.9 | 0 | 0 | 0.06 | 0.06 | 24.1 | 64.36 | 16.17 | -64.3 | 0 | 0 | 0 | Battery-supported
2025-06-14 18:00 | 165 | 6 | Winter | 18 | 0 | -23.1 | 8.05 | 36.7 | 0 | 0 | 13.18 | 13.18 | 23.1 | 64.23 | 15 | -2.92 | 48.13 | 15.4 | 0 | Diesel-backup
2025-06-14 19:00 | 165 | 6 | Winter | 19 | 0 | -27.6 | 23.35 | 57.3 | 0 | 0 | 120 | 120 | 27.6 | 69.46 | 33.6 | 50.54 | 0 | 0 | 0 | Normal
2025-06-14 20:00 | 165 | 6 | Winter | 20 | 0 | -24.8 | 5.26 | 74.2 | 0 | 0 | 0.76 | 0.76 | 24.8 | 70.6 | 15 | -46.5 | 23.34 | 8.117 | 0 | Diesel-backup
2025-06-14 21:00 | 165 | 6 | Winter | 21 | 0 | -21 | 23.73 | 52.5 | 0 | 0 | 120 | 120 | 21 | 55.9 | 38.59 | 64.1 | 0 | 0 | 0 | Normal
2025-06-14 22:00 | 165 | 6 | Winter | 22 | 0 | -24.6 | 12.94 | 61.8 | 0 | 0 | 117.74 | 117.74 | 24.6 | 66.75 | 57.35 | 50.99 | 0 | 0 | 0 | Normal
2025-06-14 23:00 | 165 | 6 | Winter | 23 | 0 | -25 | 11.67 | 33.6 | 0 | 0 | 76.33 | 76.33 | 25 | 62.52 | 62.44 | 13.81 | 0 | 0 | 0 | Normal
2025-06-15 | 166 | 6 | Winter | 0 | 0 | -20.4 | 12.52 | 24.9 | 0 | 0 | 102.71 | 102.71 | 20.4 | 52.57 | 80.89 | 50.14 | 0 | 0 | 0 | Normal
2025-06-15 01:00 | 166 | 6 | Winter | 1 | 0 | -20.3 | 7.93 | 78.4 | 0 | 0 | 12.17 | 12.17 | 20.3 | 57.11 | 62.91 | -44.94 | 0 | 0 | 0 | Battery-supported
2025-06-15 02:00 | 166 | 6 | Winter | 2 | 0 | -22.1 | 5.43 | 11 | 0 | 0 | 1.01 | 1.01 | 22.1 | 57.7 | 40.23 | -56.69 | 0 | 0 | 0 | Battery-supported
2025-06-15 03:00 | 166 | 6 | Winter | 3 | 0 | -24.3 | 9.98 | 16.2 | 0 | 0 | 38.08 | 38.08 | 24.3 | 64.89 | 29.51 | -26.81 | 0 | 0 | 0 | Battery-supported
2025-06-15 04:00 | 166 | 6 | Winter | 4 | 0 | -23.8 | 11.95 | 82.7 | 0 | 0 | 84.45 | 84.45 | 23.8 | 62.09 | 37.74 | 22.36 | 0 | 0 | 0 | Normal
2025-06-15 05:00 | 166 | 6 | Winter | 5 | 0 | -25 | 13.31 | 40.5 | 0 | 0 | 120 | 120 | 25 | 60.27 | 59.72 | 59.73 | 0 | 0 | 0 | Normal
2025-06-15 06:00 | 166 | 6 | Winter | 6 | 0 | -25.5 | 13.01 | 64.2 | 0 | 0 | 120 | 120 | 25.5 | 67.49 | 79.04 | 52.51 | 0 | 0 | 0 | Normal
2025-06-15 07:00 | 166 | 6 | Winter | 7 | 0 | -25.6 | 14.97 | 31.9 | 0 | 0 | 120 | 120 | 25.6 | 62.83 | 95 | 43.36 | 0 | 0 | 0 | Normal
2025-06-15 08:00 | 166 | 6 | Winter | 8 | 0 | -24.6 | 28.93 | 90.4 | 0 | 0 | 0 | 0 | 24.6 | 70 | 67 | -70 | 0 | 0 | 0 | Battery-supported
2025-06-15 09:00 | 166 | 6 | Winter | 9 | 0 | -25.6 | 11.35 | 78.9 | 0 | 0 | 67.7 | 67.7 | 25.6 | 74.61 | 64.24 | -6.91 | 0 | 0 | 0 | Battery-supported
2025-06-15 10:00 | 166 | 6 | Winter | 10 | 0 | -26.7 | 19.33 | 17.6 | 0 | 0 | 120 | 120 | 26.7 | 73.13 | 81.48 | 46.87 | 0 | 0 | 0 | Normal
2025-06-15 11:00 | 166 | 6 | Winter | 11 | 0 | -22.8 | 13.59 | 69.8 | 0 | 0 | 120 | 120 | 22.8 | 66.66 | 95 | 36.73 | 0 | 0 | 0 | Normal
2025-06-15 12:00 | 166 | 6 | Winter | 12 | 0 | -22.8 | 30.67 | 23.1 | 0 | 0 | 0 | 0 | 22.8 | 65.49 | 68.8 | -65.49 | 0 | 0 | 0 | Battery-supported
2025-06-15 13:00 | 166 | 6 | Winter | 13 | 0 | -19.5 | 10.39 | 32.8 | 0 | 0 | 45.78 | 45.78 | 19.5 | 54.42 | 65.35 | -8.64 | 0 | 0 | 0 | Battery-supported
2025-06-15 14:00 | 166 | 6 | Winter | 14 | 0 | -24.7 | 9.72 | 44.9 | 0 | 0 | 33.68 | 33.68 | 24.7 | 60.32 | 54.69 | -26.64 | 0 | 0 | 0 | Battery-supported
2025-06-15 15:00 | 166 | 6 | Winter | 15 | 0 | -22.6 | 18.64 | 73 | 0 | 0 | 120 | 120 | 22.6 | 65.13 | 74.88 | 54.87 | 0 | 0 | 0 | Normal
2025-06-15 16:00 | 166 | 6 | Winter | 16 | 0 | -22.6 | 18.66 | 59.8 | 0 | 0 | 120 | 120 | 22.6 | 63.38 | 95 | 54.66 | 0 | 0 | 0 | Normal
2025-06-15 17:00 | 166 | 6 | Winter | 17 | 0 | -23.8 | 8.34 | 47.7 | 0 | 0 | 15.87 | 15.87 | 23.8 | 66.88 | 74.6 | -51.01 | 0 | 0 | 0 | Battery-supported
2025-06-15 18:00 | 166 | 6 | Winter | 18 | 0 | -21.6 | 13.31 | 49.3 | 0 | 0 | 120 | 120 | 21.6 | 68.67 | 93.49 | 51.33 | 0 | 0 | 0 | Normal
2025-06-15 19:00 | 166 | 6 | Winter | 19 | 0 | -21.6 | 15.06 | 69.8 | 0 | 0 | 120 | 120 | 21.6 | 61.51 | 95 | 4.12 | 0 | 0 | 0 | Normal
2025-06-15 20:00 | 166 | 6 | Winter | 20 | 0 | -22.6 | 14.57 | 8.5 | 0 | 0 | 120 | 120 | 22.6 | 59.29 | 95 | 0 | 0 | 0 | 0 | Normal
2025-06-15 21:00 | 166 | 6 | Winter | 21 | 0 | -23.8 | 12.53 | 50.8 | 0 | 0 | 103.06 | 103.06 | 23.8 | 53.6 | 95 | 0 | 0 | 0 | 0 | Normal
2025-06-15 22:00 | 166 | 6 | Winter | 22 | 0 | -24.1 | 2.83 | 57.8 | 0 | 0 | 0 | 0 | 24.1 | 55.16 | 72.94 | -55.16 | 0 | 0 | 0 | Battery-supported
2025-06-15 23:00 | 166 | 6 | Winter | 23 | 0 | -26.3 | 14.69 | 21.4 | 0 | 0 | 120 | 120 | 26.3 | 56.74 | 95 | 59.96 | 0 | 0 | 0 | Normal
2025-06-16 | 167 | 6 | Winter | 0 | 0 | -25.2 | 15.11 | 42 | 0 | 0 | 120 | 120 | 25.2 | 60.37 | 95 | 0 | 0 | 0 | 0 | Normal
2025-06-16 01:00 | 167 | 6 | Winter | 1 | 0 | -24.8 | 12.85 | 48.3 | 0 | 0 | 114.41 | 114.41 | 24.8 | 65.96 | 95 | 0 | 0 | 0 | 0 | Normal
2025-06-16 02:00 | 167 | 6 | Winter | 2 | 0 | -25.9 | 7.79 | 76.8 | 0 | 0 | 11.05 | 11.05 | 25.9 | 63.36 | 74.08 | -52.31 | 0 | 0 | 0 | Battery-supported
2025-06-16 03:00 | 167 | 6 | Winter | 3 | 0 | -22.4 | 22.11 | 32.9 | 0 | 0 | 120 | 120 | 22.4 | 60.16 | 95 | 56.86 | 0 | 0 | 0 | Normal
2025-06-16 04:00 | 167 | 6 | Winter | 4 | 0 | -20.8 | 5.36 | 27.9 | 0 | 0 | 0.9 | 0.9 | 20.8 | 56.68 | 72.69 | -55.78 | 0 | 0 | 0 | Battery-supported
2025-06-16 05:00 | 167 | 6 | Winter | 5 | 0 | -25.4 | 18.88 | 82.4 | 0 | 0 | 120 | 120 | 25.4 | 55.44 | 95 | 60.63 | 0 | 0 | 0 | Normal
2025-06-16 06:00 | 167 | 6 | Winter | 6 | 0 | -22.8 | 5.32 | 39.3 | 0 | 0 | 0.84 | 0.84 | 22.8 | 66.76 | 68.63 | -65.92 | 0 | 0 | 0 | Battery-supported
2025-06-16 07:00 | 167 | 6 | Winter | 7 | 0 | -25.7 | 17.57 | 46.6 | 0 | 0 | 120 | 120 | 25.7 | 59.43 | 90.92 | 60.57 | 0 | 0 | 0 | Normal
2025-06-16 08:00 | 167 | 6 | Winter | 8 | 0 | -24.1 | 5.48 | 74.7 | 0 | 0 | 1.09 | 1.09 | 24.1 | 70.2 | 63.28 | -69.11 | 0 | 0 | 0 | Battery-supported
2025-06-16 09:00 | 167 | 6 | Winter | 9 | 0 | -24.9 | 16.99 | 13.5 | 0 | 0 | 120 | 120 | 24.9 | 58.95 | 85.74 | 61.05 | 0 | 0 | 0 | Normal
2025-06-16 10:00 | 167 | 6 | Winter | 10 | 0 | -22.1 | 24.9 | 78.2 | 0 | 0 | 120 | 120 | 22.1 | 64.74 | 95 | 25.15 | 0 | 0 | 0 | Normal
2025-06-16 11:00 | 167 | 6 | Winter | 11 | 0 | -24.9 | 24.95 | 32.7 | 0 | 0 | 120 | 120 | 24.9 | 67.21 | 95 | 0 | 0 | 0 | 0 | Normal
2025-06-16 12:00 | 167 | 6 | Winter | 12 | 0 | -21.2 | 21.9 | 83.3 | 0 | 0 | 120 | 120 | 21.2 | 63.13 | 95 | 0 | 0 | 0 | 0 | Normal
2025-06-16 13:00 | 167 | 6 | Winter | 13 | 0 | -23.9 | 10.37 | 18.9 | 0 | 0 | 45.38 | 45.38 | 23.9 | 61.29 | 88.64 | -15.91 | 0 | 0 | 0 | Battery-supported
2025-06-16 14:00 | 167 | 6 | Winter | 14 | 0 | -24.8 | 6.98 | 54.1 | 0 | 0 | 5.9 | 5.9 | 24.8 | 68.59 | 63.56 | -62.69 | 0 | 0 | 0 | Battery-supported
2025-06-16 15:00 | 167 | 6 | Winter | 15 | 0 | -26.1 | 1.25 | 67.8 | 0 | 0 | 0 | 0 | 26.1 | 73.98 | 33.97 | -73.98 | 0 | 0 | 0 | Battery-supported
2025-06-16 16:00 | 167 | 6 | Winter | 16 | 0 | -22.8 | 9.39 | 57.8 | 0 | 0 | 28.6 | 28.6 | 22.8 | 74.2 | 15.73 | -45.6 | 0 | 0 | 0 | Battery-supported
2025-06-16 17:00 | 167 | 6 | Winter | 17 | 0 | -21.4 | 18.07 | 67.9 | 0 | 0 | 120 | 120 | 21.4 | 71 | 33.76 | 49 | 0 | 0 | 0 | Normal
2025-06-16 18:00 | 167 | 6 | Winter | 18 | 0 | -22.8 | 14.59 | 39.9 | 0 | 0 | 120 | 120 | 22.8 | 70.86 | 51.84 | 49.14 | 0 | 0 | 0 | Normal
2025-06-16 19:00 | 167 | 6 | Winter | 19 | 0 | -18.5 | 32.29 | 44 | 0 | 0 | 0 | 0 | 18.5 | 68.34 | 24.51 | -68.34 | 0 | 0 | 0 | Battery-supported
2025-06-16 20:00 | 167 | 6 | Winter | 20 | 0 | -20.2 | 7.43 | 54.4 | 0 | 0 | 8.5 | 8.5 | 20.2 | 70.5 | 15 | -23.77 | 38.23 | 12.565 | 0 | Diesel-backup
2025-06-16 21:00 | 167 | 6 | Winter | 21 | 0 | -24.1 | 25.86 | 63.6 | 0 | 0 | 120 | 120 | 24.1 | 55.41 | 38.77 | 64.59 | 0 | 0 | 0 | Normal
2025-06-16 22:00 | 167 | 6 | Winter | 22 | 0 | -24.1 | 9.85 | 70.9 | 0 | 0 | 35.84 | 35.84 | 24.1 | 60.11 | 29.06 | -24.27 | 0 | 0 | 0 | Battery-supported
2025-06-16 23:00 | 167 | 6 | Winter | 23 | 0 | -22.4 | 5.3 | 81.1 | 0 | 0 | 0.82 | 0.82 | 22.4 | 52.29 | 15 | -35.15 | 16.32 | 5.821 | 0 | Diesel-backup
2025-06-17 | 168 | 6 | Winter | 0 | 0 | -25.3 | 12.32 | 87.2 | 0 | 0 | 96.03 | 96.03 | 25.3 | 62.45 | 27.36 | 33.58 | 0 | 0 | 0 | Normal
2025-06-17 01:00 | 168 | 6 | Winter | 1 | 0 | -20.9 | 14.39 | 69.6 | 0 | 0 | 120 | 120 | 20.9 | 54.92 | 51.31 | 65.08 | 0 | 0 | 0 | Normal
2025-06-17 02:00 | 168 | 6 | Winter | 2 | 0 | -22.7 | 20.79 | 39.1 | 0 | 0 | 120 | 120 | 22.7 | 57.08 | 74.46 | 62.92 | 0 | 0 | 0 | Normal
2025-06-17 03:00 | 168 | 6 | Winter | 3 | 0 | -22.9 | 7.42 | 70.8 | 0 | 0 | 8.43 | 8.43 | 22.9 | 56.81 | 55.11 | -48.38 | 0 | 0 | 0 | Battery-supported
2025-06-17 04:00 | 168 | 6 | Winter | 4 | 0 | -22 | 12.32 | 31.7 | 0 | 0 | 96.03 | 96.03 | 22 | 47.02 | 73.15 | 49.01 | 0 | 0 | 0 | Normal
2025-06-17 05:00 | 168 | 6 | Winter | 5 | 0 | -19.7 | 10.5 | 69.3 | 0 | 0 | 48.01 | 48.01 | 19.7 | 47.06 | 73.49 | 0.95 | 0 | 0 | 0 | Normal
2025-06-17 06:00 | 168 | 6 | Winter | 6 | 0 | -23.1 | 8.35 | 21.1 | 0 | 0 | 15.97 | 15.97 | 23.1 | 61.52 | 55.27 | -45.55 | 0 | 0 | 0 | Battery-supported
2025-06-17 07:00 | 168 | 6 | Winter | 7 | 0 | -23.7 | 24.41 | 16.2 | 0 | 0 | 120 | 120 | 23.7 | 56 | 78.83 | 64 | 0 | 0 | 0 | Normal
2025-06-17 08:00 | 168 | 6 | Winter | 8 | 0 | -20.2 | 14.51 | 53 | 0 | 0 | 120 | 120 | 20.2 | 67.29 | 95 | 43.95 | 0 | 0 | 0 | Normal
2025-06-17 09:00 | 168 | 6 | Winter | 9 | 0 | -21.4 | 1.93 | 77.9 | 0 | 0 | 0 | 0 | 21.4 | 63.76 | 69.5 | -63.76 | 0 | 0 | 0 | Battery-supported
2025-06-17 10:00 | 168 | 6 | Winter | 10 | 0 | -24.2 | 12.44 | 0 | 0 | 0 | 100.01 | 100.01 | 24.2 | 60.86 | 83.9 | 39.15 | 0 | 0 | 0 | Normal
2025-06-17 11:00 | 168 | 6 | Winter | 11 | 0 | -23.5 | 3.35 | 65.5 | 0 | 0 | 0 | 0 | 23.5 | 60.9 | 59.54 | -60.9 | 0 | 0 | 0 | Battery-supported
2025-06-17 12:00 | 168 | 6 | Winter | 12 | 0 | -23.1 | 11.72 | 71.1 | 0 | 0 | 77.74 | 77.74 | 23.1 | 63.41 | 64.82 | 14.33 | 0 | 0 | 0 | Normal
2025-06-17 13:00 | 168 | 6 | Winter | 13 | 0 | -22.7 | 3.79 | 35.8 | 0 | 0 | 0 | 0 | 22.7 | 61.99 | 40.02 | -61.99 | 0 | 0 | 0 | Battery-supported
2025-06-17 14:00 | 168 | 6 | Winter | 14 | 0 | -26.5 | 14.55 | 59.2 | 0 | 0 | 120 | 120 | 26.5 | 69.15 | 58.73 | 50.85 | 0 | 0 | 0 | Normal
2025-06-17 15:00 | 168 | 6 | Winter | 15 | 0 | -26.9 | 3.31 | 21.6 | 0 | 0 | 0 | 0 | 26.9 | 70.91 | 30.37 | -70.91 | 0 | 0 | 0 | Battery-supported
2025-06-17 16:00 | 168 | 6 | Winter | 16 | 0 | -25.4 | 5.52 | 29.3 | 0 | 0 | 1.15 | 1.15 | 25.4 | 69.76 | 15 | -38.42 | 30.19 | 10.232 | 0 | Diesel-backup
2025-06-17 17:00 | 168 | 6 | Winter | 17 | 0 | -25.6 | 16.47 | 75.1 | 0 | 0 | 120 | 120 | 25.6 | 69.51 | 33.58 | 50.49 | 0 | 0 | 0 | Normal
2025-06-17 18:00 | 168 | 6 | Winter | 18 | 0 | -24.9 | 10.39 | 58.8 | 0 | 0 | 45.78 | 45.78 | 24.9 | 71.44 | 23.32 | -25.66 | 0 | 0 | 0 | Battery-supported
2025-06-17 19:00 | 168 | 6 | Winter | 19 | 0 | -22.1 | 4.05 | 57.1 | 0 | 0 | 0.02 | 0.02 | 22.1 | 69.11 | 15 | -20.79 | 48.3 | 15.456 | 0 | Diesel-backup
2025-06-17 20:00 | 168 | 6 | Winter | 20 | 0 | -23.9 | 23.55 | 18.2 | 0 | 0 | 120 | 120 | 23.9 | 63.18 | 35.91 | 56.82 | 0 | 0 | 0 | Normal
2025-06-17 21:00 | 168 | 6 | Winter | 21 | 0 | -23.1 | 8.04 | 55 | 0 | 0 | 13.1 | 13.1 | 23.1 | 50.64 | 20.89 | -37.54 | 0 | 0 | 0 | Battery-supported
2025-06-17 22:00 | 168 | 6 | Winter | 22 | 0 | -26.2 | 8.9 | 56.1 | 0 | 0 | 22.04 | 22.04 | 26.2 | 58.49 | 15 | -14.73 | 21.72 | 7.596 | 0 | Diesel-backup
2025-06-17 23:00 | 168 | 6 | Winter | 23 | 0 | -24.5 | 9.41 | 28.3 | 0 | 0 | 28.89 | 28.89 | 24.5 | 59.83 | 15 | 0 | 30.94 | 10.458 | 0 | Diesel-backup
2025-06-18 | 169 | 6 | Winter | 0 | 0 | -22.3 | 15.27 | 55.9 | 0 | 0 | 120 | 120 | 22.3 | 55.2 | 38.85 | 64.8 | 0 | 0 | 0 | Normal
2025-06-18 01:00 | 169 | 6 | Winter | 1 | 0 | -22.3 | 8.45 | 4.7 | 0 | 0 | 16.98 | 16.98 | 22.3 | 59.83 | 21.71 | -42.85 | 0 | 0 | 0 | Battery-supported
2025-06-18 02:00 | 169 | 6 | Winter | 2 | 0 | -25.2 | 9.65 | 50.2 | 0 | 0 | 32.56 | 32.56 | 25.2 | 54.87 | 15 | -16.77 | 5.54 | 2.054 | 0 | Diesel-backup
2025-06-18 03:00 | 169 | 6 | Winter | 3 | 0 | -23.2 | 19.68 | 44.5 | 0 | 0 | 120 | 120 | 23.2 | 64.52 | 35.42 | 55.48 | 0 | 0 | 0 | Normal
2025-06-18 04:00 | 169 | 6 | Winter | 4 | 0 | -18.7 | 18.3 | 72.2 | 0 | 0 | 120 | 120 | 18.7 | 56.84 | 58.66 | 63.16 | 0 | 0 | 0 | Normal
2025-06-18 05:00 | 169 | 6 | Winter | 5 | 0 | -23.6 | 9.29 | 33.7 | 0 | 0 | 27.17 | 27.17 | 23.6 | 57.06 | 46.7 | -29.89 | 0 | 0 | 0 | Battery-supported
2025-06-18 06:00 | 169 | 6 | Winter | 6 | 0 | -25.1 | 9.49 | 64.8 | 0 | 0 | 30.08 | 30.08 | 25.1 | 57.05 | 35.92 | -26.97 | 0 | 0 | 0 | Battery-supported
2025-06-18 07:00 | 169 | 6 | Winter | 7 | 0 | -24 | 1.35 | 59.8 | 0 | 0 | 0 | 0 | 24 | 58.39 | 15 | -52.29 | 6.1 | 2.256 | 0 | Diesel-backup
2025-06-18 08:00 | 169 | 6 | Winter | 8 | 0 | -23.4 | 11.61 | 65.8 | 0 | 0 | 74.66 | 74.66 | 23.4 | 70.99 | 16.35 | 3.67 | 0 | 0 | 0 | Normal
2025-06-18 09:00 | 169 | 6 | Winter | 9 | 0 | -23.9 | 16.85 | 71.3 | 0 | 0 | 120 | 120 | 23.9 | 65.3 | 36.48 | 54.7 | 0 | 0 | 0 | Normal
2025-06-18 10:00 | 169 | 6 | Winter | 10 | 0 | -23.7 | 8.17 | 49.1 | 0 | 0 | 14.25 | 14.25 | 23.7 | 64.37 | 16.43 | -50.12 | 0 | 0 | 0 | Battery-supported
2025-06-18 11:00 | 169 | 6 | Winter | 11 | 0 | -26.8 | 21.61 | 54.3 | 0 | 0 | 120 | 120 | 26.8 | 69.78 | 34.91 | 50.22 | 0 | 0 | 0 | Normal
2025-06-18 12:00 | 169 | 6 | Winter | 12 | 0 | -25.7 | 3.04 | 41.3 | 0 | 0 | 0 | 0 | 25.7 | 63.68 | 15 | -49.78 | 13.9 | 5 | 0 | Diesel-backup
2025-06-18 13:00 | 169 | 6 | Winter | 13 | 0 | -23.9 | 5.78 | 50.9 | 0 | 0 | 1.66 | 1.66 | 23.9 | 71.2 | 15 | 0 | 69.54 | 22.253 | 0 | Diesel-backup
2025-06-18 14:00 | 169 | 6 | Winter | 14 | 0 | -23.9 | 20.65 | 45.4 | 0 | 0 | 120 | 120 | 23.9 | 69.39 | 33.62 | 50.61 | 0 | 0 | 0 | Normal
2025-06-18 15:00 | 169 | 6 | Winter | 15 | 0 | -24.8 | 16.47 | 77.8 | 0 | 0 | 120 | 120 | 24.8 | 71.42 | 51.5 | 48.58 | 0 | 0 | 0 | Normal
2025-06-18 16:00 | 169 | 6 | Winter | 16 | 0 | -24 | 2.9 | 81.6 | 0 | 0 | 0 | 0 | 24 | 72.54 | 22.49 | -72.54 | 0 | 0 | 0 | Battery-supported
2025-06-18 17:00 | 169 | 6 | Winter | 17 | 0 | -23.5 | 3.35 | 38.5 | 0 | 0 | 0 | 0 | 23.5 | 63.34 | 15 | -18.71 | 44.63 | 14.301 | 0 | Diesel-backup
2025-06-18 18:00 | 169 | 6 | Winter | 18 | 0 | -21.6 | 14.7 | 52.2 | 0 | 0 | 120 | 120 | 21.6 | 64.66 | 35.37 | 55.34 | 0 | 0 | 0 | Normal
2025-06-18 19:00 | 169 | 6 | Winter | 19 | 0 | -23.8 | 12.97 | 60.9 | 0 | 0 | 118.87 | 118.87 | 23.8 | 66.42 | 54.67 | 52.45 | 0 | 0 | 0 | Normal
2025-06-18 20:00 | 169 | 6 | Winter | 20 | 0 | -22.7 | 8.82 | 79.5 | 0 | 0 | 21.07 | 21.07 | 22.7 | 72.04 | 34.28 | -50.97 | 0 | 0 | 0 | Battery-supported
2025-06-18 21:00 | 169 | 6 | Winter | 21 | 0 | -24.8 | 21.2 | 65.5 | 0 | 0 | 120 | 120 | 24.8 | 58.14 | 57.04 | 61.86 | 0 | 0 | 0 | Normal
2025-06-18 22:00 | 169 | 6 | Winter | 22 | 0 | -22.3 | 6.77 | 49 | 0 | 0 | 4.89 | 4.89 | 22.3 | 50.14 | 38.94 | -45.25 | 0 | 0 | 0 | Battery-supported
2025-06-18 23:00 | 169 | 6 | Winter | 23 | 0 | -22.8 | 2.03 | 30 | 0 | 0 | 0 | 0 | 22.8 | 55.96 | 16.56 | -55.96 | 0 | 0 | 0 | Battery-supported
2025-06-19 | 170 | 6 | Winter | 0 | 0 | -21.8 | 15.29 | 59.4 | 0 | 0 | 120 | 120 | 21.8 | 60.34 | 38.51 | 59.66 | 0 | 0 | 0 | Normal
2025-06-19 01:00 | 170 | 6 | Winter | 1 | 0 | -22.1 | 17.27 | 53.6 | 0 | 0 | 120 | 120 | 22.1 | 59.23 | 60.88 | 60.77 | 0 | 0 | 0 | Normal
2025-06-19 02:00 | 170 | 6 | Winter | 2 | 0 | -22.4 | 7.04 | 54.8 | 0 | 0 | 6.21 | 6.21 | 22.4 | 57.03 | 40.55 | -50.82 | 0 | 0 | 0 | Battery-supported
2025-06-19 03:00 | 170 | 6 | Winter | 3 | 0 | -23.9 | 4.73 | 68.4 | 0 | 0 | 0.26 | 0.26 | 23.9 | 57.38 | 17.7 | -57.12 | 0 | 0 | 0 | Battery-supported
2025-06-19 04:00 | 170 | 6 | Winter | 4 | 0 | -23.1 | 2.12 | 56.7 | 0 | 0 | 0 | 0 | 23.1 | 59.46 | 15 | -6.75 | 52.71 | 16.866 | 0 | Diesel-backup
2025-06-19 05:00 | 170 | 6 | Winter | 5 | 0 | -21.3 | 10.3 | 76.1 | 0 | 0 | 44.01 | 44.01 | 21.3 | 58.56 | 15 | 0 | 14.55 | 5.223 | 0 | Diesel-backup
2025-06-19 06:00 | 170 | 6 | Winter | 6 | 0 | -25.1 | 12.61 | 83.7 | 0 | 0 | 105.82 | 105.82 | 25.1 | 60.97 | 31.5 | 44.85 | 0 | 0 | 0 | Normal
2025-06-19 07:00 | 170 | 6 | Winter | 7 | 0 | -25.1 | 18 | 58.7 | 0 | 0 | 120 | 120 | 25.1 | 58.7 | 54.06 | 61.3 | 0 | 0 | 0 | Normal
2025-06-19 08:00 | 170 | 6 | Winter | 8 | 0 | -23.3 | 13.07 | 50 | 0 | 0 | 120 | 120 | 23.3 | 66.18 | 73.87 | 53.82 | 0 | 0 | 0 | Normal
2025-06-19 09:00 | 170 | 6 | Winter | 9 | 0 | -22.8 | 7.4 | 59.3 | 0 | 0 | 8.3 | 8.3 | 22.8 | 63.61 | 51.74 | -55.31 | 0 | 0 | 0 | Battery-supported
2025-06-19 10:00 | 170 | 6 | Winter | 10 | 0 | -25.5 | 11.63 | 14.4 | 0 | 0 | 75.21 | 75.21 | 25.5 | 72.64 | 52.69 | 2.57 | 0 | 0 | 0 | Normal
2025-06-19 11:00 | 170 | 6 | Winter | 11 | 0 | -23.8 | 18.52 | 55.5 | 0 | 0 | 120 | 120 | 23.8 | 66.27 | 72.46 | 53.73 | 0 | 0 | 0 | Normal
2025-06-19 12:00 | 170 | 6 | Winter | 12 | 0 | -23.9 | 12.52 | 33.7 | 0 | 0 | 102.71 | 102.71 | 23.9 | 63.16 | 87.02 | 39.55 | 0 | 0 | 0 | Normal
2025-06-19 13:00 | 170 | 6 | Winter | 13 | 0 | -28.6 | 17 | 69.1 | 0 | 0 | 120 | 120 | 28.6 | 80.64 | 95 | 21.69 | 0 | 0 | 0 | Normal
2025-06-19 14:00 | 170 | 6 | Winter | 14 | 0 | -24.2 | 4.89 | 78.7 | 0 | 0 | 0.38 | 0.38 | 24.2 | 64.29 | 69.44 | -63.91 | 0 | 0 | 0 | Battery-supported
2025-06-19 15:00 | 170 | 6 | Winter | 15 | 0 | -24 | 14.95 | 65.6 | 0 | 0 | 120 | 120 | 24 | 63.43 | 90.25 | 56.57 | 0 | 0 | 0 | Normal
2025-06-19 16:00 | 170 | 6 | Winter | 16 | 0 | -24 | 13.08 | 19.6 | 0 | 0 | 120 | 120 | 24 | 62.19 | 95 | 12.9 | 0 | 0 | 0 | Normal
2025-06-19 17:00 | 170 | 6 | Winter | 17 | 0 | -20.6 | 8.41 | 92.2 | 0 | 0 | 16.57 | 16.57 | 20.6 | 60.85 | 77.29 | -44.28 | 0 | 0 | 0 | Battery-supported
2025-06-19 18:00 | 170 | 6 | Winter | 18 | 0 | -26.4 | 18.71 | 44.6 | 0 | 0 | 120 | 120 | 26.4 | 72.38 | 94.81 | 47.62 | 0 | 0 | 0 | Normal
2025-06-19 19:00 | 170 | 6 | Winter | 19 | 0 | -25.5 | 28.9 | 69.5 | 0 | 0 | 0 | 0 | 25.5 | 62.18 | 69.94 | -62.18 | 0 | 0 | 0 | Battery-supported
2025-06-19 20:00 | 170 | 6 | Winter | 20 | 0 | -29.4 | 3.67 | 73.9 | 0 | 0 | 0 | 0 | 29.4 | 73.04 | 40.72 | -73.04 | 0 | 0 | 0 | Battery-supported
2025-06-19 21:00 | 170 | 6 | Winter | 21 | 0 | -24.7 | 2.82 | 82.5 | 0 | 0 | 0 | 0 | 24.7 | 57.37 | 17.78 | -57.37 | 0 | 0 | 0 | Battery-supported
2025-06-19 22:00 | 170 | 6 | Winter | 22 | 0 | -24.6 | 8.67 | 62.5 | 0 | 0 | 19.34 | 19.34 | 24.6 | 56.35 | 15 | -6.94 | 30.07 | 10.197 | 0 | Diesel-backup
2025-06-19 23:00 | 170 | 6 | Winter | 23 | 0 | -24.8 | 9.85 | 92.2 | 0 | 0 | 35.84 | 35.84 | 24.8 | 52.84 | 15 | 0 | 17 | 6.049 | 0 | Diesel-backup
2025-06-20 | 171 | 6 | Winter | 0 | 0 | -21.3 | 10.32 | 48.8 | 0 | 0 | 44.4 | 44.4 | 21.3 | 56.12 | 15 | 0 | 11.72 | 4.25 | 0 | Diesel-backup
2025-06-20 01:00 | 171 | 6 | Winter | 1 | 0 | -21.9 | 6.89 | 8.6 | 0 | 0 | 5.45 | 5.45 | 21.9 | 50.05 | 15 | 0 | 44.6 | 14.295 | 0 | Diesel-backup
2025-06-20 02:00 | 171 | 6 | Winter | 2 | 0 | -23.6 | 3.26 | 68.5 | 0 | 0 | 0 | 0 | 23.6 | 57.48 | 15 | 0 | 57.48 | 18.394 | 0 | Diesel-backup
2025-06-20 03:00 | 171 | 6 | Winter | 3 | 0 | -24.6 | 8.96 | 88.1 | 0 | 0 | 22.78 | 22.78 | 24.6 | 60.97 | 15 | 0 | 38.19 | 12.554 | 0 | Diesel-backup
2025-06-20 04:00 | 171 | 6 | Winter | 4 | 0 | -21.5 | 9.91 | 0 | 0 | 0 | 36.86 | 36.86 | 21.5 | 47.46 | 15 | 0 | 10.6 | 3.859 | 0 | Diesel-backup
2025-06-20 05:00 | 171 | 6 | Winter | 5 | 0 | -23.8 | 8.49 | 35.2 | 0 | 0 | 17.39 | 17.39 | 23.8 | 61.58 | 15 | 0 | 44.19 | 14.187 | 0 | Diesel-backup
2025-06-20 06:00 | 171 | 6 | Winter | 6 | 0 | -25.6 | 10.06 | 87.8 | 0 | 0 | 39.51 | 39.51 | 25.6 | 52.69 | 15 | 0 | 13.18 | 4.754 | 0 | Diesel-backup
2025-06-20 07:00 | 171 | 6 | Winter | 7 | 0 | -27.5 | 11.81 | 88.7 | 0 | 0 | 80.32 | 80.32 | 27.5 | 69.76 | 18.89 | 10.56 | 0 | 0 | 0 | Normal
2025-06-20 08:00 | 171 | 6 | Winter | 8 | 0 | -24.7 | 9.17 | 22.4 | 0 | 0 | 25.51 | 25.51 | 24.7 | 66.92 | 15 | -9.72 | 31.69 | 10.682 | 0 | Diesel-backup
2025-06-20 09:00 | 171 | 6 | Winter | 9 | 0 | -22.1 | 6.84 | 77 | 0 | 0 | 5.21 | 5.21 | 22.1 | 61.65 | 15 | 0 | 56.44 | 18.061 | 0 | Diesel-backup
2025-06-20 10:00 | 171 | 6 | Winter | 10 | 0 | -18.8 | 10.09 | 66.8 | 0 | 0 | 40.06 | 40.06 | 18.8 | 62.62 | 15 | 0 | 22.56 | 7.867 | 0 | Diesel-backup
2025-06-20 11:00 | 171 | 6 | Winter | 11 | 0 | -23.6 | 12.35 | 45.6 | 0 | 0 | 97.02 | 97.02 | 23.6 | 63 | 27.52 | 34.02 | 0 | 0 | 0 | Normal
2025-06-20 12:00 | 171 | 6 | Winter | 12 | 0 | -25.5 | 10.64 | 55.8 | 0 | 0 | 50.95 | 50.95 | 25.5 | 58.78 | 24.39 | -7.83 | 0 | 0 | 0 | Battery-supported
2025-06-20 13:00 | 171 | 6 | Winter | 13 | 0 | -26.4 | 30.02 | 44.3 | 0 | 0 | 0 | 0 | 26.4 | 73.95 | 15 | -23.47 | 50.48 | 16.154 | 0 | Diesel-backup
2025-06-20 14:00 | 171 | 6 | Winter | 14 | 0 | -22.6 | 12.87 | 65.9 | 0 | 0 | 115.14 | 115.14 | 22.6 | 64.21 | 33.74 | 50.93 | 0 | 0 | 0 | Normal
2025-06-20 15:00 | 171 | 6 | Winter | 15 | 0 | -27.7 | 10.35 | 39.5 | 0 | 0 | 44.99 | 44.99 | 27.7 | 71 | 23.34 | -26.01 | 0 | 0 | 0 | Battery-supported
2025-06-20 16:00 | 171 | 6 | Winter | 16 | 0 | -22.6 | 6.21 | 60.1 | 0 | 0 | 2.79 | 2.79 | 22.6 | 64.94 | 15 | -20.85 | 41.3 | 13.413 | 0 | Diesel-backup
2025-06-20 17:00 | 171 | 6 | Winter | 17 | 0 | -22 | 6.3 | 82.5 | 0 | 0 | 3.07 | 3.07 | 22 | 61.68 | 15 | 0 | 58.61 | 18.755 | 0 | Diesel-backup
2025-06-20 18:00 | 171 | 6 | Winter | 18 | 0 | -22.8 | 8.5 | 17 | 0 | 0 | 17.5 | 17.5 | 22.8 | 61.33 | 15 | 0 | 43.83 | 14.091 | 0 | Diesel-backup
2025-06-20 19:00 | 171 | 6 | Winter | 19 | 0 | -24.3 | 8.66 | 37 | 0 | 0 | 19.23 | 19.23 | 24.3 | 70.22 | 15 | 0 | 50.99 | 16.317 | 0 | Diesel-backup
2025-06-20 20:00 | 171 | 6 | Winter | 20 | 0 | -22.5 | 8.46 | 27.3 | 0 | 0 | 17.08 | 17.08 | 22.5 | 67.55 | 15 | 0 | 50.47 | 16.15 | 0 | Diesel-backup
2025-06-20 21:00 | 171 | 6 | Winter | 21 | 0 | -23.4 | 13.2 | 49.3 | 0 | 0 | 120 | 120 | 23.4 | 58.23 | 37.73 | 61.77 | 0 | 0 | 0 | Normal
2025-06-20 22:00 | 171 | 6 | Winter | 22 | 0 | -25.5 | 18.39 | 26.2 | 0 | 0 | 120 | 120 | 25.5 | 64.59 | 58.12 | 55.41 | 0 | 0 | 0 | Normal
2025-06-20 23:00 | 171 | 6 | Winter | 23 | 0 | -19.7 | 15.34 | 10.6 | 0 | 0 | 120 | 120 | 19.7 | 54.4 | 82.26 | 65.6 | 0 | 0 | 0 | Normal
2025-06-21 | 172 | 6 | Winter | 0 | 0 | -24.6 | 14.35 | 16.1 | 0 | 0 | 120 | 120 | 24.6 | 64.07 | 95 | 34.61 | 0 | 0 | 0 | Normal
2025-06-21 01:00 | 172 | 6 | Winter | 1 | 0 | -22.2 | 5.77 | 66.2 | 0 | 0 | 1.64 | 1.64 | 22.2 | 63.1 | 70.42 | -61.46 | 0 | 0 | 0 | Battery-supported
2025-06-21 02:00 | 172 | 6 | Winter | 2 | 0 | -29.2 | 19.97 | 78.4 | 0 | 0 | 120 | 120 | 29.2 | 68.53 | 89.36 | 51.47 | 0 | 0 | 0 | Normal
2025-06-21 03:00 | 172 | 6 | Winter | 3 | 0 | -21.1 | 6.13 | 38.2 | 0 | 0 | 2.55 | 2.55 | 21.1 | 57.74 | 67.28 | -55.19 | 0 | 0 | 0 | Battery-supported
2025-06-21 04:00 | 172 | 6 | Winter | 4 | 0 | -20.6 | 12.19 | 70.5 | 0 | 0 | 91.85 | 91.85 | 20.6 | 51.56 | 82.11 | 40.29 | 0 | 0 | 0 | Normal
2025-06-21 05:00 | 172 | 6 | Winter | 5 | 0 | -23.8 | 13.84 | 12.5 | 0 | 0 | 120 | 120 | 23.8 | 60.57 | 95 | 35.03 | 0 | 0 | 0 | Normal
2025-06-21 06:00 | 172 | 6 | Winter | 6 | 0 | -22.6 | 20.3 | 20.3 | 0 | 0 | 120 | 120 | 22.6 | 55.7 | 95 | 0 | 0 | 0 | 0 | Normal
2025-06-21 07:00 | 172 | 6 | Winter | 7 | 0 | -22.6 | 27.03 | 73.2 | 0 | 0 | 120 | 120 | 22.6 | 60.48 | 95 | 0 | 0 | 0 | 0 | Normal
2025-06-21 08:00 | 172 | 6 | Winter | 8 | 0 | -25.3 | 8.29 | 23.7 | 0 | 0 | 15.38 | 15.38 | 25.3 | 74.76 | 71.25 | -59.38 | 0 | 0 | 0 | Battery-supported
2025-06-21 09:00 | 172 | 6 | Winter | 9 | 0 | -22.7 | 11.6 | 38.4 | 0 | 0 | 74.38 | 74.38 | 22.7 | 65.34 | 74.57 | 9.04 | 0 | 0 | 0 | Normal
2025-06-21 10:00 | 172 | 6 | Winter | 10 | 0 | -25.6 | 19.27 | 39.6 | 0 | 0 | 120 | 120 | 25.6 | 64.12 | 95 | 55.5 | 0 | 0 | 0 | Normal
2025-06-21 11:00 | 172 | 6 | Winter | 11 | 0 | -25.2 | 28.33 | 50.4 | 0 | 0 | 0 | 0 | 25.2 | 71.01 | 66.6 | -71.01 | 0 | 0 | 0 | Battery-supported
2025-06-21 12:00 | 172 | 6 | Winter | 12 | 0 | -21.4 | 8.85 | 32.1 | 0 | 0 | 21.43 | 21.43 | 21.4 | 64.37 | 49.42 | -42.94 | 0 | 0 | 0 | Battery-supported
2025-06-21 13:00 | 172 | 6 | Winter | 13 | 0 | -21.7 | 5.96 | 23.4 | 0 | 0 | 2.08 | 2.08 | 21.7 | 70.85 | 21.91 | -68.77 | 0 | 0 | 0 | Battery-supported
2025-06-21 14:00 | 172 | 6 | Winter | 14 | 0 | -25.4 | 4.06 | 49 | 0 | 0 | 0.02 | 0.02 | 25.4 | 68.62 | 15 | -17.28 | 51.32 | 16.422 | 0 | Diesel-backup
2025-06-21 15:00 | 172 | 6 | Winter | 15 | 0 | -25.5 | 2.94 | 64.9 | 0 | 0 | 0 | 0 | 25.5 | 68.22 | 15 | 0 | 68.22 | 21.83 | 0 | Diesel-backup
2025-06-21 16:00 | 172 | 6 | Winter | 16 | 0 | -25.3 | 6.63 | 83.3 | 0 | 0 | 4.29 | 4.29 | 25.3 | 68.68 | 15 | 0 | 64.39 | 20.605 | 0 | Diesel-backup
2025-06-21 17:00 | 172 | 6 | Winter | 17 | 0 | -22.3 | 17.15 | 31.5 | 0 | 0 | 120 | 120 | 22.3 | 66.53 | 34.68 | 53.47 | 0 | 0 | 0 | Normal
2025-06-21 18:00 | 172 | 6 | Winter | 18 | 0 | -26.1 | 17.72 | 44.1 | 0 | 0 | 120 | 120 | 26.1 | 61.17 | 56.33 | 58.83 | 0 | 0 | 0 | Normal
2025-06-21 19:00 | 172 | 6 | Winter | 19 | 0 | -23.1 | 12.89 | 68.7 | 0 | 0 | 115.88 | 115.88 | 23.1 | 62.85 | 75.84 | 53.03 | 0 | 0 | 0 | Normal
2025-06-21 20:00 | 172 | 6 | Winter | 20 | 0 | -22.2 | 8.61 | 80.5 | 0 | 0 | 18.68 | 18.68 | 22.2 | 69.63 | 55.46 | -50.95 | 0 | 0 | 0 | Battery-supported
2025-06-21 21:00 | 172 | 6 | Winter | 21 | 0 | -24.1 | 13.24 | 54.4 | 0 | 0 | 120 | 120 | 24.1 | 56.49 | 78.83 | 63.51 | 0 | 0 | 0 | Normal
2025-06-21 22:00 | 172 | 6 | Winter | 22 | 0 | -21.6 | 10.75 | 65.5 | 0 | 0 | 53.34 | 53.34 | 21.6 | 56.48 | 77.58 | -3.14 | 0 | 0 | 0 | Battery-supported
2025-06-21 23:00 | 172 | 6 | Winter | 23 | 0 | -24.5 | 8.86 | 49.8 | 0 | 0 | 21.55 | 21.55 | 24.5 | 58.58 | 62.77 | -37.03 | 0 | 0 | 0 | Battery-supported
2025-06-22 | 173 | 6 | Winter | 0 | 0 | -24.4 | 12.56 | 16.7 | 0 | 0 | 104.09 | 104.09 | 24.4 | 56.65 | 80.22 | 47.44 | 0 | 0 | 0 | Normal
2025-06-22 01:00 | 173 | 6 | Winter | 1 | 0 | -26.1 | 8.39 | 45.6 | 0 | 0 | 16.37 | 16.37 | 26.1 | 60.46 | 62.59 | -44.09 | 0 | 0 | 0 | Battery-supported
2025-06-22 02:00 | 173 | 6 | Winter | 2 | 0 | -21.7 | 12.52 | 68.6 | 0 | 0 | 102.71 | 102.71 | 21.7 | 52.61 | 81.02 | 50.1 | 0 | 0 | 0 | Normal
2025-06-22 03:00 | 173 | 6 | Winter | 3 | 0 | -25.6 | 13.68 | 21.6 | 0 | 0 | 120 | 120 | 25.6 | 54.68 | 95 | 37.98 | 0 | 0 | 0 | Normal
2025-06-22 04:00 | 173 | 6 | Winter | 4 | 0 | -23.2 | 15.63 | 11.9 | 0 | 0 | 120 | 120 | 23.2 | 59.02 | 95 | 0 | 0 | 0 | 0 | Normal
2025-06-22 05:00 | 173 | 6 | Winter | 5 | 0 | -24.1 | 3.37 | 34.3 | 0 | 0 | 0 | 0 | 24.1 | 65.55 | 68.78 | -65.55 | 0 | 0 | 0 | Battery-supported
2025-06-22 06:00 | 173 | 6 | Winter | 6 | 0 | -26.3 | 20.15 | 70.1 | 0 | 0 | 120 | 120 | 26.3 | 64.29 | 89.28 | 55.71 | 0 | 0 | 0 | Normal
2025-06-22 07:00 | 173 | 6 | Winter | 7 | 0 | -25.3 | 9.93 | 54.5 | 0 | 0 | 37.21 | 37.21 | 25.3 | 63.37 | 78.82 | -26.16 | 0 | 0 | 0 | Battery-supported
2025-06-22 08:00 | 173 | 6 | Winter | 8 | 0 | -20.9 | 27.23 | 18.9 | 0 | 0 | 120 | 120 | 20.9 | 68.12 | 95 | 43.97 | 0 | 0 | 0 | Normal
2025-06-22 09:00 | 173 | 6 | Winter | 9 | 0 | -23.5 | 17.24 | 55.8 | 0 | 0 | 120 | 120 | 23.5 | 67.32 | 95 | 0 | 0 | 0 | 0 | Normal
2025-06-22 10:00 | 173 | 6 | Winter | 10 | 0 | -26.2 | 6.08 | 71.7 | 0 | 0 | 2.4 | 2.4 | 26.2 | 69.29 | 68.24 | -66.89 | 0 | 0 | 0 | Battery-supported
2025-06-22 11:00 | 173 | 6 | Winter | 11 | 0 | -23.3 | 14.5 | 17.8 | 0 | 0 | 120 | 120 | 23.3 | 62.86 | 89.27 | 57.14 | 0 | 0 | 0 | Normal
2025-06-22 12:00 | 173 | 6 | Winter | 12 | 0 | -24.3 | 19.33 | 63.4 | 0 | 0 | 120 | 120 | 24.3 | 70.45 | 95 | 15.57 | 0 | 0 | 0 | Normal
2025-06-22 13:00 | 173 | 6 | Winter | 13 | 0 | -16.3 | 9.15 | 27.5 | 0 | 0 | 25.24 | 25.24 | 16.3 | 60.41 | 80.93 | -35.17 | 0 | 0 | 0 | Battery-supported
2025-06-22 14:00 | 173 | 6 | Winter | 14 | 0 | -23.3 | 5.79 | 11.7 | 0 | 0 | 1.68 | 1.68 | 23.3 | 63.55 | 56.18 | -61.87 | 0 | 0 | 0 | Battery-supported
2025-06-22 15:00 | 173 | 6 | Winter | 15 | 0 | -24.8 | 5.16 | 73.2 | 0 | 0 | 0.64 | 0.64 | 24.8 | 66.54 | 29.82 | -65.9 | 0 | 0 | 0 | Battery-supported
2025-06-22 16:00 | 173 | 6 | Winter | 16 | 0 | -20.8 | 3.98 | 85.1 | 0 | 0 | 0.02 | 0.02 | 20.8 | 59.29 | 15 | -37.06 | 22.21 | 7.755 | 0 | Diesel-backup
2025-06-22 17:00 | 173 | 6 | Winter | 17 | 0 | -28 | 2.23 | 72.7 | 0 | 0 | 0 | 0 | 28 | 73.1 | 15 | 0 | 73.1 | 23.392 | 0 | Diesel-backup
2025-06-22 18:00 | 173 | 6 | Winter | 18 | 0 | -23.7 | 10.05 | 78.2 | 0 | 0 | 39.33 | 39.33 | 23.7 | 72.88 | 15 | 0 | 33.55 | 11.228 | 0 | Diesel-backup
2025-06-22 19:00 | 173 | 6 | Winter | 19 | 0 | -19.6 | 5.34 | 58.3 | 0 | 0 | 0.87 | 0.87 | 19.6 | 58.08 | 15 | 0 | 57.21 | 18.307 | 0 | Diesel-backup
2025-06-22 20:00 | 173 | 6 | Winter | 20 | 0 | -24.2 | 7.07 | 83.5 | 0 | 0 | 6.37 | 6.37 | 24.2 | 71.38 | 15 | 0 | 65.01 | 20.803 | 0 | Diesel-backup
2025-06-22 21:00 | 173 | 6 | Winter | 21 | 0 | -27.8 | 27.6 | 29.3 | 0 | 0 | 120 | 120 | 27.8 | 67.64 | 34.27 | 52.36 | 0 | 0 | 0 | Normal
2025-06-22 22:00 | 173 | 6 | Winter | 22 | 0 | -24.8 | 13.72 | 10.9 | 0 | 0 | 120 | 120 | 24.8 | 55.15 | 58.13 | 64.85 | 0 | 0 | 0 | Normal
2025-06-22 23:00 | 173 | 6 | Winter | 23 | 0 | -20.7 | 5.96 | 75.3 | 0 | 0 | 2.08 | 2.08 | 20.7 | 47.43 | 39.99 | -45.35 | 0 | 0 | 0 | Battery-supported
2025-06-23 | 174 | 6 | Winter | 0 | 0 | -23.2 | 34.78 | 7.9 | 0 | 0 | 0 | 0 | 23.2 | 58.45 | 16.61 | -58.45 | 0 | 0 | 0 | Battery-supported
2025-06-23 01:00 | 174 | 6 | Winter | 1 | 0 | -25.9 | 12.48 | 38.7 | 0 | 0 | 101.35 | 101.35 | 25.9 | 60.21 | 31.75 | 41.14 | 0 | 0 | 0 | Normal
2025-06-23 02:00 | 174 | 6 | Winter | 2 | 0 | -25.5 | 0.84 | 80.3 | 0 | 0 | 0 | 0 | 25.5 | 59.62 | 15 | -41.88 | 17.74 | 6.295 | 0 | Diesel-backup
2025-06-23 03:00 | 174 | 6 | Winter | 3 | 0 | -25.3 | 33.07 | 88.7 | 0 | 0 | 0 | 0 | 25.3 | 64.81 | 15 | 0 | 64.81 | 20.739 | 0 | Diesel-backup
2025-06-23 04:00 | 174 | 6 | Winter | 4 | 0 | -23.2 | 23.98 | 39.7 | 0 | 0 | 120 | 120 | 23.2 | 56.79 | 38.26 | 63.21 | 0 | 0 | 0 | Normal
2025-06-23 05:00 | 174 | 6 | Winter | 5 | 0 | -21.1 | 12.73 | 74.2 | 0 | 0 | 110.06 | 110.06 | 21.1 | 65.78 | 54.56 | 44.28 | 0 | 0 | 0 | Normal
2025-06-23 06:00 | 174 | 6 | Winter | 6 | 0 | -21.7 | 10.01 | 26.1 | 0 | 0 | 38.61 | 38.61 | 21.7 | 50.56 | 49.78 | -11.95 | 0 | 0 | 0 | Battery-supported
2025-06-23 07:00 | 174 | 6 | Winter | 7 | 0 | -23 | 17.06 | 28.6 | 0 | 0 | 120 | 120 | 23 | 54.53 | 73.87 | 65.47 | 0 | 0 | 0 | Normal
2025-06-23 08:00 | 174 | 6 | Winter | 8 | 0 | -27 | 12.1 | 25.5 | 0 | 0 | 89.02 | 89.02 | 27 | 66.51 | 82.15 | 22.51 | 0 | 0 | 0 | Normal
2025-06-23 09:00 | 174 | 6 | Winter | 9 | 0 | -27 | 7.97 | 62.5 | 0 | 0 | 12.5 | 12.5 | 27 | 69.25 | 59.45 | -56.75 | 0 | 0 | 0 | Battery-supported
2025-06-23 10:00 | 174 | 6 | Winter | 10 | 0 | -22.9 | 7.66 | 61.8 | 0 | 0 | 10.08 | 10.08 | 22.9 | 71.58 | 34.85 | -61.5 | 0 | 0 | 0 | Battery-supported
2025-06-23 11:00 | 174 | 6 | Winter | 11 | 0 | -27 | 18.62 | 81.8 | 0 | 0 | 120 | 120 | 27 | 65.53 | 54.9 | 54.47 | 0 | 0 | 0 | Normal
2025-06-23 12:00 | 174 | 6 | Winter | 12 | 0 | -24.5 | 5.96 | 39 | 0 | 0 | 2.08 | 2.08 | 24.5 | 63.89 | 30.17 | -61.81 | 0 | 0 | 0 | Battery-supported
2025-06-23 13:00 | 174 | 6 | Winter | 13 | 0 | -23.4 | 18.47 | 46.2 | 0 | 0 | 120 | 120 | 23.4 | 63.86 | 50.83 | 56.14 | 0 | 0 | 0 | Normal
2025-06-23 14:00 | 174 | 6 | Winter | 14 | 0 | -26.5 | 10.95 | 10.4 | 0 | 0 | 57.87 | 57.87 | 26.5 | 69.14 | 46.33 | -11.27 | 0 | 0 | 0 | Battery-supported
2025-06-23 15:00 | 174 | 6 | Winter | 15 | 0 | -26.3 | 3.47 | 63.1 | 0 | 0 | 0 | 0 | 26.3 | 69.95 | 18.35 | -69.95 | 0 | 0 | 0 | Battery-supported
2025-06-23 16:00 | 174 | 6 | Winter | 16 | 0 | -24.2 | 19.32 | 79.8 | 0 | 0 | 120 | 120 | 24.2 | 65.64 | 38.35 | 54.36 | 0 | 0 | 0 | Normal
2025-06-23 17:00 | 174 | 6 | Winter | 17 | 0 | -22.9 | 6.07 | 47.9 | 0 | 0 | 2.38 | 2.38 | 22.9 | 60.74 | 15.01 | -58.36 | 0 | 0 | 0 | Battery-supported
2025-06-23 18:00 | 174 | 6 | Winter | 18 | 0 | -21.7 | 6.61 | 26.1 | 0 | 0 | 4.21 | 4.21 | 21.7 | 64.31 | 15 | -0.01 | 60.09 | 19.227 | 0 | Diesel-backup
2025-06-23 19:00 | 174 | 6 | Winter | 19 | 0 | -22.7 | 9.42 | 25.7 | 0 | 0 | 29.04 | 29.04 | 22.7 | 71.43 | 15 | 0 | 42.39 | 13.706 | 0 | Diesel-backup
2025-06-23 20:00 | 174 | 6 | Winter | 20 | 0 | -23.9 | 10.36 | 21.3 | 0 | 0 | 45.18 | 45.18 | 23.9 | 70.56 | 15 | 0 | 25.38 | 8.759 | 0 | Diesel-backup
2025-06-23 21:00 | 174 | 6 | Winter | 21 | 0 | -25.7 | 12.78 | 21.1 | 0 | 0 | 111.85 | 111.85 | 25.7 | 58.87 | 34.5 | 52.98 | 0 | 0 | 0 | Normal
2025-06-23 22:00 | 174 | 6 | Winter | 22 | 0 | -26.4 | 18.75 | 85.8 | 0 | 0 | 120 | 120 | 26.4 | 61.69 | 55.95 | 58.31 | 0 | 0 | 0 | Normal
2025-06-23 23:00 | 174 | 6 | Winter | 23 | 0 | -25.2 | 18.4 | 42.7 | 0 | 0 | 120 | 120 | 25.2 | 62.2 | 77.23 | 57.8 | 0 | 0 | 0 | Normal
2025-06-24 | 175 | 6 | Winter | 0 | 0 | -23.2 | 7.53 | 22.5 | 0 | 0 | 9.16 | 9.16 | 23.2 | 61.74 | 56.19 | -52.58 | 0 | 0 | 0 | Battery-supported
2025-06-24 01:00 | 175 | 6 | Winter | 1 | 0 | -23.4 | 7.68 | 80.3 | 0 | 0 | 10.22 | 10.22 | 23.4 | 64.54 | 34.47 | -54.32 | 0 | 0 | 0 | Battery-supported
2025-06-24 02:00 | 175 | 6 | Winter | 2 | 0 | -28.7 | 17.64 | 41.9 | 0 | 0 | 120 | 120 | 28.7 | 64.77 | 54.79 | 55.23 | 0 | 0 | 0 | Normal
2025-06-24 03:00 | 175 | 6 | Winter | 3 | 0 | -25.8 | 5.38 | 89 | 0 | 0 | 0.93 | 0.93 | 25.8 | 56.11 | 32.72 | -55.18 | 0 | 0 | 0 | Battery-supported
2025-06-24 04:00 | 175 | 6 | Winter | 4 | 0 | -21.5 | 10.96 | 90.1 | 0 | 0 | 58.11 | 58.11 | 21.5 | 50.38 | 35.56 | 7.73 | 0 | 0 | 0 | Normal
2025-06-24 05:00 | 175 | 6 | Winter | 5 | 0 | -23.9 | 23.01 | 33.6 | 0 | 0 | 120 | 120 | 23.9 | 61.31 | 57.16 | 58.69 | 0 | 0 | 0 | Normal
2025-06-24 06:00 | 175 | 6 | Winter | 6 | 0 | -27.2 | 8.25 | 67.1 | 0 | 0 | 15 | 15 | 27.2 | 56.41 | 40.6 | -41.41 | 0 | 0 | 0 | Battery-supported
2025-06-24 07:00 | 175 | 6 | Winter | 7 | 0 | -18.9 | 3.95 | 55.8 | 0 | 0 | 0.01 | 0.01 | 18.9 | 57.16 | 17.74 | -57.15 | 0 | 0 | 0 | Battery-supported
2025-06-24 08:00 | 175 | 6 | Winter | 8 | 0 | -24.2 | 6.07 | 9 | 0 | 0 | 2.38 | 2.38 | 24.2 | 64.81 | 15 | -6.84 | 55.59 | 17.789 | 0 | Diesel-backup
2025-06-24 09:00 | 175 | 6 | Winter | 9 | 0 | -23.3 | 6.33 | 27 | 0 | 0 | 3.17 | 3.17 | 23.3 | 61.44 | 15 | 0 | 58.27 | 18.646 | 0 | Diesel-backup
2025-06-24 10:00 | 175 | 6 | Winter | 10 | 0 | -23.2 | 5.74 | 33.4 | 0 | 0 | 1.57 | 1.57 | 23.2 | 68.25 | 15 | 0 | 66.68 | 21.338 | 0 | Diesel-backup
2025-06-24 11:00 | 175 | 6 | Winter | 11 | 0 | -24.9 | 9.16 | 52.3 | 0 | 0 | 25.38 | 25.38 | 24.9 | 63.81 | 15 | 0 | 38.43 | 12.621 | 0 | Diesel-backup
2025-06-24 12:00 | 175 | 6 | Winter | 12 | 0 | -25.7 | 32.74 | 34.5 | 0 | 0 | 0 | 0 | 25.7 | 70.59 | 15 | 0 | 70.59 | 22.589 | 0 | Diesel-backup
2025-06-24 13:00 | 175 | 6 | Winter | 13 | 0 | -19.4 | 14.31 | 45.6 | 0 | 0 | 120 | 120 | 19.4 | 63.13 | 35.93 | 56.87 | 0 | 0 | 0 | Normal
2025-06-24 14:00 | 175 | 6 | Winter | 14 | 0 | -21.9 | 9.71 | 98.6 | 0 | 0 | 33.52 | 33.52 | 21.9 | 57.29 | 26.42 | -23.77 | 0 | 0 | 0 | Battery-supported
2025-06-24 15:00 | 175 | 6 | Winter | 15 | 0 | -22.3 | 10.22 | 57.4 | 0 | 0 | 42.47 | 42.47 | 22.3 | 70.96 | 15.02 | -28.49 | 0 | 0 | 0 | Battery-supported
2025-06-24 16:00 | 175 | 6 | Winter | 16 | 0 | -22.8 | 6.88 | 22.4 | 0 | 0 | 5.4 | 5.4 | 22.8 | 70.97 | 15 | -0.06 | 65.51 | 20.963 | 0 | Diesel-backup
2025-06-24 17:00 | 175 | 6 | Winter | 17 | 0 | -26.3 | 10.2 | 43.6 | 0 | 0 | 42.1 | 42.1 | 26.3 | 73.11 | 15 | 0 | 31.01 | 10.479 | 0 | Diesel-backup
2025-06-24 18:00 | 175 | 6 | Winter | 18 | 0 | -21.3 | 22.45 | 27.7 | 0 | 0 | 120 | 120 | 21.3 | 68.19 | 34.07 | 51.81 | 0 | 0 | 0 | Normal
2025-06-24 19:00 | 175 | 6 | Winter | 19 | 0 | -26 | 11.18 | 57.9 | 0 | 0 | 63.4 | 63.4 | 26 | 66.09 | 32.99 | -2.69 | 0 | 0 | 0 | Battery-supported
2025-06-24 20:00 | 175 | 6 | Winter | 20 | 0 | -23.5 | 18.35 | 39.9 | 0 | 0 | 120 | 120 | 23.5 | 71.14 | 50.97 | 48.86 | 0 | 0 | 0 | Normal
2025-06-24 21:00 | 175 | 6 | Winter | 21 | 0 | -27.7 | 16.98 | 74.5 | 0 | 0 | 120 | 120 | 27.7 | 65.73 | 70.94 | 54.27 | 0 | 0 | 0 | Normal
2025-06-24 22:00 | 175 | 6 | Winter | 22 | 0 | -28.6 | 31.9 | 87.5 | 0 | 0 | 0 | 0 | 28.6 | 55.23 | 48.85 | -55.23 | 0 | 0 | 0 | Battery-supported
2025-06-24 23:00 | 175 | 6 | Winter | 23 | 0 | -23.4 | 16.81 | 49.1 | 0 | 0 | 120 | 120 | 23.4 | 54.54 | 72.94 | 65.46 | 0 | 0 | 0 | Normal
2025-06-25 | 176 | 6 | Winter | 0 | 0 | -26 | 30.69 | 21.4 | 0 | 0 | 0 | 0 | 26 | 57.97 | 49.75 | -57.97 | 0 | 0 | 0 | Battery-supported
2025-06-25 01:00 | 176 | 6 | Winter | 1 | 0 | -28.6 | 19.16 | 79.8 | 0 | 0 | 120 | 120 | 28.6 | 69.51 | 68.33 | 50.49 | 0 | 0 | 0 | Normal
2025-06-25 02:00 | 176 | 6 | Winter | 2 | 0 | -23 | 12.82 | 65.3 | 0 | 0 | 113.31 | 113.31 | 23 | 54.14 | 90.11 | 59.17 | 0 | 0 | 0 | Normal
2025-06-25 03:00 | 176 | 6 | Winter | 3 | 0 | -19.5 | 6.51 | 90.1 | 0 | 0 | 3.82 | 3.82 | 19.5 | 52.15 | 70.77 | -48.33 | 0 | 0 | 0 | Battery-supported
2025-06-25 04:00 | 176 | 6 | Winter | 4 | 0 | -21.1 | 18.31 | 27.3 | 0 | 0 | 120 | 120 | 21.1 | 50.96 | 95 | 65.83 | 0 | 0 | 0 | Normal
2025-06-25 05:00 | 176 | 6 | Winter | 5 | 0 | -24.8 | 19.2 | 53.2 | 0 | 0 | 120 | 120 | 24.8 | 57.89 | 95 | 0 | 0 | 0 | 0 | Normal
2025-06-25 06:00 | 176 | 6 | Winter | 6 | 0 | -24.2 | 19.49 | 12.3 | 0 | 0 | 120 | 120 | 24.2 | 63.34 | 95 | 0 | 0 | 0 | 0 | Normal
2025-06-25 07:00 | 176 | 6 | Winter | 7 | 0 | -22.2 | 1.24 | 60.3 | 0 | 0 | 0 | 0 | 22.2 | 51.51 | 74.4 | -51.51 | 0 | 0 | 0 | Battery-supported
2025-06-25 08:00 | 176 | 6 | Winter | 8 | 0 | -21.7 | 8.12 | 67.6 | 0 | 0 | 13.8 | 13.8 | 21.7 | 66.59 | 53.28 | -52.79 | 0 | 0 | 0 | Battery-supported
2025-06-25 09:00 | 176 | 6 | Winter | 9 | 0 | -24.9 | 14.22 | 25.1 | 0 | 0 | 120 | 120 | 24.9 | 64.39 | 73.74 | 55.61 | 0 | 0 | 0 | Normal
2025-06-25 10:00 | 176 | 6 | Winter | 10 | 0 | -24.1 | 8.51 | 65.3 | 0 | 0 | 17.6 | 17.6 | 24.1 | 74.63 | 50.93 | -57.03 | 0 | 0 | 0 | Battery-supported
2025-06-25 11:00 | 176 | 6 | Winter | 11 | 0 | -23.5 | 7.65 | 23.2 | 0 | 0 | 10 | 10 | 23.5 | 66.96 | 28.15 | -56.96 | 0 | 0 | 0 | Battery-supported
2025-06-25 12:00 | 176 | 6 | Winter | 12 | 0 | -23 | 6.87 | 35.4 | 0 | 0 | 5.36 | 5.36 | 23 | 65.66 | 15 | -32.87 | 27.43 | 9.394 | 0 | Diesel-backup
2025-06-25 13:00 | 176 | 6 | Winter | 13 | 0 | -24.5 | 3.56 | 81.7 | 0 | 0 | 0 | 0 | 24.5 | 65.18 | 15 | 0 | 65.18 | 20.858 | 0 | Diesel-backup
2025-06-25 14:00 | 176 | 6 | Winter | 14 | 0 | -24.5 | 13.78 | 73.4 | 0 | 0 | 120 | 120 | 24.5 | 68.36 | 34 | 51.64 | 0 | 0 | 0 | Normal
2025-06-25 15:00 | 176 | 6 | Winter | 15 | 0 | -21.2 | 7.32 | 56.1 | 0 | 0 | 7.8 | 7.8 | 21.2 | 58.32 | 15 | -47.51 | 3.01 | 1.125 | 0 | Diesel-backup
2025-06-25 16:00 | 176 | 6 | Winter | 16 | 0 | -21.5 | 8.26 | 47 | 0 | 0 | 15.09 | 15.09 | 21.5 | 64.89 | 15 | 0 | 49.8 | 15.936 | 0 | Diesel-backup
2025-06-25 17:00 | 176 | 6 | Winter | 17 | 0 | -23.1 | 9.72 | 32.2 | 0 | 0 | 33.68 | 33.68 | 23.1 | 63.75 | 15 | 0 | 30.07 | 10.197 | 0 | Diesel-backup
2025-06-25 18:00 | 176 | 6 | Winter | 18 | 0 | -20.4 | 15.09 | 33.9 | 0 | 0 | 120 | 120 | 20.4 | 60.88 | 36.76 | 59.12 | 0 | 0 | 0 | Normal
2025-06-25 19:00 | 176 | 6 | Winter | 19 | 0 | -25 | 12.61 | 77.6 | 0 | 0 | 105.82 | 105.82 | 25 | 76.24 | 47.64 | 29.58 | 0 | 0 | 0 | Normal
2025-06-25 20:00 | 176 | 6 | Winter | 20 | 0 | -20.6 | 12.27 | 93.8 | 0 | 0 | 94.41 | 94.41 | 20.6 | 69.22 | 56.91 | 25.19 | 0 | 0 | 0 | Normal
2025-06-25 21:00 | 176 | 6 | Winter | 21 | 0 | -23 | 1.95 | 29 | 0 | 0 | 0 | 0 | 23 | 63.84 | 31.38 | -63.84 | 0 | 0 | 0 | Battery-supported
2025-06-25 22:00 | 176 | 6 | Winter | 22 | 0 | -17 | 18.58 | 52.2 | 0 | 0 | 120 | 120 | 17 | 55.4 | 55.15 | 64.6 | 0 | 0 | 0 | Normal
2025-06-25 23:00 | 176 | 6 | Winter | 23 | 0 | -26.8 | 26.39 | 51.3 | 0 | 0 | 120 | 120 | 26.8 | 63.43 | 75.97 | 56.57 | 0 | 0 | 0 | Normal
2025-06-26 | 177 | 6 | Winter | 0 | 0 | -25.8 | 12.08 | 77.3 | 0 | 0 | 88.4 | 88.4 | 25.8 | 66.67 | 83.96 | 21.73 | 0 | 0 | 0 | Normal
2025-06-26 01:00 | 177 | 6 | Winter | 1 | 0 | -23.3 | 5.26 | 58.6 | 0 | 0 | 0.76 | 0.76 | 23.3 | 59.61 | 60.42 | -58.85 | 0 | 0 | 0 | Battery-supported
2025-06-26 02:00 | 177 | 6 | Winter | 2 | 0 | -23.4 | 7.79 | 86.5 | 0 | 0 | 11.05 | 11.05 | 23.4 | 60.87 | 40.49 | -49.82 | 0 | 0 | 0 | Battery-supported
2025-06-26 03:00 | 177 | 6 | Winter | 3 | 0 | -20 | 5.43 | 80.1 | 0 | 0 | 1.01 | 1.01 | 20 | 60.55 | 16.68 | -59.54 | 0 | 0 | 0 | Battery-supported
2025-06-26 04:00 | 177 | 6 | Winter | 4 | 0 | -25.7 | 24.68 | 40.8 | 0 | 0 | 120 | 120 | 25.7 | 63.96 | 37.3 | 56.04 | 0 | 0 | 0 | Normal
2025-06-26 05:00 | 177 | 6 | Winter | 5 | 0 | -22.3 | 8.24 | 73.9 | 0 | 0 | 14.91 | 14.91 | 22.3 | 59.07 | 19.64 | -44.16 | 0 | 0 | 0 | Battery-supported
2025-06-26 06:00 | 177 | 6 | Winter | 6 | 0 | -21.7 | 12.41 | 39 | 0 | 0 | 99 | 99 | 21.7 | 59.88 | 34.03 | 39.12 | 0 | 0 | 0 | Normal
2025-06-26 07:00 | 177 | 6 | Winter | 7 | 0 | -22.7 | 9.49 | 40.2 | 0 | 0 | 30.08 | 30.08 | 22.7 | 58.14 | 22.81 | -28.06 | 0 | 0 | 0 | Battery-supported
2025-06-26 08:00 | 177 | 6 | Winter | 8 | 0 | -26.4 | 14.7 | 93.8 | 0 | 0 | 120 | 120 | 26.4 | 71.43 | 40.68 | 48.57 | 0 | 0 | 0 | Normal
2025-06-26 09:00 | 177 | 6 | Winter | 9 | 0 | -21.2 | 6.24 | 14.7 | 0 | 0 | 2.88 | 2.88 | 21.2 | 66.62 | 15.19 | -63.74 | 0 | 0 | 0 | Battery-supported
2025-06-26 10:00 | 177 | 6 | Winter | 10 | 0 | -21.6 | 12.13 | 18.5 | 0 | 0 | 89.96 | 89.96 | 21.6 | 59.66 | 26.34 | 30.3 | 0 | 0 | 0 | Normal
2025-06-26 11:00 | 177 | 6 | Winter | 11 | 0 | -22.9 | 8.29 | 21.8 | 0 | 0 | 15.38 | 15.38 | 22.9 | 62.95 | 15 | -28.34 | 19.23 | 6.786 | 0 | Diesel-backup
2025-06-26 12:00 | 177 | 6 | Winter | 12 | 0 | -23.8 | 20.01 | 69.4 | 0 | 0 | 120 | 120 | 23.8 | 69.71 | 33.51 | 50.29 | 0 | 0 | 0 | Normal
2025-06-26 13:00 | 177 | 6 | Winter | 13 | 0 | -23.8 | 2.12 | 74.1 | 0 | 0 | 0 | 0 | 23.8 | 67.33 | 15 | -46.27 | 21.06 | 7.386 | 0 | Diesel-backup
2025-06-26 14:00 | 177 | 6 | Winter | 14 | 0 | -24.4 | 8.87 | 2.9 | 0 | 0 | 21.67 | 21.67 | 24.4 | 67.33 | 15 | 0 | 45.66 | 14.611 | 0 | Diesel-backup
2025-06-26 15:00 | 177 | 6 | Winter | 15 | 0 | -22.9 | 18.93 | 31.9 | 0 | 0 | 120 | 120 | 22.9 | 67.07 | 34.48 | 52.93 | 0 | 0 | 0 | Normal
2025-06-26 16:00 | 177 | 6 | Winter | 16 | 0 | -24.2 | 17.68 | 66.3 | 0 | 0 | 120 | 120 | 24.2 | 59.27 | 56.83 | 60.73 | 0 | 0 | 0 | Normal
2025-06-26 17:00 | 177 | 6 | Winter | 17 | 0 | -26.1 | 3.76 | 25.6 | 0 | 0 | 0 | 0 | 26.1 | 68.42 | 29.46 | -68.42 | 0 | 0 | 0 | Battery-supported
2025-06-26 18:00 | 177 | 6 | Winter | 18 | 0 | -26.6 | 16.58 | 22.8 | 0 | 0 | 120 | 120 | 26.6 | 68.96 | 48.24 | 51.04 | 0 | 0 | 0 | Normal
2025-06-26 19:00 | 177 | 6 | Winter | 19 | 0 | -25.9 | 5.86 | 57.4 | 0 | 0 | 1.84 | 1.84 | 25.9 | 69.62 | 21.13 | -67.78 | 0 | 0 | 0 | Battery-supported
2025-06-26 20:00 | 177 | 6 | Winter | 20 | 0 | -23.8 | 7.04 | 59.9 | 0 | 0 | 6.21 | 6.21 | 23.8 | 70.22 | 15 | -15.32 | 48.69 | 15.58 | 0 | Diesel-backup
2025-06-26 21:00 | 177 | 6 | Winter | 21 | 0 | -24.3 | 18.34 | 38 | 0 | 0 | 120 | 120 | 24.3 | 57.84 | 37.87 | 62.16 | 0 | 0 | 0 | Normal
2025-06-26 22:00 | 177 | 6 | Winter | 22 | 0 | -23.8 | 8.76 | 42.5 | 0 | 0 | 20.37 | 20.37 | 23.8 | 64.18 | 20.35 | -43.81 | 0 | 0 | 0 | Battery-supported
2025-06-26 23:00 | 177 | 6 | Winter | 23 | 0 | -23.2 | 3.58 | 64.8 | 0 | 0 | 0 | 0 | 23.2 | 54.31 | 15 | -13.38 | 40.93 | 13.312 | 0 | Diesel-backup
2025-06-27 | 178 | 6 | Winter | 0 | 0 | -25.7 | 4.91 | 58.2 | 0 | 0 | 0.39 | 0.39 | 25.7 | 63.48 | 15 | 0 | 63.09 | 20.189 | 0 | Diesel-backup
2025-06-27 01:00 | 178 | 6 | Winter | 1 | 0 | -21.1 | 11.07 | 73.2 | 0 | 0 | 60.72 | 60.72 | 21.1 | 54.02 | 17.47 | 6.7 | 0 | 0 | 0 | Normal
2025-06-27 02:00 | 178 | 6 | Winter | 2 | 0 | -24.9 | 8.59 | 78.4 | 0 | 0 | 18.46 | 18.46 | 24.9 | 64.57 | 15 | -6.16 | 39.95 | 13.041 | 0 | Diesel-backup
2025-06-27 03:00 | 178 | 6 | Winter | 3 | 0 | -25.3 | 8.49 | 59 | 0 | 0 | 17.39 | 17.39 | 25.3 | 61.18 | 15 | 0 | 43.79 | 14.081 | 0 | Diesel-backup
2025-06-27 04:00 | 178 | 6 | Winter | 4 | 0 | -23.3 | 14.57 | 52.4 | 0 | 0 | 120 | 120 | 23.3 | 53.48 | 39.48 | 66.52 | 0 | 0 | 0 | Normal
2025-06-27 05:00 | 178 | 6 | Winter | 5 | 0 | -28.4 | 13.07 | 56.2 | 0 | 0 | 120 | 120 | 28.4 | 63.81 | 60.16 | 56.19 | 0 | 0 | 0 | Normal
2025-06-27 06:00 | 178 | 6 | Winter | 6 | 0 | -26.1 | 8.97 | 19.2 | 0 | 0 | 22.91 | 22.91 | 26.1 | 62.7 | 44.24 | -39.79 | 0 | 0 | 0 | Battery-supported
2025-06-27 07:00 | 178 | 6 | Winter | 7 | 0 | -22.2 | 17.87 | 67.5 | 0 | 0 | 120 | 120 | 22.2 | 58.1 | 67.02 | 61.9 | 0 | 0 | 0 | Normal
2025-06-27 08:00 | 178 | 6 | Winter | 8 | 0 | -28.2 | 14.64 | 92.2 | 0 | 0 | 120 | 120 | 28.2 | 72.52 | 84.49 | 47.48 | 0 | 0 | 0 | Normal
2025-06-27 09:00 | 178 | 6 | Winter | 9 | 0 | -21.9 | 12.61 | 43.5 | 0 | 0 | 105.82 | 105.82 | 21.9 | 64 | 95 | 28.55 | 0 | 0 | 0 | Normal
2025-06-27 10:00 | 178 | 6 | Winter | 10 | 0 | -21 | 7.76 | 32.1 | 0 | 0 | 10.82 | 10.82 | 21 | 61.76 | 74.62 | -50.94 | 0 | 0 | 0 | Battery-supported
2025-06-27 11:00 | 178 | 6 | Winter | 11 | 0 | -25.1 | 19.49 | 58.6 | 0 | 0 | 120 | 120 | 25.1 | 61.52 | 95 | 55.37 | 0 | 0 | 0 | Normal
2025-06-27 12:00 | 178 | 6 | Winter | 12 | 0 | -23.7 | 8.43 | 51.5 | 0 | 0 | 16.77 | 16.77 | 23.7 | 69.03 | 74.1 | -52.26 | 0 | 0 | 0 | Battery-supported
2025-06-27 13:00 | 178 | 6 | Winter | 13 | 0 | -21.9 | 8.91 | 25.6 | 0 | 0 | 22.16 | 22.16 | 21.9 | 66.93 | 56.19 | -44.77 | 0 | 0 | 0 | Battery-supported
2025-06-27 14:00 | 178 | 6 | Winter | 14 | 0 | -25.4 | 25.02 | 91.8 | 0 | 0 | 120 | 120 | 25.4 | 76.04 | 72.37 | 43.96 | 0 | 0 | 0 | Normal
2025-06-27 15:00 | 178 | 6 | Winter | 15 | 0 | -22.4 | 6.08 | 89 | 0 | 0 | 2.4 | 2.4 | 22.4 | 65.23 | 47.23 | -62.83 | 0 | 0 | 0 | Battery-supported
2025-06-27 16:00 | 178 | 6 | Winter | 16 | 0 | -25.8 | 6.02 | 15.8 | 0 | 0 | 2.24 | 2.24 | 25.8 | 69.91 | 20.17 | -67.67 | 0 | 0 | 0 | Battery-supported
2025-06-27 17:00 | 178 | 6 | Winter | 17 | 0 | -25.4 | 9.12 | 81.7 | 0 | 0 | 24.84 | 24.84 | 25.4 | 69 | 15 | -12.91 | 31.25 | 10.549 | 0 | Diesel-backup
2025-06-27 18:00 | 178 | 6 | Winter | 18 | 0 | -26.1 | 5.24 | 72.8 | 0 | 0 | 0.74 | 0.74 | 26.1 | 72.57 | 15 | 0 | 71.83 | 22.986 | 0 | Diesel-backup
2025-06-27 19:00 | 178 | 6 | Winter | 19 | 0 | -23.6 | 5.33 | 72.9 | 0 | 0 | 0.86 | 0.86 | 23.6 | 64.54 | 15 | 0 | 63.68 | 20.378 | 0 | Diesel-backup
2025-06-27 20:00 | 178 | 6 | Winter | 20 | 0 | -21.8 | 24.61 | 21.4 | 0 | 0 | 120 | 120 | 21.8 | 65.4 | 35.09 | 54.6 | 0 | 0 | 0 | Normal
2025-06-27 21:00 | 178 | 6 | Winter | 21 | 0 | -24.7 | 9.03 | 82.9 | 0 | 0 | 23.67 | 23.67 | 24.7 | 59.81 | 20.64 | -36.14 | 0 | 0 | 0 | Battery-supported
2025-06-27 22:00 | 178 | 6 | Winter | 22 | 0 | -27.1 | 12.86 | 74.9 | 0 | 0 | 114.77 | 114.77 | 27.1 | 65.07 | 38.93 | 49.7 | 0 | 0 | 0 | Normal
2025-06-27 23:00 | 178 | 6 | Winter | 23 | 0 | -26.7 | 4.03 | 26.2 | 0 | 0 | 0.02 | 0.02 | 26.7 | 70.59 | 15 | -59.82 | 10.75 | 3.913 | 0 | Diesel-backup
2025-06-28 | 179 | 6 | Winter | 0 | 0 | -23.5 | 5.74 | 26 | 0 | 0 | 1.57 | 1.57 | 23.5 | 59.82 | 15 | 0 | 58.25 | 18.64 | 0 | Diesel-backup
2025-06-28 01:00 | 179 | 6 | Winter | 1 | 0 | -20.3 | 26.56 | 52.6 | 0 | 0 | 120 | 120 | 20.3 | 49.52 | 40.94 | 70.48 | 0 | 0 | 0 | Normal
2025-06-28 02:00 | 179 | 6 | Winter | 2 | 0 | -23.5 | 5.28 | 69.1 | 0 | 0 | 0.79 | 0.79 | 23.5 | 53.81 | 19.73 | -53.02 | 0 | 0 | 0 | Battery-supported
2025-06-28 03:00 | 179 | 6 | Winter | 3 | 0 | -25.2 | 13.11 | 27.4 | 0 | 0 | 120 | 120 | 25.2 | 64.42 | 40.18 | 55.58 | 0 | 0 | 0 | Normal
2025-06-28 04:00 | 179 | 6 | Winter | 4 | 0 | -22.7 | 1.15 | 7.6 | 0 | 0 | 0 | 0 | 22.7 | 51.04 | 19.77 | -51.04 | 0 | 0 | 0 | Battery-supported
2025-06-28 05:00 | 179 | 6 | Winter | 5 | 0 | -24.9 | 3.81 | 27.9 | 0 | 0 | 0 | 0 | 24.9 | 61.17 | 15 | -11.92 | 49.25 | 15.762 | 0 | Diesel-backup
2025-06-28 06:00 | 179 | 6 | Winter | 6 | 0 | -25.2 | 8.95 | 79.6 | 0 | 0 | 22.66 | 22.66 | 25.2 | 57.28 | 15 | 0 | 34.62 | 11.538 | 0 | Diesel-backup
2025-06-28 07:00 | 179 | 6 | Winter | 7 | 0 | -26.5 | 17.58 | 31.1 | 0 | 0 | 120 | 120 | 26.5 | 72.29 | 32.56 | 47.71 | 0 | 0 | 0 | Normal
2025-06-28 08:00 | 179 | 6 | Winter | 8 | 0 | -21.3 | 10.72 | 28.6 | 0 | 0 | 52.68 | 52.68 | 21.3 | 59.45 | 29.85 | -6.77 | 0 | 0 | 0 | Battery-supported
2025-06-28 09:00 | 179 | 6 | Winter | 9 | 0 | -30 | 9.45 | 38.8 | 0 | 0 | 29.48 | 29.48 | 30 | 70.35 | 15 | -37.12 | 3.75 | 1.397 | 0 | Diesel-backup
2025-06-28 10:00 | 179 | 6 | Winter | 10 | 0 | -22.6 | 15.34 | 41.6 | 0 | 0 | 120 | 120 | 22.6 | 68.73 | 33.87 | 51.27 | 0 | 0 | 0 | Normal
2025-06-28 11:00 | 179 | 6 | Winter | 11 | 0 | -25.4 | 12.05 | 80.2 | 0 | 0 | 87.48 | 87.48 | 25.4 | 67.47 | 41.23 | 20.01 | 0 | 0 | 0 | Normal
2025-06-28 12:00 | 179 | 6 | Winter | 12 | 0 | -25.3 | 3.1 | 90.1 | 0 | 0 | 0 | 0 | 25.3 | 65.42 | 15.06 | -65.42 | 0 | 0 | 0 | Battery-supported
2025-06-28 13:00 | 179 | 6 | Winter | 13 | 0 | -20.7 | 10.3 | 22.7 | 0 | 0 | 44.01 | 44.01 | 20.7 | 59.84 | 15 | -0.16 | 15.67 | 5.603 | 0 | Diesel-backup
2025-06-28 14:00 | 179 | 6 | Winter | 14 | 0 | -26 | 7.87 | 21.1 | 0 | 0 | 11.68 | 11.68 | 26 | 66.37 | 15 | 0 | 54.69 | 17.501 | 0 | Diesel-backup
2025-06-28 15:00 | 179 | 6 | Winter | 15 | 0 | -25.9 | 9.24 | 0 | 0 | 0 | 26.47 | 26.47 | 25.9 | 65.28 | 15 | 0 | 38.81 | 12.727 | 0 | Diesel-backup
2025-06-28 16:00 | 179 | 6 | Winter | 16 | 0 | -24.7 | 7.73 | 43.9 | 0 | 0 | 10.59 | 10.59 | 24.7 | 67.65 | 15 | 0 | 57.06 | 18.259 | 0 | Diesel-backup
2025-06-28 17:00 | 179 | 6 | Winter | 17 | 0 | -23.5 | 10.38 | 51.9 | 0 | 0 | 45.58 | 45.58 | 23.5 | 74.2 | 15 | 0 | 28.62 | 9.758 | 0 | Diesel-backup
2025-06-28 18:00 | 179 | 6 | Winter | 18 | 0 | -25.4 | 13.37 | 74.2 | 0 | 0 | 120 | 120 | 25.4 | 76.65 | 30.95 | 43.35 | 0 | 0 | 0 | Normal
2025-06-28 19:00 | 179 | 6 | Winter | 19 | 0 | -27.9 | 4.39 | 40.5 | 0 | 0 | 0.1 | 0.1 | 27.9 | 79.08 | 15 | -39.88 | 39.1 | 12.807 | 0 | Diesel-backup
2025-06-28 20:00 | 179 | 6 | Winter | 20 | 0 | -26.3 | 6.74 | 27.1 | 0 | 0 | 4.76 | 4.76 | 26.3 | 68.78 | 15 | 0 | 64.02 | 20.486 | 0 | Diesel-backup
2025-06-28 21:00 | 179 | 6 | Winter | 21 | 0 | -21.6 | 15.06 | 77.8 | 0 | 0 | 120 | 120 | 21.6 | 59.46 | 37.28 | 60.54 | 0 | 0 | 0 | Normal
2025-06-28 22:00 | 179 | 6 | Winter | 22 | 0 | -24.2 | 16.15 | 44.5 | 0 | 0 | 120 | 120 | 24.2 | 59.71 | 59.47 | 60.29 | 0 | 0 | 0 | Normal
2025-06-28 23:00 | 179 | 6 | Winter | 23 | 0 | -23.4 | 22.67 | 59.5 | 0 | 0 | 120 | 120 | 23.4 | 55.12 | 83.34 | 64.88 | 0 | 0 | 0 | Normal
2025-06-29 | 180 | 6 | Winter | 0 | 0 | -25 | 10.86 | 58.5 | 0 | 0 | 55.8 | 55.8 | 25 | 52.78 | 84.45 | 3.02 | 0 | 0 | 0 | Normal
2025-06-29 01:00 | 180 | 6 | Winter | 1 | 0 | -25.9 | 6.5 | 69.2 | 0 | 0 | 3.78 | 3.78 | 25.9 | 53.85 | 64.42 | -50.07 | 0 | 0 | 0 | Battery-supported
2025-06-29 02:00 | 180 | 6 | Winter | 2 | 0 | -20.8 | 6.82 | 19.6 | 0 | 0 | 5.12 | 5.12 | 20.8 | 56.42 | 43.9 | -51.3 | 0 | 0 | 0 | Battery-supported
2025-06-29 03:00 | 180 | 6 | Winter | 3 | 0 | -24.9 | 10.65 | 73.5 | 0 | 0 | 51.16 | 51.16 | 24.9 | 54.45 | 42.59 | -3.29 | 0 | 0 | 0 | Battery-supported
2025-06-29 04:00 | 180 | 6 | Winter | 4 | 0 | -25.4 | 5.74 | 37.9 | 0 | 0 | 1.57 | 1.57 | 25.4 | 57.22 | 20.33 | -55.65 | 0 | 0 | 0 | Battery-supported
2025-06-29 05:00 | 180 | 6 | Winter | 5 | 0 | -22 | 21.81 | 92.6 | 0 | 0 | 120 | 120 | 22 | 58.48 | 42.97 | 61.52 | 0 | 0 | 0 | Normal
2025-06-29 06:00 | 180 | 6 | Winter | 6 | 0 | -26 | 7.7 | 31.5 | 0 | 0 | 10.37 | 10.37 | 26 | 51.67 | 26.45 | -41.3 | 0 | 0 | 0 | Battery-supported
2025-06-29 07:00 | 180 | 6 | Winter | 7 | 0 | -25.8 | 20.1 | 42.9 | 0 | 0 | 120 | 120 | 25.8 | 66.67 | 46.07 | 53.33 | 0 | 0 | 0 | Normal
2025-06-29 08:00 | 180 | 6 | Winter | 8 | 0 | -24.4 | 5.24 | 58.4 | 0 | 0 | 0.74 | 0.74 | 24.4 | 67.61 | 19.33 | -66.87 | 0 | 0 | 0 | Battery-supported
2025-06-29 09:00 | 180 | 6 | Winter | 9 | 0 | -24.5 | 9.27 | 68.1 | 0 | 0 | 26.89 | 26.89 | 24.5 | 65.99 | 15 | -10.81 | 28.29 | 9.657 | 0 | Diesel-backup
2025-06-29 10:00 | 180 | 6 | Winter | 10 | 0 | -23.9 | 8.43 | 58.4 | 0 | 0 | 16.77 | 16.77 | 23.9 | 64.35 | 15 | 0 | 47.58 | 15.226 | 0 | Diesel-backup
2025-06-29 11:00 | 180 | 6 | Winter | 11 | 0 | -19.9 | 3.95 | 48.2 | 0 | 0 | 0.01 | 0.01 | 19.9 | 64.79 | 15 | 0 | 64.78 | 20.73 | 0 | Diesel-backup
2025-06-29 12:00 | 180 | 6 | Winter | 12 | 0 | -23.7 | 8.83 | 57.7 | 0 | 0 | 21.19 | 21.19 | 23.7 | 62.84 | 15 | 0 | 41.65 | 13.507 | 0 | Diesel-backup
2025-06-29 13:00 | 180 | 6 | Winter | 13 | 0 | -29.7 | 12.03 | 16.5 | 0 | 0 | 86.87 | 86.87 | 29.7 | 77.98 | 18.27 | 8.89 | 0 | 0 | 0 | Normal
2025-06-29 14:00 | 180 | 6 | Winter | 14 | 0 | -23.7 | 2 | 45.8 | 0 | 0 | 0 | 0 | 23.7 | 70.17 | 15 | -8.18 | 61.99 | 19.837 | 0 | Diesel-backup
2025-06-29 15:00 | 180 | 6 | Winter | 15 | 0 | -24.4 | 14.11 | 69.1 | 0 | 0 | 120 | 120 | 24.4 | 64.5 | 35.42 | 55.5 | 0 | 0 | 0 | Normal
2025-06-29 16:00 | 180 | 6 | Winter | 16 | 0 | -24.4 | 12.64 | 47.5 | 0 | 0 | 106.87 | 106.87 | 24.4 | 66.62 | 50.24 | 40.25 | 0 | 0 | 0 | Normal
2025-06-29 17:00 | 180 | 6 | Winter | 17 | 0 | -23.9 | 10.24 | 67.6 | 0 | 0 | 42.85 | 42.85 | 23.9 | 71.75 | 38.68 | -28.9 | 0 | 0 | 0 | Battery-supported
2025-06-29 18:00 | 180 | 6 | Winter | 18 | 0 | -24.5 | 15.75 | 35.5 | 0 | 0 | 120 | 120 | 24.5 | 69.12 | 57.4 | 50.88 | 0 | 0 | 0 | Normal
2025-06-29 19:00 | 180 | 6 | Winter | 19 | 0 | -24.6 | 16.38 | 25.4 | 0 | 0 | 120 | 120 | 24.6 | 66.7 | 77.01 | 53.3 | 0 | 0 | 0 | Normal
2025-06-29 20:00 | 180 | 6 | Winter | 20 | 0 | -23.1 | 39.32 | 23 | 0 | 0 | 0 | 0 | 23.1 | 63.12 | 51.77 | -63.12 | 0 | 0 | 0 | Battery-supported
2025-06-29 21:00 | 180 | 6 | Winter | 21 | 0 | -25.7 | 3.81 | 26 | 0 | 0 | 0 | 0 | 25.7 | 60.25 | 27.67 | -60.25 | 0 | 0 | 0 | Battery-supported
2025-06-29 22:00 | 180 | 6 | Winter | 22 | 0 | -26.5 | 23.63 | 60.5 | 0 | 0 | 120 | 120 | 26.5 | 59.85 | 49.8 | 60.15 | 0 | 0 | 0 | Normal
2025-06-29 23:00 | 180 | 6 | Winter | 23 | 0 | -17.8 | 18.1 | 43.1 | 0 | 0 | 120 | 120 | 17.8 | 54.04 | 74.07 | 65.96 | 0 | 0 | 0 | Normal
2025-06-30 | 181 | 6 | Winter | 0 | 0 | -26.1 | 12.65 | 36.3 | 0 | 0 | 107.22 | 107.22 | 26.1 | 59.84 | 91.51 | 47.38 | 0 | 0 | 0 | Normal
2025-06-30 01:00 | 181 | 6 | Winter | 1 | 0 | -24.3 | 5.32 | 25.7 | 0 | 0 | 0.84 | 0.84 | 24.3 | 55.43 | 69.67 | -54.59 | 0 | 0 | 0 | Battery-supported
2025-06-30 02:00 | 181 | 6 | Winter | 2 | 0 | -27.8 | 8.06 | 7.9 | 0 | 0 | 13.27 | 13.27 | 27.8 | 67.19 | 48.11 | -53.92 | 0 | 0 | 0 | Battery-supported
2025-06-30 03:00 | 181 | 6 | Winter | 3 | 0 | -24.3 | 7.35 | 47.5 | 0 | 0 | 7.99 | 7.99 | 24.3 | 61.47 | 26.71 | -53.48 | 0 | 0 | 0 | Battery-supported
2025-06-30 04:00 | 181 | 6 | Winter | 4 | 0 | -26.6 | 9.62 | 2.9 | 0 | 0 | 32.08 | 32.08 | 26.6 | 57.61 | 16.5 | -25.53 | 0 | 0 | 0 | Battery-supported
2025-06-30 05:00 | 181 | 6 | Winter | 5 | 0 | -25.5 | 15.41 | 34.1 | 0 | 0 | 120 | 120 | 25.5 | 58.14 | 39.27 | 61.86 | 0 | 0 | 0 | Normal
2025-06-30 06:00 | 181 | 6 | Winter | 6 | 0 | -22.2 | 21.16 | 39.5 | 0 | 0 | 120 | 120 | 22.2 | 60.04 | 61.33 | 59.96 | 0 | 0 | 0 | Normal
2025-06-30 07:00 | 181 | 6 | Winter | 7 | 0 | -23.5 | 27.47 | 29.8 | 0 | 0 | 120 | 120 | 23.5 | 55.14 | 85.2 | 64.86 | 0 | 0 | 0 | Normal
2025-06-30 08:00 | 181 | 6 | Winter | 8 | 0 | -23.3 | 8.09 | 35.8 | 0 | 0 | 13.53 | 13.53 | 23.3 | 65.62 | 64.36 | -52.09 | 0 | 0 | 0 | Battery-supported
2025-06-30 09:00 | 181 | 6 | Winter | 9 | 0 | -28.4 | 11.49 | 88.9 | 0 | 0 | 71.39 | 71.39 | 28.4 | 70.24 | 64.79 | 1.15 | 0 | 0 | 0 | Normal
2025-06-30 10:00 | 181 | 6 | Winter | 10 | 0 | -20.5 | 6 | 50.2 | 0 | 0 | 2.19 | 2.19 | 20.5 | 60.61 | 41.42 | -58.42 | 0 | 0 | 0 | Battery-supported
2025-06-30 11:00 | 181 | 6 | Winter | 11 | 0 | -27.1 | 18.59 | 81.6 | 0 | 0 | 120 | 120 | 27.1 | 65.85 | 61.35 | 54.15 | 0 | 0 | 0 | Normal
2025-06-30 12:00 | 181 | 6 | Winter | 12 | 0 | -21.2 | 13.12 | 60.3 | 0 | 0 | 120 | 120 | 21.2 | 63.98 | 81.96 | 56.02 | 0 | 0 | 0 | Normal
2025-06-30 13:00 | 181 | 6 | Winter | 13 | 0 | -22.3 | 9.09 | 59.1 | 0 | 0 | 24.45 | 24.45 | 22.3 | 61.58 | 67.11 | -37.13 | 0 | 0 | 0 | Battery-supported
2025-06-30 14:00 | 181 | 6 | Winter | 14 | 0 | -23.2 | 3.64 | 98.6 | 0 | 0 | 0 | 0 | 23.2 | 63.81 | 41.59 | -63.81 | 0 | 0 | 0 | Battery-supported
2025-06-30 15:00 | 181 | 6 | Winter | 15 | 0 | -26.4 | 11.59 | 49.7 | 0 | 0 | 74.11 | 74.11 | 26.4 | 72.8 | 42.07 | 1.31 | 0 | 0 | 0 | Normal
2025-06-30 16:00 | 181 | 6 | Winter | 16 | 0 | -24.2 | 12.31 | 84.1 | 0 | 0 | 95.71 | 95.71 | 24.2 | 64.33 | 53.62 | 31.38 | 0 | 0 | 0 | Normal
2025-06-30 17:00 | 181 | 6 | Winter | 17 | 0 | -25.6 | 2.87 | 33.5 | 0 | 0 | 0 | 0 | 25.6 | 70.43 | 25.44 | -70.43 | 0 | 0 | 0 | Battery-supported
2025-06-30 18:00 | 181 | 6 | Winter | 18 | 0 | -24.5 | 4.44 | 67.9 | 0 | 0 | 0.12 | 0.12 | 24.5 | 71.33 | 15 | -26.11 | 45.1 | 14.432 | 0 | Diesel-backup
2025-06-30 19:00 | 181 | 6 | Winter | 19 | 0 | -25.1 | 11.42 | 81.4 | 0 | 0 | 69.53 | 69.53 | 25.1 | 67.67 | 15.68 | 1.86 | 0 | 0 | 0 | Normal
2025-06-30 20:00 | 181 | 6 | Winter | 20 | 0 | -29 | 26.13 | 43.7 | 0 | 0 | 120 | 120 | 29 | 74.04 | 32.6 | 45.96 | 0 | 0 | 0 | Normal
2025-06-30 21:00 | 181 | 6 | Winter | 21 | 0 | -22.1 | 19.7 | 25.5 | 0 | 0 | 120 | 120 | 22.1 | 53.67 | 57.01 | 66.33 | 0 | 0 | 0 | Normal
2025-06-30 22:00 | 181 | 6 | Winter | 22 | 0 | -24.7 | 9.25 | 88.4 | 0 | 0 | 26.61 | 26.61 | 24.7 | 62.66 | 42.59 | -36.05 | 0 | 0 | 0 | Battery-supported
2025-06-30 23:00 | 181 | 6 | Winter | 23 | 0 | -25.6 | 8.41 | 60.2 | 0 | 0 | 16.57 | 16.57 | 25.6 | 63.18 | 23.94 | -46.61 | 0 | 0 | 0 | Battery-supported
2025-07-01 | 182 | 7 | Winter | 0 | 0 | -25.8 | 6.63 | 28.5 | 0 | 0 | 4.29 | 4.29 | 25.8 | 66.62 | 15 | -22.36 | 39.97 | 13.048 | 0 | Diesel-backup
2025-07-01 01:00 | 182 | 7 | Winter | 1 | 0 | -23.8 | 6.19 | 57.8 | 0 | 0 | 2.72 | 2.72 | 23.8 | 63.49 | 15 | 0 | 60.77 | 19.446 | 0 | Diesel-backup
2025-07-01 02:00 | 182 | 7 | Winter | 2 | 0 | -26.5 | 8.8 | 14.4 | 0 | 0 | 20.84 | 20.84 | 26.5 | 62.56 | 15 | 0 | 41.72 | 13.526 | 0 | Diesel-backup
2025-07-01 03:00 | 182 | 7 | Winter | 3 | 0 | -29.5 | 30.55 | 10.2 | 0 | 0 | 0 | 0 | 29.5 | 75.54 | 15 | 0 | 75.54 | 24.173 | 0 | Diesel-backup
2025-07-01 04:00 | 182 | 7 | Winter | 4 | 0 | -23.7 | 8.38 | 73.2 | 0 | 0 | 16.27 | 16.27 | 23.7 | 62.24 | 15 | 0 | 45.97 | 14.71 | 0 | Diesel-backup
2025-07-01 05:00 | 182 | 7 | Winter | 5 | 0 | -23.4 | 10.42 | 18.5 | 0 | 0 | 46.38 | 46.38 | 23.4 | 63.49 | 15 | 0 | 17.11 | 6.086 | 0 | Diesel-backup
2025-07-01 06:00 | 182 | 7 | Winter | 6 | 0 | -25 | 4.67 | 80.7 | 0 | 0 | 0.22 | 0.22 | 25 | 58.16 | 15 | 0 | 57.94 | 18.541 | 0 | Diesel-backup
2025-07-01 07:00 | 182 | 7 | Winter | 7 | 0 | -27.1 | 14.44 | 55.5 | 0 | 0 | 120 | 120 | 27.1 | 60.63 | 36.85 | 59.37 | 0 | 0 | 0 | Normal
2025-07-01 08:00 | 182 | 7 | Winter | 8 | 0 | -24.4 | 10.31 | 41.8 | 0 | 0 | 44.2 | 44.2 | 24.4 | 67.69 | 27.45 | -23.49 | 0 | 0 | 0 | Battery-supported
2025-07-01 09:00 | 182 | 7 | Winter | 9 | 0 | -27.8 | 8.07 | 87 | 0 | 0 | 13.36 | 13.36 | 27.8 | 66.79 | 15 | -31.13 | 22.3 | 7.784 | 0 | Diesel-backup
2025-07-01 10:00 | 182 | 7 | Winter | 10 | 0 | -26.8 | 5.45 | 34.7 | 0 | 0 | 1.04 | 1.04 | 26.8 | 69.95 | 15 | 0 | 68.91 | 22.051 | 0 | Diesel-backup
2025-07-01 11:00 | 182 | 7 | Winter | 11 | 0 | -26.2 | 6.39 | 43.6 | 0 | 0 | 3.38 | 3.38 | 26.2 | 69.04 | 15 | 0 | 65.66 | 21.011 | 0 | Diesel-backup
2025-07-01 12:00 | 182 | 7 | Winter | 12 | 0 | -22.7 | 7.74 | 69.4 | 0 | 0 | 10.67 | 10.67 | 22.7 | 70.08 | 15 | 0 | 59.41 | 19.011 | 0 | Diesel-backup
2025-07-01 13:00 | 182 | 7 | Winter | 13 | 0 | -25.4 | 8.05 | 74.4 | 0 | 0 | 13.18 | 13.18 | 25.4 | 73.07 | 15 | 0 | 59.89 | 19.165 | 0 | Diesel-backup
2025-07-01 14:00 | 182 | 7 | Winter | 14 | 0 | -25.6 | 5.41 | 91.7 | 0 | 0 | 0.98 | 0.98 | 25.6 | 69.08 | 15 | 0 | 68.1 | 21.792 | 0 | Diesel-backup
2025-07-01 15:00 | 182 | 7 | Winter | 15 | 0 | -20.3 | 9.74 | 75.4 | 0 | 0 | 34.01 | 34.01 | 20.3 | 61.81 | 15 | 0 | 27.8 | 9.508 | 0 | Diesel-backup
2025-07-01 16:00 | 182 | 7 | Winter | 16 | 0 | -23.8 | 11.76 | 25.7 | 0 | 0 | 78.88 | 78.88 | 23.8 | 73.96 | 16.81 | 4.92 | 0 | 0 | 0 | Normal
2025-07-01 17:00 | 182 | 7 | Winter | 17 | 0 | -23.8 | 15.93 | 42.4 | 0 | 0 | 120 | 120 | 23.8 | 60.72 | 38.63 | 59.28 | 0 | 0 | 0 | Normal
2025-07-01 18:00 | 182 | 7 | Winter | 18 | 0 | -25.4 | 25.33 | 33.3 | 0 | 0 | 120 | 120 | 25.4 | 62.19 | 59.9 | 57.81 | 0 | 0 | 0 | Normal
2025-07-01 19:00 | 182 | 7 | Winter | 19 | 0 | -25.9 | 2.82 | 78.4 | 0 | 0 | 0 | 0 | 25.9 | 70.82 | 31.57 | -70.82 | 0 | 0 | 0 | Battery-supported
2025-07-01 20:00 | 182 | 7 | Winter | 20 | 0 | -29.4 | 12.8 | 84 | 0 | 0 | 112.58 | 112.58 | 29.4 | 72.12 | 46.46 | 40.46 | 0 | 0 | 0 | Normal
2025-07-01 21:00 | 182 | 7 | Winter | 21 | 0 | -22.4 | 8.63 | 51.5 | 0 | 0 | 18.9 | 18.9 | 22.4 | 56.17 | 31.55 | -37.27 | 0 | 0 | 0 | Battery-supported
2025-07-01 22:00 | 182 | 7 | Winter | 22 | 0 | -23.6 | 2.22 | 14.3 | 0 | 0 | 0 | 0 | 23.6 | 51.28 | 15 | -41.38 | 9.9 | 3.612 | 0 | Diesel-backup
2025-07-01 23:00 | 182 | 7 | Winter | 23 | 0 | -25 | 6.93 | 38.2 | 0 | 0 | 5.65 | 5.65 | 25 | 56.49 | 15 | 0 | 50.84 | 16.269 | 0 | Diesel-backup
2025-07-02 | 183 | 7 | Winter | 0 | 0 | -24.9 | 3.1 | 83.2 | 0 | 0 | 0 | 0 | 24.9 | 65.81 | 15 | 0 | 65.81 | 21.059 | 0 | Diesel-backup
2025-07-02 01:00 | 183 | 7 | Winter | 1 | 0 | -23 | 15 | 73.9 | 0 | 0 | 120 | 120 | 23 | 63.23 | 35.89 | 56.77 | 0 | 0 | 0 | Normal
2025-07-02 02:00 | 183 | 7 | Winter | 2 | 0 | -28 | 13.9 | 39.7 | 0 | 0 | 120 | 120 | 28 | 66.16 | 55.7 | 53.84 | 0 | 0 | 0 | Normal
2025-07-02 03:00 | 183 | 7 | Winter | 3 | 0 | -25.9 | 11.12 | 14.2 | 0 | 0 | 61.93 | 61.93 | 25.9 | 57.64 | 57.28 | 4.29 | 0 | 0 | 0 | Normal
2025-07-02 04:00 | 183 | 7 | Winter | 4 | 0 | -27.1 | 6.49 | 35.7 | 0 | 0 | 3.74 | 3.74 | 27.1 | 60.77 | 34.47 | -57.03 | 0 | 0 | 0 | Battery-supported
2025-07-02 05:00 | 183 | 7 | Winter | 5 | 0 | -20.7 | 21.64 | 17.8 | 0 | 0 | 120 | 120 | 20.7 | 54.09 | 58.73 | 65.91 | 0 | 0 | 0 | Normal
2025-07-02 06:00 | 183 | 7 | Winter | 6 | 0 | -22.7 | 4.97 | 51.1 | 0 | 0 | 0.44 | 0.44 | 22.7 | 54.99 | 36.91 | -54.55 | 0 | 0 | 0 | Battery-supported
2025-07-02 07:00 | 183 | 7 | Winter | 7 | 0 | -29.5 | 8.15 | 52.8 | 0 | 0 | 14.07 | 14.07 | 29.5 | 62.32 | 17.61 | -48.25 | 0 | 0 | 0 | Battery-supported
2025-07-02 08:00 | 183 | 7 | Winter | 8 | 0 | -28 | 9.08 | 46 | 0 | 0 | 24.32 | 24.32 | 28 | 70.6 | 15 | -6.52 | 39.76 | 12.991 | 0 | Diesel-backup
2025-07-02 09:00 | 183 | 7 | Winter | 9 | 0 | -24.9 | 9.86 | 61.1 | 0 | 0 | 36.01 | 36.01 | 24.9 | 62 | 15 | 0 | 25.99 | 8.949 | 0 | Diesel-backup
2025-07-02 10:00 | 183 | 7 | Winter | 10 | 0 | -25.7 | 33.81 | 25.9 | 0 | 0 | 0 | 0 | 25.7 | 73.42 | 15 | 0 | 73.42 | 23.494 | 0 | Diesel-backup
2025-07-02 11:00 | 183 | 7 | Winter | 11 | 0 | -27.5 | 24.18 | 69.4 | 0 | 0 | 120 | 120 | 27.5 | 69.96 | 33.41 | 50.04 | 0 | 0 | 0 | Normal
2025-07-02 12:00 | 183 | 7 | Winter | 12 | 0 | -20.3 | 13.64 | 56.6 | 0 | 0 | 120 | 120 | 20.3 | 61.29 | 55.02 | 58.71 | 0 | 0 | 0 | Normal
2025-07-02 13:00 | 183 | 7 | Winter | 13 | 0 | -23.9 | 10.36 | 49.9 | 0 | 0 | 45.18 | 45.18 | 23.9 | 60.59 | 48.86 | -15.41 | 0 | 0 | 0 | Battery-supported
2025-07-02 14:00 | 183 | 7 | Winter | 14 | 0 | -23.6 | 10.29 | 91.6 | 0 | 0 | 43.81 | 43.81 | 23.6 | 69.73 | 38.49 | -25.92 | 0 | 0 | 0 | Battery-supported
2025-07-02 15:00 | 183 | 7 | Winter | 15 | 0 | -26.2 | 15.64 | 30 | 0 | 0 | 120 | 120 | 26.2 | 65.03 | 58.72 | 54.97 | 0 | 0 | 0 | Normal
2025-07-02 16:00 | 183 | 7 | Winter | 16 | 0 | -23 | 19.33 | 77.6 | 0 | 0 | 120 | 120 | 23 | 67.93 | 77.88 | 52.07 | 0 | 0 | 0 | Normal
2025-07-02 17:00 | 183 | 7 | Winter | 17 | 0 | -25.5 | 4.89 | 20.2 | 0 | 0 | 0.38 | 0.38 | 25.5 | 64.98 | 52.04 | -64.6 | 0 | 0 | 0 | Battery-supported
2025-07-02 18:00 | 183 | 7 | Winter | 18 | 0 | -25.3 | 25.49 | 41.8 | 0 | 0 | 120 | 120 | 25.3 | 68.76 | 70.9 | 51.24 | 0 | 0 | 0 | Normal
2025-07-02 19:00 | 183 | 7 | Winter | 19 | 0 | -23.3 | 13.25 | 32.9 | 0 | 0 | 120 | 120 | 23.3 | 61.17 | 92.54 | 58.83 | 0 | 0 | 0 | Normal
2025-07-02 20:00 | 183 | 7 | Winter | 20 | 0 | -28.2 | 7.34 | 44.3 | 0 | 0 | 7.93 | 7.93 | 28.2 | 70.52 | 67.51 | -62.59 | 0 | 0 | 0 | Battery-supported
2025-07-02 21:00 | 183 | 7 | Winter | 21 | 0 | -21.1 | 9.52 | 59.4 | 0 | 0 | 30.54 | 30.54 | 21.1 | 55.79 | 57.41 | -25.25 | 0 | 0 | 0 | Battery-supported
2025-07-02 22:00 | 183 | 7 | Winter | 22 | 0 | -24.2 | 13.67 | 71.8 | 0 | 0 | 120 | 120 | 24.2 | 59.85 | 79.54 | 60.15 | 0 | 0 | 0 | Normal
2025-07-02 23:00 | 183 | 7 | Winter | 23 | 0 | -21.8 | 14.05 | 15.7 | 0 | 0 | 120 | 120 | 21.8 | 60.33 | 95 | 42 | 0 | 0 | 0 | Normal
2025-07-03 | 184 | 7 | Winter | 0 | 0 | -27 | 5.48 | 68 | 0 | 0 | 1.09 | 1.09 | 27 | 64.07 | 69.81 | -62.98 | 0 | 0 | 0 | Battery-supported
2025-07-03 01:00 | 184 | 7 | Winter | 1 | 0 | -26.7 | 10.06 | 30.7 | 0 | 0 | 39.51 | 39.51 | 26.7 | 67.95 | 58.43 | -28.44 | 0 | 0 | 0 | Battery-supported
2025-07-03 02:00 | 184 | 7 | Winter | 2 | 0 | -27.2 | 11.75 | 2.1 | 0 | 0 | 78.59 | 78.59 | 27.2 | 56.48 | 66.57 | 22.11 | 0 | 0 | 0 | Normal
2025-07-03 03:00 | 184 | 7 | Winter | 3 | 0 | -24.1 | 19.51 | 51.5 | 0 | 0 | 120 | 120 | 24.1 | 67.47 | 85.9 | 52.53 | 0 | 0 | 0 | Normal
2025-07-03 04:00 | 184 | 7 | Winter | 4 | 0 | -24.5 | 20.7 | 72.4 | 0 | 0 | 120 | 120 | 24.5 | 63.26 | 95 | 24.73 | 0 | 0 | 0 | Normal
2025-07-03 05:00 | 184 | 7 | Winter | 5 | 0 | -25.7 | 4.51 | 57.4 | 0 | 0 | 0.14 | 0.14 | 25.7 | 58.93 | 71.48 | -58.79 | 0 | 0 | 0 | Battery-supported
2025-07-03 06:00 | 184 | 7 | Winter | 6 | 0 | -26.9 | 10.68 | 100 | 0 | 0 | 51.81 | 51.81 | 26.9 | 65.86 | 65.86 | -14.05 | 0 | 0 | 0 | Battery-supported
2025-07-03 07:00 | 184 | 7 | Winter | 7 | 0 | -27.5 | 7.11 | 65.6 | 0 | 0 | 6.58 | 6.58 | 27.5 | 69.57 | 40.67 | -62.99 | 0 | 0 | 0 | Battery-supported
2025-07-03 08:00 | 184 | 7 | Winter | 8 | 0 | -24.8 | 13.49 | 36.9 | 0 | 0 | 120 | 120 | 24.8 | 72.25 | 58.24 | 47.75 | 0 | 0 | 0 | Normal
2025-07-03 09:00 | 184 | 7 | Winter | 9 | 0 | -25.7 | 32.87 | 35.9 | 0 | 0 | 0 | 0 | 25.7 | 64.75 | 32.34 | -64.75 | 0 | 0 | 0 | Battery-supported
2025-07-03 10:00 | 184 | 7 | Winter | 10 | 0 | -26.2 | 18.23 | 29 | 0 | 0 | 120 | 120 | 26.2 | 69.36 | 50.98 | 50.64 | 0 | 0 | 0 | Normal
2025-07-03 11:00 | 184 | 7 | Winter | 11 | 0 | -21.3 | 14.19 | 28.2 | 0 | 0 | 120 | 120 | 21.3 | 67.32 | 70.36 | 52.68 | 0 | 0 | 0 | Normal
2025-07-03 12:00 | 184 | 7 | Winter | 12 | 0 | -24.9 | 16.5 | 13.7 | 0 | 0 | 120 | 120 | 24.9 | 67.77 | 89.58 | 52.23 | 0 | 0 | 0 | Normal
2025-07-03 13:00 | 184 | 7 | Winter | 13 | 0 | -21.9 | 23.23 | 34.2 | 0 | 0 | 120 | 120 | 21.9 | 66.66 | 95 | 14.72 | 0 | 0 | 0 | Normal
2025-07-03 14:00 | 184 | 7 | Winter | 14 | 0 | -25.9 | 17.31 | 65.7 | 0 | 0 | 120 | 120 | 25.9 | 70.94 | 95 | 0 | 0 | 0 | 0 | Normal
2025-07-03 15:00 | 184 | 7 | Winter | 15 | 0 | -24.1 | 5.06 | 30.8 | 0 | 0 | 0.53 | 0.53 | 24.1 | 63.15 | 69.95 | -62.62 | 0 | 0 | 0 | Battery-supported
2025-07-03 16:00 | 184 | 7 | Winter | 16 | 0 | -24.8 | 26.59 | 3.6 | 0 | 0 | 120 | 120 | 24.8 | 72.83 | 87.31 | 47.17 | 0 | 0 | 0 | Normal
2025-07-03 17:00 | 184 | 7 | Winter | 17 | 0 | -28.4 | 11.32 | 79.1 | 0 | 0 | 66.93 | 66.93 | 28.4 | 71.77 | 85.37 | -4.84 | 0 | 0 | 0 | Battery-supported
2025-07-03 18:00 | 184 | 7 | Winter | 18 | 0 | -21.5 | 13.18 | 28.4 | 0 | 0 | 120 | 120 | 21.5 | 64.32 | 95 | 26.16 | 0 | 0 | 0 | Normal
2025-07-03 19:00 | 184 | 7 | Winter | 19 | 0 | -25 | 20.69 | 84.5 | 0 | 0 | 120 | 120 | 25 | 64.4 | 95 | 0 | 0 | 0 | 0 | Normal
2025-07-03 20:00 | 184 | 7 | Winter | 20 | 0 | -23 | 31.98 | 73 | 0 | 0 | 0 | 0 | 23 | 65.03 | 68.99 | -65.03 | 0 | 0 | 0 | Battery-supported
2025-07-03 21:00 | 184 | 7 | Winter | 21 | 0 | -26.3 | 8.14 | 32.7 | 0 | 0 | 13.98 | 13.98 | 26.3 | 65.05 | 48.56 | -51.07 | 0 | 0 | 0 | Battery-supported
2025-07-03 22:00 | 184 | 7 | Winter | 22 | 0 | -25 | 20.05 | 62.8 | 0 | 0 | 120 | 120 | 25 | 60.96 | 70.29 | 59.04 | 0 | 0 | 0 | Normal
2025-07-03 23:00 | 184 | 7 | Winter | 23 | 0 | -26.6 | 7.83 | 37.1 | 0 | 0 | 11.36 | 11.36 | 26.6 | 64.43 | 49.06 | -53.07 | 0 | 0 | 0 | Battery-supported
2025-07-04 | 185 | 7 | Winter | 0 | 0 | -22 | 12.56 | 20.9 | 0 | 0 | 104.09 | 104.09 | 22 | 56.86 | 66.44 | 47.23 | 0 | 0 | 0 | Normal
2025-07-04 01:00 | 185 | 7 | Winter | 1 | 0 | -24 | 3.98 | 39.8 | 0 | 0 | 0.02 | 0.02 | 24 | 59.35 | 42.71 | -59.33 | 0 | 0 | 0 | Battery-supported
2025-07-04 02:00 | 185 | 7 | Winter | 2 | 0 | -23.9 | 7.86 | 50.6 | 0 | 0 | 11.6 | 11.6 | 23.9 | 52.33 | 26.42 | -40.73 | 0 | 0 | 0 | Battery-supported
2025-07-04 03:00 | 185 | 7 | Winter | 3 | 0 | -21.7 | 12.2 | 56.3 | 0 | 0 | 92.17 | 92.17 | 21.7 | 58.27 | 38.89 | 33.9 | 0 | 0 | 0 | Normal
2025-07-04 04:00 | 185 | 7 | Winter | 4 | 0 | -22.2 | 14.64 | 40.3 | 0 | 0 | 120 | 120 | 22.2 | 56.42 | 62.29 | 63.58 | 0 | 0 | 0 | Normal
2025-07-04 05:00 | 185 | 7 | Winter | 5 | 0 | -23 | 14.17 | 56.6 | 0 | 0 | 120 | 120 | 23 | 59.27 | 84.64 | 60.73 | 0 | 0 | 0 | Normal
2025-07-04 06:00 | 185 | 7 | Winter | 6 | 0 | -27.9 | 18.63 | 0 | 0 | 0 | 120 | 120 | 27.9 | 54.3 | 95 | 28.16 | 0 | 0 | 0 | Normal
2025-07-04 07:00 | 185 | 7 | Winter | 7 | 0 | -26.3 | 8.59 | 41.4 | 0 | 0 | 18.46 | 18.46 | 26.3 | 71.43 | 73.81 | -52.97 | 0 | 0 | 0 | Battery-supported
2025-07-04 08:00 | 185 | 7 | Winter | 8 | 0 | -26.9 | 10.15 | 59 | 0 | 0 | 41.16 | 41.16 | 26.9 | 70.19 | 62.2 | -29.03 | 0 | 0 | 0 | Battery-supported
2025-07-04 09:00 | 185 | 7 | Winter | 9 | 0 | -23.1 | 10.45 | 45.7 | 0 | 0 | 46.99 | 46.99 | 23.1 | 67.95 | 53.82 | -20.96 | 0 | 0 | 0 | Battery-supported
2025-07-04 10:00 | 185 | 7 | Winter | 10 | 0 | -24.3 | 8.98 | 67 | 0 | 0 | 23.03 | 23.03 | 24.3 | 68.85 | 35.49 | -45.82 | 0 | 0 | 0 | Battery-supported
2025-07-04 11:00 | 185 | 7 | Winter | 11 | 0 | -27.8 | 6.12 | 87.7 | 0 | 0 | 2.52 | 2.52 | 27.8 | 69.54 | 15 | -51.22 | 15.8 | 5.647 | 0 | Diesel-backup
2025-07-04 12:00 | 185 | 7 | Winter | 12 | 0 | -25.1 | 11.37 | 96.7 | 0 | 0 | 68.22 | 68.22 | 25.1 | 69.79 | 15 | 0 | 1.57 | 0.59 | 0 | Diesel-backup
2025-07-04 13:00 | 185 | 7 | Winter | 13 | 0 | -28 | 16.94 | 38.3 | 0 | 0 | 120 | 120 | 28 | 75.75 | 31.28 | 44.25 | 0 | 0 | 0 | Normal
2025-07-04 14:00 | 185 | 7 | Winter | 14 | 0 | -24.8 | 13.03 | 79.4 | 0 | 0 | 120 | 120 | 24.8 | 68.51 | 50.23 | 51.49 | 0 | 0 | 0 | Normal
2025-07-04 15:00 | 185 | 7 | Winter | 15 | 0 | -28.4 | 8.31 | 60.1 | 0 | 0 | 15.58 | 15.58 | 28.4 | 74.83 | 26.53 | -59.25 | 0 | 0 | 0 | Battery-supported
2025-07-04 16:00 | 185 | 7 | Winter | 16 | 0 | -23.6 | 11.5 | 53.6 | 0 | 0 | 71.66 | 71.66 | 23.6 | 69.68 | 27.26 | 1.98 | 0 | 0 | 0 | Normal
2025-07-04 17:00 | 185 | 7 | Winter | 17 | 0 | -23.9 | 8 | 27.7 | 0 | 0 | 12.75 | 12.75 | 23.9 | 69.73 | 15 | -30.65 | 26.33 | 9.054 | 0 | Diesel-backup
2025-07-04 18:00 | 185 | 7 | Winter | 18 | 0 | -20.5 | 14.85 | 28.7 | 0 | 0 | 120 | 120 | 20.5 | 70.9 | 33.07 | 49.1 | 0 | 0 | 0 | Normal
2025-07-04 19:00 | 185 | 7 | Winter | 19 | 0 | -22.9 | 17.25 | 73.7 | 0 | 0 | 120 | 120 | 22.9 | 67.31 | 52.46 | 52.69 | 0 | 0 | 0 | Normal
2025-07-04 20:00 | 185 | 7 | Winter | 20 | 0 | -25.7 | 17.49 | 48.5 | 0 | 0 | 120 | 120 | 25.7 | 68.39 | 71.45 | 51.61 | 0 | 0 | 0 | Normal
2025-07-04 21:00 | 185 | 7 | Winter | 21 | 0 | -22.9 | 9.53 | 25 | 0 | 0 | 30.69 | 30.69 | 22.9 | 57.73 | 60.64 | -27.04 | 0 | 0 | 0 | Battery-supported
2025-07-04 22:00 | 185 | 7 | Winter | 22 | 0 | -27.8 | 8.11 | 40.8 | 0 | 0 | 13.71 | 13.71 | 27.8 | 64.43 | 40.35 | -50.72 | 0 | 0 | 0 | Battery-supported
2025-07-04 23:00 | 185 | 7 | Winter | 23 | 0 | -26.8 | 18.63 | 54.4 | 0 | 0 | 120 | 120 | 26.8 | 56.39 | 63.76 | 63.61 | 0 | 0 | 0 | Normal
2025-07-05 | 186 | 7 | Winter | 0 | 0 | -24 | 9.1 | 57.5 | 0 | 0 | 24.58 | 24.58 | 24 | 64.6 | 47.75 | -40.02 | 0 | 0 | 0 | Battery-supported
2025-07-05 01:00 | 186 | 7 | Winter | 1 | 0 | -29.5 | 11.4 | 40.8 | 0 | 0 | 69.01 | 69.01 | 29.5 | 63.52 | 49.77 | 5.49 | 0 | 0 | 0 | Normal
2025-07-05 02:00 | 186 | 7 | Winter | 2 | 0 | -24.8 | 12.96 | 91.6 | 0 | 0 | 118.49 | 118.49 | 24.8 | 59.43 | 71.5 | 59.06 | 0 | 0 | 0 | Normal
2025-07-05 03:00 | 186 | 7 | Winter | 3 | 0 | -27 | 10.85 | 43.2 | 0 | 0 | 55.57 | 55.57 | 27 | 56.79 | 71.01 | -1.22 | 0 | 0 | 0 | Battery-supported
2025-07-05 04:00 | 186 | 7 | Winter | 4 | 0 | -24.5 | 16.07 | 39.4 | 0 | 0 | 120 | 120 | 24.5 | 59.94 | 93.12 | 60.06 | 0 | 0 | 0 | Normal
2025-07-05 05:00 | 186 | 7 | Winter | 5 | 0 | -27.1 | 4.3 | 75.7 | 0 | 0 | 0.07 | 0.07 | 27.1 | 56.68 | 70.47 | -56.61 | 0 | 0 | 0 | Battery-supported
2025-07-05 06:00 | 186 | 7 | Winter | 6 | 0 | -23.8 | 14.09 | 7.4 | 0 | 0 | 120 | 120 | 23.8 | 52.07 | 95 | 66.65 | 0 | 0 | 0 | Normal
2025-07-05 07:00 | 186 | 7 | Winter | 7 | 0 | -24.7 | 6.67 | 35.6 | 0 | 0 | 4.46 | 4.46 | 24.7 | 56.78 | 74.07 | -52.32 | 0 | 0 | 0 | Battery-supported
2025-07-05 08:00 | 186 | 7 | Winter | 8 | 0 | -21.7 | 8.5 | 66.1 | 0 | 0 | 17.5 | 17.5 | 21.7 | 63.71 | 55.59 | -46.21 | 0 | 0 | 0 | Battery-supported
2025-07-05 09:00 | 186 | 7 | Winter | 9 | 0 | -24.8 | 12.04 | 71.3 | 0 | 0 | 87.17 | 87.17 | 24.8 | 64.37 | 63.98 | 22.8 | 0 | 0 | 0 | Normal
2025-07-05 10:00 | 186 | 7 | Winter | 10 | 0 | -26.5 | 3.58 | 25.4 | 0 | 0 | 0 | 0 | 26.5 | 70.64 | 35.72 | -70.64 | 0 | 0 | 0 | Battery-supported
2025-07-05 11:00 | 186 | 7 | Winter | 11 | 0 | -25.3 | 9.84 | 30.1 | 0 | 0 | 35.67 | 35.67 | 25.3 | 73.2 | 20.71 | -37.53 | 0 | 0 | 0 | Battery-supported
2025-07-05 12:00 | 186 | 7 | Winter | 12 | 0 | -27.7 | 8.87 | 19 | 0 | 0 | 21.67 | 21.67 | 27.7 | 71.57 | 15 | -14.28 | 35.62 | 11.827 | 0 | Diesel-backup
2025-07-05 13:00 | 186 | 7 | Winter | 13 | 0 | -23.9 | 10.16 | 82 | 0 | 0 | 41.35 | 41.35 | 23.9 | 58.03 | 15 | 0 | 16.68 | 5.942 | 0 | Diesel-backup
2025-07-05 14:00 | 186 | 7 | Winter | 14 | 0 | -23.5 | 8.58 | 24.8 | 0 | 0 | 18.35 | 18.35 | 23.5 | 66.43 | 15 | 0 | 48.08 | 15.386 | 0 | Diesel-backup
2025-07-05 15:00 | 186 | 7 | Winter | 15 | 0 | -19.3 | 11.44 | 61.3 | 0 | 0 | 70.06 | 70.06 | 19.3 | 64.62 | 17 | 5.44 | 0 | 0 | 0 | Normal
2025-07-05 16:00 | 186 | 7 | Winter | 16 | 0 | -26.1 | 7.83 | 77.8 | 0 | 0 | 11.36 | 11.36 | 26.1 | 67.62 | 15 | -5 | 51.26 | 16.402 | 0 | Diesel-backup
2025-07-05 17:00 | 186 | 7 | Winter | 17 | 0 | -25.4 | 10.61 | 60.2 | 0 | 0 | 50.31 | 50.31 | 25.4 | 69.66 | 15 | 0 | 19.35 | 6.827 | 0 | Diesel-backup
2025-07-05 18:00 | 186 | 7 | Winter | 18 | 0 | -26 | 12.03 | 84.9 | 0 | 0 | 86.87 | 86.87 | 26 | 70.06 | 21.19 | 16.81 | 0 | 0 | 0 | Normal
2025-07-05 19:00 | 186 | 7 | Winter | 19 | 0 | -24.3 | 19.02 | 51.3 | 0 | 0 | 120 | 120 | 24.3 | 62.9 | 42.2 | 57.1 | 0 | 0 | 0 | Normal
2025-07-05 20:00 | 186 | 7 | Winter | 20 | 0 | -23.9 | 21.33 | 86.2 | 0 | 0 | 120 | 120 | 23.9 | 71.72 | 59.97 | 48.28 | 0 | 0 | 0 | Normal
2025-07-05 21:00 | 186 | 7 | Winter | 21 | 0 | -24.9 | 4.55 | 64.7 | 0 | 0 | 0.16 | 0.16 | 24.9 | 58.74 | 36.53 | -58.58 | 0 | 0 | 0 | Battery-supported
2025-07-05 22:00 | 186 | 7 | Winter | 22 | 0 | -22.4 | 19.83 | 74.6 | 0 | 0 | 120 | 120 | 22.4 | 56.08 | 60.06 | 63.92 | 0 | 0 | 0 | Normal
2025-07-05 23:00 | 186 | 7 | Winter | 23 | 0 | -26.1 | 6.1 | 59 | 0 | 0 | 2.46 | 2.46 | 26.1 | 62.91 | 35.88 | -60.45 | 0 | 0 | 0 | Battery-supported
2025-07-06 | 187 | 7 | Winter | 0 | 0 | -22.6 | 10.67 | 67.9 | 0 | 0 | 51.59 | 51.59 | 22.6 | 51.18 | 36.03 | 0.41 | 0 | 0 | 0 | Normal
2025-07-06 01:00 | 187 | 7 | Winter | 1 | 0 | -23.6 | 3.75 | 47.2 | 0 | 0 | 0 | 0 | 23.6 | 63.66 | 15 | -52.57 | 11.09 | 4.031 | 0 | Diesel-backup
2025-07-06 02:00 | 187 | 7 | Winter | 2 | 0 | -24.8 | 2.55 | 83.7 | 0 | 0 | 0 | 0 | 24.8 | 55.87 | 15 | 0 | 55.87 | 17.878 | 0 | Diesel-backup
2025-07-06 03:00 | 187 | 7 | Winter | 3 | 0 | -25.5 | 31.86 | 42 | 0 | 0 | 0 | 0 | 25.5 | 67.74 | 15 | 0 | 67.74 | 21.677 | 0 | Diesel-backup
2025-07-06 04:00 | 187 | 7 | Winter | 4 | 0 | -19.5 | 10.84 | 14.8 | 0 | 0 | 55.35 | 55.35 | 19.5 | 59.01 | 15 | 0 | 3.66 | 1.365 | 0 | Diesel-backup
2025-07-06 05:00 | 187 | 7 | Winter | 5 | 0 | -26.6 | 9.48 | 86.3 | 0 | 0 | 29.93 | 29.93 | 26.6 | 57.56 | 15 | 0 | 27.63 | 9.456 | 0 | Diesel-backup
2025-07-06 06:00 | 187 | 7 | Winter | 6 | 0 | -24.1 | 12.84 | 59.8 | 0 | 0 | 114.04 | 114.04 | 24.1 | 60.43 | 34.73 | 53.61 | 0 | 0 | 0 | Normal
2025-07-06 07:00 | 187 | 7 | Winter | 7 | 0 | -26.5 | 9.62 | 39.9 | 0 | 0 | 32.08 | 32.08 | 26.5 | 57.68 | 24.49 | -25.6 | 0 | 0 | 0 | Battery-supported
2025-07-06 08:00 | 187 | 7 | Winter | 8 | 0 | -20.9 | 17.16 | 31.6 | 0 | 0 | 120 | 120 | 20.9 | 59.53 | 46.74 | 60.47 | 0 | 0 | 0 | Normal
2025-07-06 09:00 | 187 | 7 | Winter | 9 | 0 | -22.9 | 12.43 | 46.8 | 0 | 0 | 99.67 | 99.67 | 22.9 | 55.91 | 62.85 | 43.76 | 0 | 0 | 0 | Normal
2025-07-06 10:00 | 187 | 7 | Winter | 10 | 0 | -26.3 | 15.63 | 66.1 | 0 | 0 | 120 | 120 | 26.3 | 71.84 | 80.57 | 48.16 | 0 | 0 | 0 | Normal
2025-07-06 11:00 | 187 | 7 | Winter | 11 | 0 | -23.7 | 6.72 | 75.3 | 0 | 0 | 4.67 | 4.67 | 23.7 | 64.87 | 56.49 | -60.2 | 0 | 0 | 0 | Battery-supported
2025-07-06 12:00 | 187 | 7 | Winter | 12 | 0 | -24.2 | 4.13 | 83.9 | 0 | 0 | 0.03 | 0.03 | 24.2 | 70.34 | 28.36 | -70.31 | 0 | 0 | 0 | Battery-supported
2025-07-06 13:00 | 187 | 7 | Winter | 13 | 0 | -25.9 | 18.24 | 35.8 | 0 | 0 | 120 | 120 | 25.9 | 69.8 | 46.84 | 50.2 | 0 | 0 | 0 | Normal
2025-07-06 14:00 | 187 | 7 | Winter | 14 | 0 | -23.1 | 13.16 | 68.7 | 0 | 0 | 120 | 120 | 23.1 | 61.23 | 68.46 | 58.77 | 0 | 0 | 0 | Normal
2025-07-06 15:00 | 187 | 7 | Winter | 15 | 0 | -23.9 | 5.07 | 9.9 | 0 | 0 | 0.54 | 0.54 | 23.9 | 70.26 | 40.58 | -69.72 | 0 | 0 | 0 | Battery-supported
2025-07-06 16:00 | 187 | 7 | Winter | 16 | 0 | -24.3 | 5.13 | 45.6 | 0 | 0 | 0.61 | 0.61 | 24.3 | 69.38 | 15 | -63.94 | 4.83 | 1.793 | 0 | Diesel-backup
2025-07-06 17:00 | 187 | 7 | Winter | 17 | 0 | -24.9 | 11.59 | 53.4 | 0 | 0 | 74.11 | 74.11 | 24.9 | 65.98 | 17.99 | 8.13 | 0 | 0 | 0 | Normal
2025-07-06 18:00 | 187 | 7 | Winter | 18 | 0 | -23.9 | 14.95 | 29.3 | 0 | 0 | 120 | 120 | 23.9 | 70.8 | 36.1 | 49.2 | 0 | 0 | 0 | Normal
2025-07-06 19:00 | 187 | 7 | Winter | 19 | 0 | -24.3 | 6.07 | 100 | 0 | 0 | 2.38 | 2.38 | 24.3 | 66.22 | 15 | -52.74 | 11.1 | 4.032 | 0 | Diesel-backup
2025-07-06 20:00 | 187 | 7 | Winter | 20 | 0 | -24.7 | 23.89 | 20.9 | 0 | 0 | 120 | 120 | 24.7 | 64.56 | 35.4 | 55.44 | 0 | 0 | 0 | Normal
2025-07-06 21:00 | 187 | 7 | Winter | 21 | 0 | -26.2 | 16.05 | 38.3 | 0 | 0 | 120 | 120 | 26.2 | 60.44 | 57.32 | 59.56 | 0 | 0 | 0 | Normal
2025-07-06 22:00 | 187 | 7 | Winter | 22 | 0 | -21.1 | 18.96 | 62.1 | 0 | 0 | 120 | 120 | 21.1 | 54.62 | 81.38 | 65.38 | 0 | 0 | 0 | Normal
2025-07-06 23:00 | 187 | 7 | Winter | 23 | 0 | -27.1 | 11.42 | 64 | 0 | 0 | 69.53 | 69.53 | 27.1 | 56.16 | 86.3 | 13.37 | 0 | 0 | 0 | Normal
2025-07-07 | 188 | 7 | Winter | 0 | 0 | -23.9 | 10.88 | 6.5 | 0 | 0 | 56.26 | 56.26 | 23.9 | 48.35 | 89.21 | 7.91 | 0 | 0 | 0 | Normal
2025-07-07 01:00 | 188 | 7 | Winter | 1 | 0 | -25.5 | 4.78 | 48.7 | 0 | 0 | 0.29 | 0.29 | 25.5 | 67.09 | 62.49 | -66.8 | 0 | 0 | 0 | Battery-supported
2025-07-07 02:00 | 188 | 7 | Winter | 2 | 0 | -21 | 6.76 | 63.8 | 0 | 0 | 4.85 | 4.85 | 21 | 60.53 | 40.22 | -55.68 | 0 | 0 | 0 | Battery-supported
2025-07-07 03:00 | 188 | 7 | Winter | 3 | 0 | -26.8 | 10.1 | 67.5 | 0 | 0 | 40.24 | 40.24 | 26.8 | 67.71 | 29.23 | -27.47 | 0 | 0 | 0 | Battery-supported
2025-07-07 04:00 | 188 | 7 | Winter | 4 | 0 | -26.5 | 13.36 | 38.6 | 0 | 0 | 120 | 120 | 26.5 | 65.11 | 49.43 | 54.89 | 0 | 0 | 0 | Normal
2025-07-07 05:00 | 188 | 7 | Winter | 5 | 0 | -27 | 12.03 | 76.3 | 0 | 0 | 86.87 | 86.87 | 27 | 60.34 | 59.19 | 26.53 | 0 | 0 | 0 | Normal
2025-07-07 06:00 | 188 | 7 | Winter | 6 | 0 | -24.1 | 2.89 | 94.4 | 0 | 0 | 0 | 0 | 24.1 | 58.4 | 35.83 | -58.4 | 0 | 0 | 0 | Battery-supported
2025-07-07 07:00 | 188 | 7 | Winter | 7 | 0 | -27.9 | 5.86 | 64.6 | 0 | 0 | 1.84 | 1.84 | 27.9 | 60.44 | 15 | -52.08 | 6.52 | 2.406 | 0 | Diesel-backup
2025-07-07 08:00 | 188 | 7 | Winter | 8 | 0 | -25.9 | 12.48 | 39.1 | 0 | 0 | 101.35 | 101.35 | 25.9 | 71.06 | 26.15 | 30.29 | 0 | 0 | 0 | Normal
2025-07-07 09:00 | 188 | 7 | Winter | 9 | 0 | -29.6 | 13.55 | 99.7 | 0 | 0 | 120 | 120 | 29.6 | 74.49 | 42.89 | 45.51 | 0 | 0 | 0 | Normal
2025-07-07 10:00 | 188 | 7 | Winter | 10 | 0 | -24.3 | 8.5 | 22.7 | 0 | 0 | 17.5 | 17.5 | 24.3 | 65.93 | 23.52 | -48.43 | 0 | 0 | 0 | Battery-supported
2025-07-07 11:00 | 188 | 7 | Winter | 11 | 0 | -25.9 | 15.29 | 71.4 | 0 | 0 | 120 | 120 | 25.9 | 70.65 | 41.68 | 49.35 | 0 | 0 | 0 | Normal
2025-07-07 12:00 | 188 | 7 | Winter | 12 | 0 | -28.1 | 15.16 | 17.5 | 0 | 0 | 120 | 120 | 28.1 | 75.74 | 57.97 | 44.26 | 0 | 0 | 0 | Normal
2025-07-07 13:00 | 188 | 7 | Winter | 13 | 0 | -22.5 | 30.7 | 16.3 | 0 | 0 | 0 | 0 | 22.5 | 65.49 | 31.77 | -65.49 | 0 | 0 | 0 | Battery-supported
2025-07-07 14:00 | 188 | 7 | Winter | 14 | 0 | -27.7 | 10.92 | 40 | 0 | 0 | 57.18 | 57.18 | 27.7 | 66.05 | 28.23 | -8.87 | 0 | 0 | 0 | Battery-supported
2025-07-07 15:00 | 188 | 7 | Winter | 15 | 0 | -23.1 | 8.3 | 39.4 | 0 | 0 | 15.48 | 15.48 | 23.1 | 67.93 | 15 | -33.07 | 19.38 | 6.838 | 0 | Diesel-backup
2025-07-07 16:00 | 188 | 7 | Winter | 16 | 0 | -26.4 | 6.1 | 39.3 | 0 | 0 | 2.46 | 2.46 | 26.4 | 64.51 | 15 | 0 | 62.05 | 19.856 | 0 | Diesel-backup
2025-07-07 17:00 | 188 | 7 | Winter | 17 | 0 | -21.3 | 4.37 | 67.3 | 0 | 0 | 0.09 | 0.09 | 21.3 | 61.06 | 15 | 0 | 60.97 | 19.51 | 0 | Diesel-backup
2025-07-07 18:00 | 188 | 7 | Winter | 18 | 0 | -23.2 | 14.81 | 34.2 | 0 | 0 | 120 | 120 | 23.2 | 67.3 | 34.39 | 52.7 | 0 | 0 | 0 | Normal
2025-07-07 19:00 | 188 | 7 | Winter | 19 | 0 | -27.1 | 13.9 | 81.1 | 0 | 0 | 120 | 120 | 27.1 | 72.57 | 51.85 | 47.43 | 0 | 0 | 0 | Normal
2025-07-07 20:00 | 188 | 7 | Winter | 20 | 0 | -26.9 | 4.75 | 73.7 | 0 | 0 | 0.27 | 0.27 | 26.9 | 70.28 | 23.84 | -70.01 | 0 | 0 | 0 | Battery-supported
2025-07-07 21:00 | 188 | 7 | Winter | 21 | 0 | -23.5 | 14.86 | 8.8 | 0 | 0 | 120 | 120 | 23.5 | 54.45 | 47.97 | 65.55 | 0 | 0 | 0 | Normal
2025-07-07 22:00 | 188 | 7 | Winter | 22 | 0 | -25.4 | 11.79 | 22.7 | 0 | 0 | 79.74 | 79.74 | 25.4 | 71.54 | 50.98 | 8.2 | 0 | 0 | 0 | Normal
2025-07-07 23:00 | 188 | 7 | Winter | 23 | 0 | -25.2 | 9.05 | 53.8 | 0 | 0 | 23.93 | 23.93 | 25.2 | 58.11 | 37.31 | -34.18 | 0 | 0 | 0 | Battery-supported
2025-07-08 | 189 | 7 | Winter | 0 | 0 | -22.1 | 2.72 | 77.7 | 0 | 0 | 0 | 0 | 22.1 | 58.92 | 15 | -55.78 | 3.14 | 1.173 | 0 | Diesel-backup
2025-07-08 01:00 | 189 | 7 | Winter | 1 | 0 | -26.5 | 13.83 | 63.2 | 0 | 0 | 120 | 120 | 26.5 | 59.16 | 37.39 | 60.84 | 0 | 0 | 0 | Normal
2025-07-08 02:00 | 189 | 7 | Winter | 2 | 0 | -24.7 | 25.73 | 26.2 | 0 | 0 | 120 | 120 | 24.7 | 55.94 | 60.96 | 64.06 | 0 | 0 | 0 | Normal
2025-07-08 03:00 | 189 | 7 | Winter | 3 | 0 | -22.8 | 6.6 | 49.8 | 0 | 0 | 4.17 | 4.17 | 22.8 | 58.01 | 39.43 | -53.84 | 0 | 0 | 0 | Battery-supported
2025-07-08 04:00 | 189 | 7 | Winter | 4 | 0 | -23.1 | 11.8 | 33.2 | 0 | 0 | 80.03 | 80.03 | 23.1 | 56.33 | 48.15 | 23.7 | 0 | 0 | 0 | Normal
2025-07-08 05:00 | 189 | 7 | Winter | 5 | 0 | -25.2 | 14.45 | 95 | 0 | 0 | 120 | 120 | 25.2 | 60.58 | 70.02 | 59.42 | 0 | 0 | 0 | Normal
2025-07-08 06:00 | 189 | 7 | Winter | 6 | 0 | -25.5 | 1.86 | 30 | 0 | 0 | 0 | 0 | 25.5 | 57.88 | 46.86 | -57.88 | 0 | 0 | 0 | Battery-supported
2025-07-08 07:00 | 189 | 7 | Winter | 7 | 0 | -28.7 | 5.94 | 54.9 | 0 | 0 | 2.03 | 2.03 | 28.7 | 64.24 | 21.98 | -62.21 | 0 | 0 | 0 | Battery-supported
2025-07-08 08:00 | 189 | 7 | Winter | 8 | 0 | -27.2 | 3.92 | 36.4 | 0 | 0 | 0.01 | 0.01 | 27.2 | 67.2 | 15 | -17.45 | 49.74 | 15.917 | 0 | Diesel-backup
2025-07-08 09:00 | 189 | 7 | Winter | 9 | 0 | -24.2 | 25.64 | 29.2 | 0 | 0 | 120 | 120 | 24.2 | 71.51 | 32.84 | 48.49 | 0 | 0 | 0 | Normal
2025-07-08 10:00 | 189 | 7 | Winter | 10 | 0 | -25.2 | 1.78 | 44.7 | 0 | 0 | 0 | 0 | 25.2 | 69.39 | 15 | -44.61 | 24.78 | 8.571 | 0 | Diesel-backup
2025-07-08 11:00 | 189 | 7 | Winter | 11 | 0 | -24.7 | 9.03 | 51.1 | 0 | 0 | 23.67 | 23.67 | 24.7 | 67.2 | 15 | 0 | 43.53 | 14.012 | 0 | Diesel-backup
2025-07-08 12:00 | 189 | 7 | Winter | 12 | 0 | -22.6 | 12.58 | 33.2 | 0 | 0 | 104.78 | 104.78 | 22.6 | 65.53 | 29.44 | 39.25 | 0 | 0 | 0 | Normal
2025-07-08 13:00 | 189 | 7 | Winter | 13 | 0 | -27.5 | 6.57 | 29.1 | 0 | 0 | 4.05 | 4.05 | 27.5 | 68.99 | 15 | -36.11 | 28.83 | 9.822 | 0 | Diesel-backup
2025-07-08 14:00 | 189 | 7 | Winter | 14 | 0 | -25.4 | 2.09 | 23.8 | 0 | 0 | 0 | 0 | 25.4 | 68.88 | 15 | 0 | 68.88 | 22.042 | 0 | Diesel-backup
2025-07-08 15:00 | 189 | 7 | Winter | 15 | 0 | -24.5 | 9.26 | 56.7 | 0 | 0 | 26.75 | 26.75 | 24.5 | 73.49 | 15 | 0 | 46.74 | 14.957 | 0 | Diesel-backup
2025-07-08 16:00 | 189 | 7 | Winter | 16 | 0 | -26.4 | 6.5 | 57.7 | 0 | 0 | 3.78 | 3.78 | 26.4 | 67.11 | 15 | 0 | 63.33 | 20.266 | 0 | Diesel-backup
2025-07-08 17:00 | 189 | 7 | Winter | 17 | 0 | -21.7 | 13.38 | 20.5 | 0 | 0 | 120 | 120 | 21.7 | 65.34 | 35.11 | 54.66 | 0 | 0 | 0 | Normal
2025-07-08 18:00 | 189 | 7 | Winter | 18 | 0 | -22.9 | 16.2 | 56.4 | 0 | 0 | 120 | 120 | 22.9 | 62.83 | 56.15 | 57.17 | 0 | 0 | 0 | Normal
2025-07-08 19:00 | 189 | 7 | Winter | 19 | 0 | -24.2 | 4.78 | 55.7 | 0 | 0 | 0.29 | 0.29 | 24.2 | 57.27 | 33.36 | -56.98 | 0 | 0 | 0 | Battery-supported
2025-07-08 20:00 | 189 | 7 | Winter | 20 | 0 | -20.9 | 6.94 | 32.8 | 0 | 0 | 5.7 | 5.7 | 20.9 | 66.35 | 15 | -45.9 | 14.75 | 5.29 | 0 | Diesel-backup
2025-07-08 21:00 | 189 | 7 | Winter | 21 | 0 | -28.2 | 7.16 | 45.6 | 0 | 0 | 6.86 | 6.86 | 28.2 | 67.51 | 15 | 0 | 60.65 | 19.408 | 0 | Diesel-backup
2025-07-08 22:00 | 189 | 7 | Winter | 22 | 0 | -24.9 | 16.07 | 27.7 | 0 | 0 | 120 | 120 | 24.9 | 61.64 | 36.48 | 58.36 | 0 | 0 | 0 | Normal
2025-07-08 23:00 | 189 | 7 | Winter | 23 | 0 | -24.1 | 11.05 | 56.9 | 0 | 0 | 60.24 | 60.24 | 24.1 | 68.44 | 33.2 | -8.2 | 0 | 0 | 0 | Battery-supported
2025-07-09 | 190 | 7 | Winter | 0 | 0 | -26.9 | 4.91 | 16.8 | 0 | 0 | 0.39 | 0.39 | 26.9 | 60.46 | 15 | -45.49 | 14.58 | 5.233 | 0 | Diesel-backup
2025-07-09 01:00 | 190 | 7 | Winter | 1 | 0 | -24.2 | 18.97 | 80.1 | 0 | 0 | 120 | 120 | 24.2 | 55.62 | 38.69 | 64.38 | 0 | 0 | 0 | Normal
2025-07-09 02:00 | 190 | 7 | Winter | 2 | 0 | -27.3 | 6.56 | 26.9 | 0 | 0 | 4.01 | 4.01 | 27.3 | 67.04 | 15 | -59.23 | 3.8 | 1.417 | 0 | Diesel-backup
2025-07-09 03:00 | 190 | 7 | Winter | 3 | 0 | -23.4 | 7.7 | 32.7 | 0 | 0 | 10.37 | 10.37 | 23.4 | 63.38 | 15 | 0 | 53.01 | 16.963 | 0 | Diesel-backup
2025-07-09 04:00 | 190 | 7 | Winter | 4 | 0 | -22.6 | 5.7 | 50.7 | 0 | 0 | 1.49 | 1.49 | 22.6 | 61.99 | 15 | 0 | 60.5 | 19.36 | 0 | Diesel-backup
2025-07-09 05:00 | 190 | 7 | Winter | 5 | 0 | -24.3 | 11.55 | 40.8 | 0 | 0 | 73.01 | 73.01 | 24.3 | 54.98 | 21.64 | 18.03 | 0 | 0 | 0 | Normal
2025-07-09 06:00 | 190 | 7 | Winter | 6 | 0 | -29 | 8.5 | 31.7 | 0 | 0 | 17.5 | 17.5 | 29 | 61.2 | 15 | -16.59 | 27.11 | 9.297 | 0 | Diesel-backup
2025-07-09 07:00 | 190 | 7 | Winter | 7 | 0 | -27 | 22.11 | 61.7 | 0 | 0 | 120 | 120 | 27 | 55.43 | 38.76 | 64.57 | 0 | 0 | 0 | Normal
2025-07-09 08:00 | 190 | 7 | Winter | 8 | 0 | -23.7 | 11.14 | 20.6 | 0 | 0 | 62.42 | 62.42 | 23.7 | 74.59 | 33.89 | -12.17 | 0 | 0 | 0 | Battery-supported
2025-07-09 09:00 | 190 | 7 | Winter | 9 | 0 | -24.9 | 5.93 | 46.1 | 0 | 0 | 2.01 | 2.01 | 24.9 | 64.22 | 15 | -47.23 | 14.98 | 5.368 | 0 | Diesel-backup
2025-07-09 10:00 | 190 | 7 | Winter | 10 | 0 | -30.8 | 10.44 | 47.2 | 0 | 0 | 46.78 | 46.78 | 30.8 | 68.97 | 15 | 0 | 22.19 | 7.749 | 0 | Diesel-backup
2025-07-09 11:00 | 190 | 7 | Winter | 11 | 0 | -22.2 | 23.86 | 54.1 | 0 | 0 | 120 | 120 | 22.2 | 64.78 | 35.32 | 55.22 | 0 | 0 | 0 | Normal
2025-07-09 12:00 | 190 | 7 | Winter | 12 | 0 | -24.6 | 4.53 | 54 | 0 | 0 | 0.15 | 0.15 | 24.6 | 68.07 | 15 | -50.8 | 17.12 | 6.089 | 0 | Diesel-backup
2025-07-09 13:00 | 190 | 7 | Winter | 13 | 0 | -26.7 | 13.83 | 23 | 0 | 0 | 120 | 120 | 26.7 | 72.36 | 32.53 | 47.64 | 0 | 0 | 0 | Normal
2025-07-09 14:00 | 190 | 7 | Winter | 14 | 0 | -22.7 | 2.75 | 24.9 | 0 | 0 | 0 | 0 | 22.7 | 65.18 | 15 | -43.83 | 21.35 | 7.479 | 0 | Diesel-backup
2025-07-09 15:00 | 190 | 7 | Winter | 15 | 0 | -26.4 | 21.25 | 43.9 | 0 | 0 | 120 | 120 | 26.4 | 66.68 | 34.62 | 53.32 | 0 | 0 | 0 | Normal
2025-07-09 16:00 | 190 | 7 | Winter | 16 | 0 | -26.4 | 7.83 | 43.3 | 0 | 0 | 11.36 | 11.36 | 26.4 | 67.82 | 15 | -49.05 | 7.41 | 2.726 | 0 | Diesel-backup
2025-07-09 17:00 | 190 | 7 | Winter | 17 | 0 | -24.1 | 5.82 | 75.7 | 0 | 0 | 1.75 | 1.75 | 24.1 | 64.69 | 15 | 0 | 62.94 | 20.141 | 0 | Diesel-backup
2025-07-09 18:00 | 190 | 7 | Winter | 18 | 0 | -21 | 23.05 | 53.2 | 0 | 0 | 120 | 120 | 21 | 69.57 | 33.56 | 50.43 | 0 | 0 | 0 | Normal
2025-07-09 19:00 | 190 | 7 | Winter | 19 | 0 | -21.3 | 10.03 | 46.6 | 0 | 0 | 38.97 | 38.97 | 21.3 | 64.27 | 23.44 | -25.3 | 0 | 0 | 0 | Battery-supported
2025-07-09 20:00 | 190 | 7 | Winter | 20 | 0 | -24.1 | 10.26 | 65.3 | 0 | 0 | 43.24 | 43.24 | 24.1 | 69.64 | 15 | -21.1 | 5.3 | 1.967 | 0 | Diesel-backup
2025-07-09 21:00 | 190 | 7 | Winter | 21 | 0 | -23.9 | 7.9 | 96.8 | 0 | 0 | 11.92 | 11.92 | 23.9 | 58.06 | 15 | 0 | 46.14 | 14.765 | 0 | Diesel-backup
2025-07-09 22:00 | 190 | 7 | Winter | 22 | 0 | -23.2 | 8.12 | 45.6 | 0 | 0 | 13.8 | 13.8 | 23.2 | 50.89 | 15 | 0 | 37.09 | 12.244 | 0 | Diesel-backup
2025-07-09 23:00 | 190 | 7 | Winter | 23 | 0 | -27.7 | 2.53 | 22.8 | 0 | 0 | 0 | 0 | 27.7 | 69.27 | 15 | 0 | 69.27 | 22.166 | 0 | Diesel-backup
2025-07-10 | 191 | 7 | Winter | 0 | 0 | -23.5 | 13.71 | 88.4 | 0 | 0 | 120 | 120 | 23.5 | 60.82 | 36.78 | 59.18 | 0 | 0 | 0 | Normal
2025-07-10 01:00 | 191 | 7 | Winter | 1 | 0 | -26.5 | 3.94 | 27.1 | 0 | 0 | 0.01 | 0.01 | 26.5 | 63.05 | 15 | -54.45 | 8.59 | 3.151 | 0 | Diesel-backup
2025-07-10 02:00 | 191 | 7 | Winter | 2 | 0 | -24.2 | 17.53 | 4.3 | 0 | 0 | 120 | 120 | 24.2 | 50.72 | 40.5 | 69.28 | 0 | 0 | 0 | Normal
2025-07-10 03:00 | 191 | 7 | Winter | 3 | 0 | -25.4 | 5.12 | 73.9 | 0 | 0 | 0.6 | 0.6 | 25.4 | 59.84 | 16.8 | -59.24 | 0 | 0 | 0 | Battery-supported
2025-07-10 04:00 | 191 | 7 | Winter | 4 | 0 | -23.8 | 10.83 | 52.2 | 0 | 0 | 55.12 | 55.12 | 23.8 | 64.97 | 15 | -4.5 | 5.35 | 1.984 | 0 | Diesel-backup
2025-07-10 05:00 | 191 | 7 | Winter | 5 | 0 | -24.7 | 7.1 | 60.9 | 0 | 0 | 6.53 | 6.53 | 24.7 | 64.88 | 15 | 0 | 58.35 | 18.672 | 0 | Diesel-backup
2025-07-10 06:00 | 191 | 7 | Winter | 6 | 0 | -31.7 | 7.9 | 41.1 | 0 | 0 | 11.92 | 11.92 | 31.7 | 65.83 | 15 | 0 | 53.91 | 17.251 | 0 | Diesel-backup
2025-07-10 07:00 | 191 | 7 | Winter | 7 | 0 | -24.5 | 8.87 | 34 | 0 | 0 | 21.67 | 21.67 | 24.5 | 64.38 | 15 | 0 | 42.71 | 13.792 | 0 | Diesel-backup
2025-07-10 08:00 | 191 | 7 | Winter | 8 | 0 | -23.5 | 12.5 | 46.4 | 0 | 0 | 102.03 | 102.03 | 23.5 | 72.78 | 25.76 | 29.25 | 0 | 0 | 0 | Normal
2025-07-10 09:00 | 191 | 7 | Winter | 9 | 0 | -23.9 | 22.69 | 52.3 | 0 | 0 | 120 | 120 | 23.9 | 66.28 | 45.53 | 53.72 | 0 | 0 | 0 | Normal
2025-07-10 10:00 | 191 | 7 | Winter | 10 | 0 | -25.2 | 7.78 | 51.2 | 0 | 0 | 10.97 | 10.97 | 25.2 | 73.47 | 20.53 | -62.5 | 0 | 0 | 0 | Battery-supported
2025-07-10 11:00 | 191 | 7 | Winter | 11 | 0 | -21.3 | 2.19 | 27.2 | 0 | 0 | 0 | 0 | 21.3 | 69.39 | 15 | -13.83 | 55.56 | 17.778 | 0 | Diesel-backup
2025-07-10 12:00 | 191 | 7 | Winter | 12 | 0 | -24.2 | 19.98 | 88.8 | 0 | 0 | 120 | 120 | 24.2 | 70.56 | 33.19 | 49.44 | 0 | 0 | 0 | Normal
2025-07-10 13:00 | 191 | 7 | Winter | 13 | 0 | -24 | 14.92 | 27.9 | 0 | 0 | 120 | 120 | 24 | 70.74 | 51.32 | 49.26 | 0 | 0 | 0 | Normal
2025-07-10 14:00 | 191 | 7 | Winter | 14 | 0 | -22.6 | 4.99 | 54 | 0 | 0 | 0.46 | 0.46 | 22.6 | 62.11 | 26.66 | -61.65 | 0 | 0 | 0 | Battery-supported
2025-07-10 15:00 | 191 | 7 | Winter | 15 | 0 | -24.1 | 4.4 | 44.1 | 0 | 0 | 0.1 | 0.1 | 24.1 | 70.24 | 15 | -29.15 | 40.99 | 13.326 | 0 | Diesel-backup
2025-07-10 16:00 | 191 | 7 | Winter | 16 | 0 | -26.9 | 12.83 | 25.9 | 0 | 0 | 113.67 | 113.67 | 26.9 | 69.4 | 31.29 | 44.27 | 0 | 0 | 0 | Normal
2025-07-10 17:00 | 191 | 7 | Winter | 17 | 0 | -30.3 | 11.56 | 38.5 | 0 | 0 | 73.29 | 73.29 | 30.3 | 69.68 | 32.62 | 3.61 | 0 | 0 | 0 | Normal
2025-07-10 18:00 | 191 | 7 | Winter | 18 | 0 | -26 | 25.85 | 28.5 | 0 | 0 | 120 | 120 | 26 | 75.08 | 49.15 | 44.92 | 0 | 0 | 0 | Normal
2025-07-10 19:00 | 191 | 7 | Winter | 19 | 0 | -23.3 | 13.79 | 55.9 | 0 | 0 | 120 | 120 | 23.3 | 65.83 | 69.08 | 54.17 | 0 | 0 | 0 | Normal
2025-07-10 20:00 | 191 | 7 | Winter | 20 | 0 | -25.7 | 6.81 | 23 | 0 | 0 | 5.08 | 5.08 | 25.7 | 69.64 | 43.26 | -64.56 | 0 | 0 | 0 | Battery-supported
2025-07-10 21:00 | 191 | 7 | Winter | 21 | 0 | -23.2 | 5.84 | 22.5 | 0 | 0 | 1.79 | 1.79 | 23.2 | 58.76 | 20.47 | -56.97 | 0 | 0 | 0 | Battery-supported
2025-07-10 22:00 | 191 | 7 | Winter | 22 | 0 | -24.6 | 10.62 | 50.8 | 0 | 0 | 50.52 | 50.52 | 24.6 | 53.37 | 19.33 | -2.85 | 0 | 0 | 0 | Battery-supported
2025-07-10 23:00 | 191 | 7 | Winter | 23 | 0 | -22.1 | 2.63 | 82.4 | 0 | 0 | 0 | 0 | 22.1 | 55.92 | 15 | -10.83 | 45.09 | 14.428 | 0 | Diesel-backup
2025-07-11 | 192 | 7 | Winter | 0 | 0 | -25.6 | 3.41 | 27.7 | 0 | 0 | 0 | 0 | 25.6 | 63.69 | 15 | 0 | 63.69 | 20.381 | 0 | Diesel-backup
2025-07-11 01:00 | 192 | 7 | Winter | 1 | 0 | -23.9 | 4.58 | 56.4 | 0 | 0 | 0.18 | 0.18 | 23.9 | 58.96 | 15 | 0 | 58.78 | 18.81 | 0 | Diesel-backup
2025-07-11 02:00 | 192 | 7 | Winter | 2 | 0 | -23.8 | 6.7 | 56.5 | 0 | 0 | 4.59 | 4.59 | 23.8 | 57.39 | 15 | 0 | 52.8 | 16.896 | 0 | Diesel-backup
2025-07-11 03:00 | 192 | 7 | Winter | 3 | 0 | -21.6 | 9.94 | 47.1 | 0 | 0 | 37.38 | 37.38 | 21.6 | 57.93 | 15 | 0 | 20.55 | 7.219 | 0 | Diesel-backup
2025-07-11 04:00 | 192 | 7 | Winter | 4 | 0 | -28.7 | 14.32 | 56.6 | 0 | 0 | 120 | 120 | 28.7 | 68 | 34.14 | 52 | 0 | 0 | 0 | Normal
2025-07-11 05:00 | 192 | 7 | Winter | 5 | 0 | -26 | 20.66 | 63.9 | 0 | 0 | 120 | 120 | 26 | 54.46 | 58.25 | 65.54 | 0 | 0 | 0 | Normal
2025-07-11 06:00 | 192 | 7 | Winter | 6 | 0 | -23.1 | 18.46 | 34.8 | 0 | 0 | 120 | 120 | 23.1 | 57.68 | 81.19 | 62.32 | 0 | 0 | 0 | Normal
2025-07-11 07:00 | 192 | 7 | Winter | 7 | 0 | -21.5 | 16.85 | 25 | 0 | 0 | 120 | 120 | 21.5 | 56.58 | 95 | 37.53 | 0 | 0 | 0 | Normal
2025-07-11 08:00 | 192 | 7 | Winter | 8 | 0 | -24.4 | 7.72 | 75.5 | 0 | 0 | 10.52 | 10.52 | 24.4 | 74.48 | 69.42 | -63.96 | 0 | 0 | 0 | Battery-supported
2025-07-11 09:00 | 192 | 7 | Winter | 9 | 0 | -25.6 | 5.95 | 40 | 0 | 0 | 2.06 | 2.06 | 25.6 | 73.43 | 40.87 | -71.37 | 0 | 0 | 0 | Battery-supported
2025-07-11 10:00 | 192 | 7 | Winter | 10 | 0 | -23.3 | 12.68 | 44.8 | 0 | 0 | 108.28 | 108.28 | 23.3 | 60.78 | 58.35 | 47.5 | 0 | 0 | 0 | Normal
2025-07-11 11:00 | 192 | 7 | Winter | 11 | 0 | -23 | 13.16 | 90 | 0 | 0 | 120 | 120 | 23 | 71.36 | 76.25 | 48.64 | 0 | 0 | 0 | Normal
2025-07-11 12:00 | 192 | 7 | Winter | 12 | 0 | -25.7 | 4.92 | 85.1 | 0 | 0 | 0.4 | 0.4 | 25.7 | 68.1 | 49.17 | -67.7 | 0 | 0 | 0 | Battery-supported
2025-07-11 13:00 | 192 | 7 | Winter | 13 | 0 | -24.2 | 8.85 | 13.6 | 0 | 0 | 21.43 | 21.43 | 24.2 | 60.76 | 33.44 | -39.33 | 0 | 0 | 0 | Battery-supported
2025-07-11 14:00 | 192 | 7 | Winter | 14 | 0 | -22.3 | 5.64 | 13.2 | 0 | 0 | 1.37 | 1.37 | 22.3 | 59.93 | 15 | -46.09 | 12.47 | 4.51 | 0 | Diesel-backup
2025-07-11 15:00 | 192 | 7 | Winter | 15 | 0 | -20.8 | 3.31 | 58.3 | 0 | 0 | 0 | 0 | 20.8 | 69.26 | 15 | 0 | 69.26 | 22.163 | 0 | Diesel-backup
2025-07-11 16:00 | 192 | 7 | Winter | 16 | 0 | -23.3 | 12.13 | 61.7 | 0 | 0 | 89.96 | 89.96 | 23.3 | 68.12 | 23.04 | 21.84 | 0 | 0 | 0 | Normal
2025-07-11 17:00 | 192 | 7 | Winter | 17 | 0 | -24.8 | 16.67 | 86.4 | 0 | 0 | 120 | 120 | 24.8 | 63.87 | 43.69 | 56.13 | 0 | 0 | 0 | Normal
2025-07-11 18:00 | 192 | 7 | Winter | 18 | 0 | -25.1 | 24.53 | 52.5 | 0 | 0 | 120 | 120 | 25.1 | 74.43 | 60.46 | 45.57 | 0 | 0 | 0 | Normal
2025-07-11 19:00 | 192 | 7 | Winter | 19 | 0 | -23.7 | 9.27 | 60.4 | 0 | 0 | 26.89 | 26.89 | 23.7 | 69.54 | 43.4 | -42.65 | 0 | 0 | 0 | Battery-supported
2025-07-11 20:00 | 192 | 7 | Winter | 20 | 0 | -25.2 | 2.85 | 15.1 | 0 | 0 | 0 | 0 | 25.2 | 67.18 | 16.53 | -67.18 | 0 | 0 | 0 | Battery-supported
2025-07-11 21:00 | 192 | 7 | Winter | 21 | 0 | -24.5 | 26.97 | 23.6 | 0 | 0 | 120 | 120 | 24.5 | 60.7 | 38.35 | 59.3 | 0 | 0 | 0 | Normal
2025-07-11 22:00 | 192 | 7 | Winter | 22 | 0 | -27.3 | 28.32 | 84.9 | 0 | 0 | 0 | 0 | 27.3 | 58.79 | 15 | -58.38 | 0.41 | 0.154 | 0 | Diesel-backup
2025-07-11 23:00 | 192 | 7 | Winter | 23 | 0 | -22.1 | 42.74 | 46.6 | 0 | 0 | 0 | 0 | 22.1 | 65.1 | 15 | 0 | 65.1 | 20.832 | 0 | Diesel-backup
2025-07-12 | 193 | 7 | Winter | 0 | 0 | -27.5 | 33.21 | 48.6 | 0 | 0 | 0 | 0 | 27.5 | 57.75 | 15 | 0 | 57.75 | 18.48 | 0 | Diesel-backup
2025-07-12 01:00 | 193 | 7 | Winter | 1 | 0 | -25.9 | 11.71 | 79.1 | 0 | 0 | 77.45 | 77.45 | 25.9 | 55.75 | 22.99 | 21.7 | 0 | 0 | 0 | Normal
2025-07-12 02:00 | 193 | 7 | Winter | 2 | 0 | -24.7 | 10.22 | 67.3 | 0 | 0 | 42.47 | 42.47 | 24.7 | 60.48 | 15.78 | -18.01 | 0 | 0 | 0 | Battery-supported
2025-07-12 03:00 | 193 | 7 | Winter | 3 | 0 | -20.6 | 15.68 | 39 | 0 | 0 | 120 | 120 | 20.6 | 67.12 | 35.24 | 52.88 | 0 | 0 | 0 | Normal
2025-07-12 04:00 | 193 | 7 | Winter | 4 | 0 | -25.9 | 3.79 | 44.1 | 0 | 0 | 0 | 0 | 25.9 | 55.28 | 15 | -50.6 | 4.68 | 1.738 | 0 | Diesel-backup
2025-07-12 05:00 | 193 | 7 | Winter | 5 | 0 | -26.4 | 6.47 | 58.9 | 0 | 0 | 3.67 | 3.67 | 26.4 | 64.66 | 15 | 0 | 60.99 | 19.517 | 0 | Diesel-backup
2025-07-12 06:00 | 193 | 7 | Winter | 6 | 0 | -26.2 | 9.35 | 59.7 | 0 | 0 | 28.02 | 28.02 | 26.2 | 61.48 | 15 | 0 | 33.46 | 11.201 | 0 | Diesel-backup
2025-07-12 07:00 | 193 | 7 | Winter | 7 | 0 | -21.3 | 18.85 | 49.7 | 0 | 0 | 120 | 120 | 21.3 | 57.9 | 37.85 | 62.1 | 0 | 0 | 0 | Normal
2025-07-12 08:00 | 193 | 7 | Winter | 8 | 0 | -31.2 | 19.33 | 71.5 | 0 | 0 | 120 | 120 | 31.2 | 78.77 | 53.03 | 41.23 | 0 | 0 | 0 | Normal
2025-07-12 09:00 | 193 | 7 | Winter | 9 | 0 | -27.2 | 9.67 | 32.5 | 0 | 0 | 32.88 | 32.88 | 27.2 | 67.46 | 39.19 | -34.58 | 0 | 0 | 0 | Battery-supported
2025-07-12 10:00 | 193 | 7 | Winter | 10 | 0 | -19 | 4.08 | 51.3 | 0 | 0 | 0.03 | 0.03 | 19 | 60.97 | 15 | -60.48 | 0.46 | 0.172 | 0 | Diesel-backup
2025-07-12 11:00 | 193 | 7 | Winter | 11 | 0 | -23.7 | 16.5 | 37.9 | 0 | 0 | 120 | 120 | 23.7 | 63.94 | 35.63 | 56.06 | 0 | 0 | 0 | Normal
2025-07-12 12:00 | 193 | 7 | Winter | 12 | 0 | -27.4 | 3.88 | 23.6 | 0 | 0 | 0.01 | 0.01 | 27.4 | 76.01 | 15 | -51.58 | 24.42 | 8.459 | 0 | Diesel-backup
2025-07-12 13:00 | 193 | 7 | Winter | 13 | 0 | -25.1 | 7.21 | 68.7 | 0 | 0 | 7.15 | 7.15 | 25.1 | 73.19 | 15 | 0 | 66.04 | 21.133 | 0 | Diesel-backup
2025-07-12 14:00 | 193 | 7 | Winter | 14 | 0 | -24.8 | 11.66 | 44.1 | 0 | 0 | 76.05 | 76.05 | 24.8 | 63.3 | 19.69 | 12.75 | 0 | 0 | 0 | Normal
2025-07-12 15:00 | 193 | 7 | Winter | 15 | 0 | -23.1 | 3.56 | 74 | 0 | 0 | 0 | 0 | 23.1 | 67.62 | 15 | -11.73 | 55.89 | 17.885 | 0 | Diesel-backup
2025-07-12 16:00 | 193 | 7 | Winter | 16 | 0 | -20.9 | 6.2 | 7.2 | 0 | 0 | 2.75 | 2.75 | 20.9 | 68.09 | 15 | 0 | 65.34 | 20.909 | 0 | Diesel-backup
2025-07-12 17:00 | 193 | 7 | Winter | 17 | 0 | -24.1 | 17.95 | 41.2 | 0 | 0 | 120 | 120 | 24.1 | 60.74 | 36.81 | 59.26 | 0 | 0 | 0 | Normal
2025-07-12 18:00 | 193 | 7 | Winter | 18 | 0 | -26.2 | 15.69 | 59.5 | 0 | 0 | 120 | 120 | 26.2 | 74.75 | 53.46 | 45.25 | 0 | 0 | 0 | Normal
2025-07-12 19:00 | 193 | 7 | Winter | 19 | 0 | -23.2 | 4.47 | 40 | 0 | 0 | 0.13 | 0.13 | 23.2 | 65.94 | 27.14 | -65.81 | 0 | 0 | 0 | Battery-supported
2025-07-12 20:00 | 193 | 7 | Winter | 20 | 0 | -26.5 | 12.5 | 58.8 | 0 | 0 | 102.03 | 102.03 | 26.5 | 67.69 | 39.77 | 34.34 | 0 | 0 | 0 | Normal
2025-07-12 21:00 | 193 | 7 | Winter | 21 | 0 | -27.2 | 2.82 | 53.7 | 0 | 0 | 0 | 0 | 27.2 | 67.79 | 15 | -61.93 | 5.86 | 2.168 | 0 | Diesel-backup
2025-07-12 22:00 | 193 | 7 | Winter | 22 | 0 | -28.8 | 14.74 | 32.3 | 0 | 0 | 120 | 120 | 28.8 | 68.32 | 34.02 | 51.68 | 0 | 0 | 0 | Normal
2025-07-12 23:00 | 193 | 7 | Winter | 23 | 0 | -28.4 | 6.58 | 52.3 | 0 | 0 | 4.09 | 4.09 | 28.4 | 57.93 | 15 | -47.55 | 6.29 | 2.326 | 0 | Diesel-backup
2025-07-13 | 194 | 7 | Winter | 0 | 0 | -27 | 8.97 | 67.1 | 0 | 0 | 22.91 | 22.91 | 27 | 64.88 | 15 | 0 | 41.97 | 13.593 | 0 | Diesel-backup
2025-07-13 01:00 | 194 | 7 | Winter | 1 | 0 | -27.6 | 10.84 | 79 | 0 | 0 | 55.35 | 55.35 | 27.6 | 65.32 | 15 | 0 | 9.97 | 3.637 | 0 | Diesel-backup
2025-07-13 02:00 | 194 | 7 | Winter | 2 | 0 | -24.3 | 4.67 | 64.2 | 0 | 0 | 0.22 | 0.22 | 24.3 | 50.58 | 15 | 0 | 50.36 | 16.115 | 0 | Diesel-backup
2025-07-13 03:00 | 194 | 7 | Winter | 3 | 0 | -27.6 | 6.24 | 36.6 | 0 | 0 | 2.88 | 2.88 | 27.6 | 64.84 | 15 | 0 | 61.96 | 19.827 | 0 | Diesel-backup
2025-07-13 04:00 | 194 | 7 | Winter | 4 | 0 | -31.9 | 25.07 | 53.5 | 0 | 0 | 120 | 120 | 31.9 | 65.25 | 35.15 | 54.75 | 0 | 0 | 0 | Normal
2025-07-13 05:00 | 194 | 7 | Winter | 5 | 0 | -27.3 | 8.57 | 81.5 | 0 | 0 | 18.24 | 18.24 | 27.3 | 66.82 | 15.72 | -48.58 | 0 | 0 | 0 | Battery-supported
2025-07-13 06:00 | 194 | 7 | Winter | 6 | 0 | -26 | 11.21 | 45.1 | 0 | 0 | 64.15 | 64.15 | 26 | 57.58 | 18.13 | 6.57 | 0 | 0 | 0 | Normal
2025-07-13 07:00 | 194 | 7 | Winter | 7 | 0 | -26.3 | 11.32 | 70.1 | 0 | 0 | 66.93 | 66.93 | 26.3 | 61.79 | 20.03 | 5.14 | 0 | 0 | 0 | Normal
2025-07-13 08:00 | 194 | 7 | Winter | 8 | 0 | -21.6 | 20.99 | 48.1 | 0 | 0 | 120 | 120 | 21.6 | 62.46 | 41.2 | 57.54 | 0 | 0 | 0 | Normal
2025-07-13 09:00 | 194 | 7 | Winter | 9 | 0 | -26.3 | 16.25 | 48.4 | 0 | 0 | 120 | 120 | 26.3 | 66.76 | 60.79 | 53.24 | 0 | 0 | 0 | Normal
2025-07-13 10:00 | 194 | 7 | Winter | 10 | 0 | -23 | 4.85 | 52.3 | 0 | 0 | 0.34 | 0.34 | 23 | 57.25 | 38.03 | -56.91 | 0 | 0 | 0 | Battery-supported
2025-07-13 11:00 | 194 | 7 | Winter | 11 | 0 | -25 | 22.5 | 27 | 0 | 0 | 120 | 120 | 25 | 72.26 | 55.6 | 47.74 | 0 | 0 | 0 | Normal
2025-07-13 12:00 | 194 | 7 | Winter | 12 | 0 | -25.1 | 27.23 | 87.8 | 0 | 0 | 120 | 120 | 25.1 | 72.74 | 72.99 | 47.26 | 0 | 0 | 0 | Normal
2025-07-13 13:00 | 194 | 7 | Winter | 13 | 0 | -26.8 | 4.83 | 72.9 | 0 | 0 | 0.33 | 0.33 | 26.8 | 70.09 | 45.08 | -69.76 | 0 | 0 | 0 | Battery-supported
2025-07-13 14:00 | 194 | 7 | Winter | 14 | 0 | -25.1 | 8.23 | 60.2 | 0 | 0 | 14.81 | 14.81 | 25.1 | 69.58 | 23.18 | -54.77 | 0 | 0 | 0 | Battery-supported
2025-07-13 15:00 | 194 | 7 | Winter | 15 | 0 | -26.7 | 9.53 | 43.1 | 0 | 0 | 30.69 | 30.69 | 26.7 | 66.77 | 15 | -20.44 | 15.64 | 5.592 | 0 | Diesel-backup
2025-07-13 16:00 | 194 | 7 | Winter | 16 | 0 | -24.6 | 8.43 | 79.6 | 0 | 0 | 16.77 | 16.77 | 24.6 | 71.9 | 15 | 0 | 55.13 | 17.642 | 0 | Diesel-backup
2025-07-13 17:00 | 194 | 7 | Winter | 17 | 0 | -25.5 | 14.78 | 45 | 0 | 0 | 120 | 120 | 25.5 | 69.49 | 33.59 | 50.51 | 0 | 0 | 0 | Normal
2025-07-13 18:00 | 194 | 7 | Winter | 18 | 0 | -27.1 | 9 | 52.1 | 0 | 0 | 23.29 | 23.29 | 27.1 | 70.35 | 15 | -46.47 | 0.59 | 0.223 | 0 | Diesel-backup
2025-07-13 19:00 | 194 | 7 | Winter | 19 | 0 | -22.8 | 7.29 | 45.4 | 0 | 0 | 7.62 | 7.62 | 22.8 | 71.69 | 15 | 0 | 64.07 | 20.502 | 0 | Diesel-backup
2025-07-13 20:00 | 194 | 7 | Winter | 20 | 0 | -24 | 15.18 | 17.9 | 0 | 0 | 120 | 120 | 24 | 61.8 | 36.42 | 58.2 | 0 | 0 | 0 | Normal
2025-07-13 21:00 | 194 | 7 | Winter | 21 | 0 | -26 | 2.24 | 55.3 | 0 | 0 | 0 | 0 | 26 | 53.23 | 15.13 | -53.23 | 0 | 0 | 0 | Battery-supported
2025-07-13 22:00 | 194 | 7 | Winter | 22 | 0 | -24.7 | 11.73 | 55.2 | 0 | 0 | 78.02 | 78.02 | 24.7 | 61.48 | 21.21 | 16.54 | 0 | 0 | 0 | Normal
2025-07-13 23:00 | 194 | 7 | Winter | 23 | 0 | -25.2 | 13.79 | 61.5 | 0 | 0 | 120 | 120 | 25.2 | 59.37 | 43.52 | 60.63 | 0 | 0 | 0 | Normal
2025-07-14 | 195 | 7 | Winter | 0 | 0 | -26.9 | 21.7 | 41.3 | 0 | 0 | 120 | 120 | 26.9 | 57.36 | 66.58 | 62.64 | 0 | 0 | 0 | Normal
2025-07-14 01:00 | 195 | 7 | Winter | 1 | 0 | -24.8 | 10.71 | 15.7 | 0 | 0 | 52.46 | 52.46 | 24.8 | 60.49 | 63.36 | -8.03 | 0 | 0 | 0 | Battery-supported
2025-07-14 02:00 | 195 | 7 | Winter | 2 | 0 | -26.4 | 2.98 | 35.3 | 0 | 0 | 0 | 0 | 26.4 | 62.85 | 38.22 | -62.85 | 0 | 0 | 0 | Battery-supported
2025-07-14 03:00 | 195 | 7 | Winter | 3 | 0 | -27.1 | 11.11 | 54.3 | 0 | 0 | 61.68 | 61.68 | 27.1 | 65.62 | 36.65 | -3.94 | 0 | 0 | 0 | Battery-supported
2025-07-14 04:00 | 195 | 7 | Winter | 4 | 0 | -28.6 | 2.81 | 44.4 | 0 | 0 | 0 | 0 | 28.6 | 59.19 | 15 | -54.12 | 5.07 | 1.882 | 0 | Diesel-backup
2025-07-14 05:00 | 195 | 7 | Winter | 5 | 0 | -25.8 | 12.94 | 53.6 | 0 | 0 | 117.74 | 117.74 | 25.8 | 59.16 | 36.56 | 58.58 | 0 | 0 | 0 | Normal
2025-07-14 06:00 | 195 | 7 | Winter | 6 | 0 | -23.7 | 19.59 | 75.3 | 0 | 0 | 120 | 120 | 23.7 | 59.9 | 58.67 | 60.1 | 0 | 0 | 0 | Normal
2025-07-14 07:00 | 195 | 7 | Winter | 7 | 0 | -26.5 | 9.84 | 68 | 0 | 0 | 35.67 | 35.67 | 26.5 | 65.93 | 46.57 | -30.26 | 0 | 0 | 0 | Battery-supported
2025-07-14 08:00 | 195 | 7 | Winter | 8 | 0 | -19.4 | 9.01 | 17.4 | 0 | 0 | 23.41 | 23.41 | 19.4 | 66.04 | 29.52 | -42.63 | 0 | 0 | 0 | Battery-supported
2025-07-14 09:00 | 195 | 7 | Winter | 9 | 0 | -23 | 16.05 | 85.1 | 0 | 0 | 120 | 120 | 23 | 64.03 | 50.12 | 55.97 | 0 | 0 | 0 | Normal
2025-07-14 10:00 | 195 | 7 | Winter | 10 | 0 | -22.1 | 12.66 | 37.3 | 0 | 0 | 107.57 | 107.57 | 22.1 | 67.18 | 64.98 | 40.39 | 0 | 0 | 0 | Normal
2025-07-14 11:00 | 195 | 7 | Winter | 11 | 0 | -23.2 | 15.36 | 90.6 | 0 | 0 | 120 | 120 | 23.2 | 64.12 | 85.54 | 55.88 | 0 | 0 | 0 | Normal
2025-07-14 12:00 | 195 | 7 | Winter | 12 | 0 | -20.9 | 32.82 | 15.6 | 0 | 0 | 0 | 0 | 20.9 | 62.25 | 60.64 | -62.25 | 0 | 0 | 0 | Battery-supported
2025-07-14 13:00 | 195 | 7 | Winter | 13 | 0 | -26.7 | 7.6 | 48 | 0 | 0 | 9.65 | 9.65 | 26.7 | 68.45 | 37.12 | -58.8 | 0 | 0 | 0 | Battery-supported
2025-07-14 14:00 | 195 | 7 | Winter | 14 | 0 | -30.6 | 13.44 | 61.2 | 0 | 0 | 120 | 120 | 30.6 | 71.03 | 55.14 | 48.97 | 0 | 0 | 0 | Normal
2025-07-14 15:00 | 195 | 7 | Winter | 15 | 0 | -26 | 22.72 | 56 | 0 | 0 | 120 | 120 | 26 | 71.94 | 72.83 | 48.06 | 0 | 0 | 0 | Normal
2025-07-14 16:00 | 195 | 7 | Winter | 16 | 0 | -23.8 | 22.92 | 66.1 | 0 | 0 | 120 | 120 | 23.8 | 70.52 | 91.04 | 49.48 | 0 | 0 | 0 | Normal
2025-07-14 17:00 | 195 | 7 | Winter | 17 | 0 | -24.7 | 14.2 | 86.7 | 0 | 0 | 120 | 120 | 24.7 | 66.1 | 95 | 10.77 | 0 | 0 | 0 | Normal
2025-07-14 18:00 | 195 | 7 | Winter | 18 | 0 | -24.4 | 8.78 | 70.3 | 0 | 0 | 20.6 | 20.6 | 24.4 | 68.1 | 76 | -47.5 | 0 | 0 | 0 | Battery-supported
2025-07-14 19:00 | 195 | 7 | Winter | 19 | 0 | -22.1 | 15.24 | 12.3 | 0 | 0 | 120 | 120 | 22.1 | 63.56 | 95 | 51.63 | 0 | 0 | 0 | Normal
2025-07-14 20:00 | 195 | 7 | Winter | 20 | 0 | -24.1 | 15.43 | 17.1 | 0 | 0 | 120 | 120 | 24.1 | 63.35 | 95 | 0 | 0 | 0 | 0 | Normal
2025-07-14 21:00 | 195 | 7 | Winter | 21 | 0 | -23.2 | 16.94 | 18.6 | 0 | 0 | 120 | 120 | 23.2 | 53.84 | 95 | 0 | 0 | 0 | 0 | Normal
2025-07-14 22:00 | 195 | 7 | Winter | 22 | 0 | -27.1 | 5.06 | 69.2 | 0 | 0 | 0.53 | 0.53 | 27.1 | 69.09 | 67.58 | -68.56 | 0 | 0 | 0 | Battery-supported
2025-07-14 23:00 | 195 | 7 | Winter | 23 | 0 | -27.4 | 26.82 | 63.9 | 0 | 0 | 120 | 120 | 27.4 | 59.42 | 89.87 | 60.58 | 0 | 0 | 0 | Normal
2025-07-15 | 196 | 7 | Winter | 0 | 0 | -21.4 | 22.77 | 16.3 | 0 | 0 | 120 | 120 | 21.4 | 58.94 | 95 | 13.94 | 0 | 0 | 0 | Normal
2025-07-15 01:00 | 196 | 7 | Winter | 1 | 0 | -24.8 | 10.04 | 16.8 | 0 | 0 | 39.15 | 39.15 | 24.8 | 61.36 | 86.12 | -22.21 | 0 | 0 | 0 | Battery-supported
2025-07-15 02:00 | 196 | 7 | Winter | 2 | 0 | -26.4 | 21.51 | 63.4 | 0 | 0 | 120 | 120 | 26.4 | 56.64 | 95 | 24.14 | 0 | 0 | 0 | Normal
2025-07-15 03:00 | 196 | 7 | Winter | 3 | 0 | -26.4 | 9.61 | 38.4 | 0 | 0 | 31.93 | 31.93 | 26.4 | 63.1 | 82.53 | -31.17 | 0 | 0 | 0 | Battery-supported
2025-07-15 04:00 | 196 | 7 | Winter | 4 | 0 | -26.4 | 24.43 | 40.6 | 0 | 0 | 120 | 120 | 26.4 | 62.58 | 95 | 33.88 | 0 | 0 | 0 | Normal
2025-07-15 05:00 | 196 | 7 | Winter | 5 | 0 | -26.6 | 11.06 | 52.6 | 0 | 0 | 60.47 | 60.47 | 26.6 | 61.5 | 94.59 | -1.03 | 0 | 0 | 0 | Battery-supported
2025-07-15 06:00 | 196 | 7 | Winter | 6 | 0 | -27.8 | 5.8 | 84.8 | 0 | 0 | 1.7 | 1.7 | 27.8 | 61.06 | 70.84 | -59.36 | 0 | 0 | 0 | Battery-supported
2025-07-15 07:00 | 196 | 7 | Winter | 7 | 0 | -28.3 | 30.36 | 5.4 | 0 | 0 | 0 | 0 | 28.3 | 63.29 | 45.53 | -63.29 | 0 | 0 | 0 | Battery-supported
2025-07-15 08:00 | 196 | 7 | Winter | 8 | 0 | -25.4 | 16.55 | 22.5 | 0 | 0 | 120 | 120 | 25.4 | 70.29 | 63.82 | 49.71 | 0 | 0 | 0 | Normal
2025-07-15 09:00 | 196 | 7 | Winter | 9 | 0 | -26.3 | 9.23 | 63.5 | 0 | 0 | 26.33 | 26.33 | 26.3 | 65.86 | 48.01 | -39.53 | 0 | 0 | 0 | Battery-supported
2025-07-15 10:00 | 196 | 7 | Winter | 10 | 0 | -22.6 | 25.58 | 8.3 | 0 | 0 | 120 | 120 | 22.6 | 71.35 | 65.91 | 48.65 | 0 | 0 | 0 | Normal
2025-07-15 11:00 | 196 | 7 | Winter | 11 | 0 | -24.4 | 15.34 | 58.1 | 0 | 0 | 120 | 120 | 24.4 | 70.15 | 84.26 | 49.85 | 0 | 0 | 0 | Normal
2025-07-15 12:00 | 196 | 7 | Winter | 12 | 0 | -24.4 | 8.51 | 55.5 | 0 | 0 | 17.6 | 17.6 | 24.4 | 57.78 | 68.19 | -40.18 | 0 | 0 | 0 | Battery-supported
2025-07-15 13:00 | 196 | 7 | Winter | 13 | 0 | -26.6 | 25.77 | 87.8 | 0 | 0 | 120 | 120 | 26.6 | 68.7 | 87.06 | 51.3 | 0 | 0 | 0 | Normal
2025-07-15 14:00 | 196 | 7 | Winter | 14 | 0 | -25.3 | 16.9 | 27.5 | 0 | 0 | 120 | 120 | 25.3 | 76.82 | 95 | 21.57 | 0 | 0 | 0 | Normal
2025-07-15 15:00 | 196 | 7 | Winter | 15 | 0 | -24.2 | 12.85 | 76.3 | 0 | 0 | 114.41 | 114.41 | 24.2 | 68.63 | 95 | 0 | 0 | 0 | 0 | Normal
2025-07-15 16:00 | 196 | 7 | Winter | 16 | 0 | -23.4 | 10.63 | 60.5 | 0 | 0 | 50.73 | 50.73 | 23.4 | 63.5 | 89.89 | -12.77 | 0 | 0 | 0 | Battery-supported
2025-07-15 17:00 | 196 | 7 | Winter | 17 | 0 | -25.2 | 5.65 | 33.9 | 0 | 0 | 1.39 | 1.39 | 25.2 | 70.76 | 62.14 | -69.37 | 0 | 0 | 0 | Battery-supported
2025-07-15 18:00 | 196 | 7 | Winter | 18 | 0 | -22.6 | 1.54 | 31.7 | 0 | 0 | 0 | 0 | 22.6 | 57.13 | 39.29 | -57.13 | 0 | 0 | 0 | Battery-supported
2025-07-15 19:00 | 196 | 7 | Winter | 19 | 0 | -25 | 15.94 | 96.1 | 0 | 0 | 120 | 120 | 25 | 69.08 | 58.03 | 50.92 | 0 | 0 | 0 | Normal
2025-07-15 20:00 | 196 | 7 | Winter | 20 | 0 | -23.3 | 4.86 | 48.8 | 0 | 0 | 0.35 | 0.35 | 23.3 | 64.29 | 32.45 | -63.94 | 0 | 0 | 0 | Battery-supported
2025-07-15 21:00 | 196 | 7 | Winter | 21 | 0 | -26.1 | 5.65 | 64.4 | 0 | 0 | 1.39 | 1.39 | 26.1 | 61.27 | 15 | -43.64 | 16.24 | 5.796 | 0 | Diesel-backup
2025-07-15 22:00 | 196 | 7 | Winter | 22 | 0 | -29 | 9.51 | 57.7 | 0 | 0 | 30.38 | 30.38 | 29 | 58.68 | 15 | 0 | 28.3 | 9.661 | 0 | Diesel-backup
2025-07-15 23:00 | 196 | 7 | Winter | 23 | 0 | -24.4 | 9.66 | 28.1 | 0 | 0 | 32.72 | 32.72 | 24.4 | 57.68 | 15 | 0 | 24.96 | 8.627 | 0 | Diesel-backup
2025-07-16 | 197 | 7 | Winter | 0 | 0 | -23.4 | 6.17 | 49.7 | 0 | 0 | 2.66 | 2.66 | 23.4 | 47.95 | 15 | 0 | 45.29 | 14.493 | 0 | Diesel-backup
2025-07-16 01:00 | 197 | 7 | Winter | 1 | 0 | -23.7 | 15.93 | 53 | 0 | 0 | 120 | 120 | 23.7 | 56.22 | 38.47 | 63.78 | 0 | 0 | 0 | Normal
2025-07-16 02:00 | 197 | 7 | Winter | 2 | 0 | -24.1 | 3.14 | 38.1 | 0 | 0 | 0 | 0 | 24.1 | 59.58 | 15 | -58.68 | 0.9 | 0.34 | 0 | Diesel-backup
2025-07-16 03:00 | 197 | 7 | Winter | 3 | 0 | -25.8 | 15.75 | 29.4 | 0 | 0 | 120 | 120 | 25.8 | 65.26 | 35.14 | 54.74 | 0 | 0 | 0 | Normal
2025-07-16 04:00 | 197 | 7 | Winter | 4 | 0 | -26.8 | 8.84 | 46.7 | 0 | 0 | 21.31 | 21.31 | 26.8 | 71.66 | 15 | -50.35 | 0 | 0 | 0 | Battery-supported
2025-07-16 05:00 | 197 | 7 | Winter | 5 | 0 | -23.8 | 5.96 | 39.9 | 0 | 0 | 2.08 | 2.08 | 23.8 | 55.52 | 15 | -0.01 | 53.43 | 17.097 | 0 | Diesel-backup
2025-07-16 06:00 | 197 | 7 | Winter | 6 | 0 | -24.1 | 3.37 | 61.5 | 0 | 0 | 0 | 0 | 24.1 | 61.12 | 15 | 0 | 61.12 | 19.558 | 0 | Diesel-backup
2025-07-16 07:00 | 197 | 7 | Winter | 7 | 0 | -26.2 | 11.73 | 57.1 | 0 | 0 | 78.02 | 78.02 | 26.2 | 59.86 | 21.68 | 18.16 | 0 | 0 | 0 | Normal
2025-07-16 08:00 | 197 | 7 | Winter | 8 | 0 | -22.6 | 4.6 | 52.3 | 0 | 0 | 0.19 | 0.19 | 22.6 | 64.4 | 15 | -16.71 | 47.5 | 15.201 | 0 | Diesel-backup
2025-07-16 09:00 | 197 | 7 | Winter | 9 | 0 | -26.9 | 4.13 | 53.4 | 0 | 0 | 0.03 | 0.03 | 26.9 | 70.26 | 15 | 0 | 70.23 | 22.474 | 0 | Diesel-backup
2025-07-16 10:00 | 197 | 7 | Winter | 10 | 0 | -26.3 | 22.59 | 57.2 | 0 | 0 | 120 | 120 | 26.3 | 68.67 | 33.89 | 51.33 | 0 | 0 | 0 | Normal
2025-07-16 11:00 | 197 | 7 | Winter | 11 | 0 | -21.4 | 3.83 | 38.6 | 0 | 0 | 0.01 | 0.01 | 21.4 | 71.87 | 15 | -47.22 | 24.64 | 8.526 | 0 | Diesel-backup
2025-07-16 12:00 | 197 | 7 | Winter | 12 | 0 | -23.1 | 3.09 | 26 | 0 | 0 | 0 | 0 | 23.1 | 64.91 | 15 | 0 | 64.91 | 20.771 | 0 | Diesel-backup
2025-07-16 13:00 | 197 | 7 | Winter | 13 | 0 | -25.8 | 15.02 | 80.4 | 0 | 0 | 120 | 120 | 25.8 | 64.23 | 35.52 | 55.77 | 0 | 0 | 0 | Normal
2025-07-16 14:00 | 197 | 7 | Winter | 14 | 0 | -24.4 | 12.3 | 70.8 | 0 | 0 | 95.38 | 95.38 | 24.4 | 68.13 | 45.55 | 27.25 | 0 | 0 | 0 | Normal
2025-07-16 15:00 | 197 | 7 | Winter | 15 | 0 | -24.7 | 7.24 | 64 | 0 | 0 | 7.32 | 7.32 | 24.7 | 63.4 | 23.12 | -56.08 | 0 | 0 | 0 | Battery-supported
2025-07-16 16:00 | 197 | 7 | Winter | 16 | 0 | -31 | 5.4 | 38 | 0 | 0 | 0.96 | 0.96 | 31 | 72.52 | 15 | -20.3 | 51.26 | 16.404 | 0 | Diesel-backup
2025-07-16 17:00 | 197 | 7 | Winter | 17 | 0 | -27 | 6.44 | 73.5 | 0 | 0 | 3.56 | 3.56 | 27 | 74.24 | 15 | 0 | 70.68 | 22.618 | 0 | Diesel-backup
2025-07-16 18:00 | 197 | 7 | Winter | 18 | 0 | -25.1 | 7.37 | 56.9 | 0 | 0 | 8.11 | 8.11 | 25.1 | 67.11 | 15 | 0 | 59 | 18.88 | 0 | Diesel-backup
2025-07-16 19:00 | 197 | 7 | Winter | 19 | 0 | -25.8 | 14.02 | 58.7 | 0 | 0 | 120 | 120 | 25.8 | 70.88 | 33.08 | 49.12 | 0 | 0 | 0 | Normal
2025-07-16 20:00 | 197 | 7 | Winter | 20 | 0 | -24.5 | 11.9 | 17.5 | 0 | 0 | 82.96 | 82.96 | 24.5 | 66.66 | 39.07 | 16.3 | 0 | 0 | 0 | Normal
2025-07-16 21:00 | 197 | 7 | Winter | 21 | 0 | -22.5 | 8.23 | 34.4 | 0 | 0 | 14.81 | 14.81 | 22.5 | 58.54 | 21.58 | -43.73 | 0 | 0 | 0 | Battery-supported
2025-07-16 22:00 | 197 | 7 | Winter | 22 | 0 | -25.7 | 8.17 | 53.7 | 0 | 0 | 14.25 | 14.25 | 25.7 | 57.91 | 15 | -16.46 | 27.2 | 9.325 | 0 | Diesel-backup
2025-07-16 23:00 | 197 | 7 | Winter | 23 | 0 | -27.3 | 15.42 | 77.5 | 0 | 0 | 120 | 120 | 27.3 | 65.55 | 35.04 | 54.45 | 0 | 0 | 0 | Normal
2025-07-17 | 198 | 7 | Winter | 0 | 0 | -24.3 | 5.94 | 65 | 0 | 0 | 2.03 | 2.03 | 24.3 | 54.03 | 15 | -50.09 | 1.91 | 0.715 | 0 | Diesel-backup
2025-07-17 01:00 | 198 | 7 | Winter | 1 | 0 | -25.7 | 3.28 | 55.5 | 0 | 0 | 0 | 0 | 25.7 | 57.5 | 15 | 0 | 57.5 | 18.4 | 0 | Diesel-backup
2025-07-17 02:00 | 198 | 7 | Winter | 2 | 0 | -25.3 | 21.2 | 28.4 | 0 | 0 | 120 | 120 | 25.3 | 60.63 | 36.85 | 59.37 | 0 | 0 | 0 | Normal
2025-07-17 03:00 | 198 | 7 | Winter | 3 | 0 | -25.6 | 8.24 | 26 | 0 | 0 | 14.91 | 14.91 | 25.6 | 63.9 | 17.25 | -48.99 | 0 | 0 | 0 | Battery-supported
2025-07-17 04:00 | 198 | 7 | Winter | 4 | 0 | -20.1 | 28.61 | 92.2 | 0 | 0 | 0 | 0 | 20.1 | 55.95 | 15 | -5.63 | 50.32 | 16.102 | 0 | Diesel-backup
2025-07-17 05:00 | 198 | 7 | Winter | 5 | 0 | -29.9 | 7.5 | 23.8 | 0 | 0 | 8.96 | 8.96 | 29.9 | 66.95 | 15 | 0 | 57.99 | 18.557 | 0 | Diesel-backup
2025-07-17 06:00 | 198 | 7 | Winter | 6 | 0 | -25.9 | 10.28 | 61.2 | 0 | 0 | 43.62 | 43.62 | 25.9 | 56.03 | 15 | 0 | 12.41 | 4.489 | 0 | Diesel-backup
2025-07-17 07:00 | 198 | 7 | Winter | 7 | 0 | -25 | 5.62 | 48.3 | 0 | 0 | 1.33 | 1.33 | 25 | 58.74 | 15 | 0 | 57.41 | 18.371 | 0 | Diesel-backup
2025-07-17 08:00 | 198 | 7 | Winter | 8 | 0 | -26.7 | 12.01 | 68.2 | 0 | 0 | 86.26 | 86.26 | 26.7 | 70.65 | 20.74 | 15.61 | 0 | 0 | 0 | Normal
2025-07-17 09:00 | 198 | 7 | Winter | 9 | 0 | -23 | 8.3 | 0 | 0 | 0 | 15.48 | 15.48 | 23 | 66.22 | 15 | -14.36 | 36.38 | 12.043 | 0 | Diesel-backup
2025-07-17 10:00 | 198 | 7 | Winter | 10 | 0 | -23.2 | 8.95 | 65.3 | 0 | 0 | 22.66 | 22.66 | 23.2 | 61.87 | 15 | 0 | 39.21 | 12.838 | 0 | Diesel-backup
2025-07-17 11:00 | 198 | 7 | Winter | 11 | 0 | -25.1 | 10.97 | 26 | 0 | 0 | 58.34 | 58.34 | 25.1 | 64.73 | 15 | 0 | 6.39 | 2.361 | 0 | Diesel-backup
2025-07-17 12:00 | 198 | 7 | Winter | 12 | 0 | -25.6 | 7.61 | 83.6 | 0 | 0 | 9.72 | 9.72 | 25.6 | 68.07 | 15 | 0 | 58.35 | 18.672 | 0 | Diesel-backup
2025-07-17 13:00 | 198 | 7 | Winter | 13 | 0 | -25.2 | 11.78 | 45.6 | 0 | 0 | 79.45 | 79.45 | 25.2 | 71.19 | 18.04 | 8.26 | 0 | 0 | 0 | Normal
2025-07-17 14:00 | 198 | 7 | Winter | 14 | 0 | -25.2 | 6.51 | 78.9 | 0 | 0 | 3.82 | 3.82 | 25.2 | 76.6 | 15 | -7.6 | 65.18 | 20.858 | 0 | Diesel-backup
2025-07-17 15:00 | 198 | 7 | Winter | 15 | 0 | -25.2 | 11.42 | 73.1 | 0 | 0 | 69.53 | 69.53 | 25.2 | 63.84 | 17.09 | 5.69 | 0 | 0 | 0 | Normal
2025-07-17 16:00 | 198 | 7 | Winter | 16 | 0 | -25.4 | 2.83 | 35.7 | 0 | 0 | 0 | 0 | 25.4 | 68.6 | 15 | -5.23 | 63.37 | 20.277 | 0 | Diesel-backup
2025-07-17 17:00 | 198 | 7 | Winter | 17 | 0 | -24.4 | 3.83 | 25.9 | 0 | 0 | 0.01 | 0.01 | 24.4 | 63.32 | 15 | 0 | 63.31 | 20.259 | 0 | Diesel-backup
2025-07-17 18:00 | 198 | 7 | Winter | 18 | 0 | -23.3 | 5.56 | 84.2 | 0 | 0 | 1.22 | 1.22 | 23.3 | 66.2 | 15 | 0 | 64.98 | 20.794 | 0 | Diesel-backup
2025-07-17 19:00 | 198 | 7 | Winter | 19 | 0 | -27.7 | 4.42 | 67.6 | 0 | 0 | 0.11 | 0.11 | 27.7 | 69.16 | 15 | 0 | 69.05 | 22.096 | 0 | Diesel-backup
2025-07-17 20:00 | 198 | 7 | Winter | 20 | 0 | -27.3 | 4.68 | 52.8 | 0 | 0 | 0.23 | 0.23 | 27.3 | 71.93 | 15 | 0 | 71.7 | 22.944 | 0 | Diesel-backup
2025-07-17 21:00 | 198 | 7 | Winter | 21 | 0 | -28.8 | 13.53 | 30.2 | 0 | 0 | 120 | 120 | 28.8 | 55.85 | 38.61 | 64.15 | 0 | 0 | 0 | Normal
2025-07-17 22:00 | 198 | 7 | Winter | 22 | 0 | -23.1 | 8.45 | 56.3 | 0 | 0 | 16.98 | 16.98 | 23.1 | 56.77 | 22.69 | -39.79 | 0 | 0 | 0 | Battery-supported
2025-07-17 23:00 | 198 | 7 | Winter | 23 | 0 | -24.4 | 7.61 | 82.4 | 0 | 0 | 9.72 | 9.72 | 24.4 | 59.83 | 15 | -19.23 | 30.88 | 10.44 | 0 | Diesel-backup
2025-07-18 | 199 | 7 | Winter | 0 | 0 | -23.9 | 11.85 | 66 | 0 | 0 | 81.48 | 81.48 | 23.9 | 59.72 | 23.01 | 21.76 | 0 | 0 | 0 | Normal
2025-07-18 01:00 | 199 | 7 | Winter | 1 | 0 | -28.1 | 12.39 | 67.3 | 0 | 0 | 98.34 | 98.34 | 28.1 | 64.41 | 35.49 | 33.93 | 0 | 0 | 0 | Normal
2025-07-18 02:00 | 199 | 7 | Winter | 2 | 0 | -21.1 | 7.06 | 59.8 | 0 | 0 | 6.31 | 6.31 | 21.1 | 56.73 | 15.33 | -50.42 | 0 | 0 | 0 | Battery-supported
2025-07-18 03:00 | 199 | 7 | Winter | 3 | 0 | -26.3 | 18.19 | 88.6 | 0 | 0 | 120 | 120 | 26.3 | 66.33 | 35.08 | 53.67 | 0 | 0 | 0 | Normal
2025-07-18 04:00 | 199 | 7 | Winter | 4 | 0 | -24.6 | 8.75 | 55.4 | 0 | 0 | 20.25 | 20.25 | 24.6 | 64.92 | 17.21 | -44.67 | 0 | 0 | 0 | Battery-supported
2025-07-18 05:00 | 199 | 7 | Winter | 5 | 0 | -23.1 | 14.28 | 30.4 | 0 | 0 | 120 | 120 | 23.1 | 57.26 | 40.3 | 62.74 | 0 | 0 | 0 | Normal
2025-07-18 06:00 | 199 | 7 | Winter | 6 | 0 | -27.2 | 6.5 | 35.7 | 0 | 0 | 3.78 | 3.78 | 27.2 | 60.12 | 17.76 | -56.34 | 0 | 0 | 0 | Battery-supported
2025-07-18 07:00 | 199 | 7 | Winter | 7 | 0 | -26.2 | 11.57 | 60.8 | 0 | 0 | 73.56 | 73.56 | 26.2 | 62 | 22.01 | 11.56 | 0 | 0 | 0 | Normal
2025-07-18 08:00 | 199 | 7 | Winter | 8 | 0 | -24.6 | 15.07 | 23.4 | 0 | 0 | 120 | 120 | 24.6 | 70.83 | 40.11 | 49.17 | 0 | 0 | 0 | Normal
2025-07-18 09:00 | 199 | 7 | Winter | 9 | 0 | -18.7 | 14.06 | 9.6 | 0 | 0 | 120 | 120 | 18.7 | 61.87 | 61.5 | 58.13 | 0 | 0 | 0 | Normal
2025-07-18 10:00 | 199 | 7 | Winter | 10 | 0 | -24.3 | 13.32 | 37.4 | 0 | 0 | 120 | 120 | 24.3 | 62.95 | 82.5 | 57.05 | 0 | 0 | 0 | Normal
2025-07-18 11:00 | 199 | 7 | Winter | 11 | 0 | -21.5 | 6.29 | 62.5 | 0 | 0 | 3.04 | 3.04 | 21.5 | 68.34 | 56.38 | -65.3 | 0 | 0 | 0 | Battery-supported
2025-07-18 12:00 | 199 | 7 | Winter | 12 | 0 | -22.3 | 4.28 | 81.2 | 0 | 0 | 0.07 | 0.07 | 22.3 | 66.88 | 29.65 | -66.81 | 0 | 0 | 0 | Battery-supported
2025-07-18 13:00 | 199 | 7 | Winter | 13 | 0 | -24.2 | 3.93 | 36.5 | 0 | 0 | 0.01 | 0.01 | 24.2 | 74.24 | 15 | -36.63 | 37.6 | 12.388 | 0 | Diesel-backup
2025-07-18 14:00 | 199 | 7 | Winter | 14 | 0 | -27.2 | 7.38 | 93.8 | 0 | 0 | 8.18 | 8.18 | 27.2 | 67.21 | 15 | 0 | 59.03 | 18.89 | 0 | Diesel-backup
2025-07-18 15:00 | 199 | 7 | Winter | 15 | 0 | -22.7 | 7.05 | 67.1 | 0 | 0 | 6.26 | 6.26 | 22.7 | 66.65 | 15 | 0 | 60.39 | 19.325 | 0 | Diesel-backup
2025-07-18 16:00 | 199 | 7 | Winter | 16 | 0 | -28.3 | 12.51 | 73.5 | 0 | 0 | 102.37 | 102.37 | 28.3 | 73.03 | 25.8 | 29.34 | 0 | 0 | 0 | Normal
2025-07-18 17:00 | 199 | 7 | Winter | 17 | 0 | -21.5 | 10.04 | 46.1 | 0 | 0 | 39.15 | 39.15 | 21.5 | 63.61 | 16.01 | -24.46 | 0 | 0 | 0 | Battery-supported
2025-07-18 18:00 | 199 | 7 | Winter | 18 | 0 | -24.6 | 4.01 | 44.5 | 0 | 0 | 0.02 | 0.02 | 24.6 | 63.81 | 15 | -2.53 | 61.26 | 19.602 | 0 | Diesel-backup
2025-07-18 19:00 | 199 | 7 | Winter | 19 | 0 | -30.8 | 16.61 | 53.7 | 0 | 0 | 120 | 120 | 30.8 | 74.92 | 31.59 | 45.08 | 0 | 0 | 0 | Normal
2025-07-18 20:00 | 199 | 7 | Winter | 20 | 0 | -25.7 | 11.2 | 67.7 | 0 | 0 | 63.9 | 63.9 | 25.7 | 66.98 | 30.36 | -3.08 | 0 | 0 | 0 | Battery-supported
2025-07-18 21:00 | 199 | 7 | Winter | 21 | 0 | -23.6 | 6.01 | 16.7 | 0 | 0 | 2.21 | 2.21 | 23.6 | 58.71 | 15 | -38.39 | 18.11 | 6.417 | 0 | Diesel-backup
2025-07-18 22:00 | 199 | 7 | Winter | 22 | 0 | -25.5 | 6.7 | 23.3 | 0 | 0 | 4.59 | 4.59 | 25.5 | 60.67 | 15 | 0 | 56.08 | 17.946 | 0 | Diesel-backup
2025-07-18 23:00 | 199 | 7 | Winter | 23 | 0 | -23.4 | 21.11 | 44.5 | 0 | 0 | 120 | 120 | 23.4 | 54.17 | 39.23 | 65.83 | 0 | 0 | 0 | Normal
2025-07-19 | 200 | 7 | Winter | 0 | 0 | -26.9 | 4.42 | 47.9 | 0 | 0 | 0.11 | 0.11 | 26.9 | 60.16 | 15.21 | -60.05 | 0 | 0 | 0 | Battery-supported
2025-07-19 01:00 | 200 | 7 | Winter | 1 | 0 | -27.9 | 21.74 | 59.4 | 0 | 0 | 120 | 120 | 27.9 | 61.26 | 36.82 | 58.74 | 0 | 0 | 0 | Normal
2025-07-19 02:00 | 200 | 7 | Winter | 2 | 0 | -25.1 | 8.31 | 45.3 | 0 | 0 | 15.58 | 15.58 | 25.1 | 60.37 | 18.91 | -44.79 | 0 | 0 | 0 | Battery-supported
2025-07-19 03:00 | 200 | 7 | Winter | 3 | 0 | -24.9 | 8.66 | 49.3 | 0 | 0 | 19.23 | 19.23 | 24.9 | 61.8 | 15 | -9.76 | 32.81 | 11.01 | 0 | Diesel-backup
2025-07-19 04:00 | 200 | 7 | Winter | 4 | 0 | -25.8 | 11.89 | 78 | 0 | 0 | 82.66 | 82.66 | 25.8 | 62.09 | 22.57 | 20.57 | 0 | 0 | 0 | Normal
2025-07-19 05:00 | 200 | 7 | Winter | 5 | 0 | -22.3 | 3.22 | 14.3 | 0 | 0 | 0 | 0 | 22.3 | 60.79 | 15 | -18.92 | 41.87 | 13.565 | 0 | Diesel-backup
2025-07-19 06:00 | 200 | 7 | Winter | 6 | 0 | -26.9 | 11.17 | 61.7 | 0 | 0 | 63.15 | 63.15 | 26.9 | 62.53 | 15.23 | 0.62 | 0 | 0 | 0 | Normal
2025-07-19 07:00 | 200 | 7 | Winter | 7 | 0 | -24.3 | 14.89 | 58.8 | 0 | 0 | 120 | 120 | 24.3 | 67.29 | 34.63 | 52.71 | 0 | 0 | 0 | Normal
2025-07-19 08:00 | 200 | 7 | Winter | 8 | 0 | -24.8 | 7.26 | 22 | 0 | 0 | 7.44 | 7.44 | 24.8 | 69.36 | 15 | -49.06 | 12.86 | 4.643 | 0 | Diesel-backup
2025-07-19 09:00 | 200 | 7 | Winter | 9 | 0 | -28.4 | 9.55 | 69.4 | 0 | 0 | 30.99 | 30.99 | 28.4 | 66.07 | 15 | 0 | 35.08 | 11.671 | 0 | Diesel-backup
2025-07-19 10:00 | 200 | 7 | Winter | 10 | 0 | -27.9 | 28.97 | 31.4 | 0 | 0 | 0 | 0 | 27.9 | 69.35 | 15 | 0 | 69.35 | 22.192 | 0 | Diesel-backup
2025-07-19 11:00 | 200 | 7 | Winter | 11 | 0 | -25 | 15.83 | 40.4 | 0 | 0 | 120 | 120 | 25 | 80.78 | 29.43 | 39.22 | 0 | 0 | 0 | Normal
2025-07-19 12:00 | 200 | 7 | Winter | 12 | 0 | -20.6 | 5.27 | 72.6 | 0 | 0 | 0.78 | 0.78 | 20.6 | 58.24 | 15 | -36.08 | 21.38 | 7.487 | 0 | Diesel-backup
2025-07-19 13:00 | 200 | 7 | Winter | 13 | 0 | -23.7 | 6.97 | 54.6 | 0 | 0 | 5.85 | 5.85 | 23.7 | 68.61 | 15 | 0 | 62.76 | 20.083 | 0 | Diesel-backup
2025-07-19 14:00 | 200 | 7 | Winter | 14 | 0 | -28.8 | 8.15 | 72.9 | 0 | 0 | 14.07 | 14.07 | 28.8 | 80.84 | 15 | 0 | 66.77 | 21.366 | 0 | Diesel-backup
2025-07-19 15:00 | 200 | 7 | Winter | 15 | 0 | -31.8 | 16.41 | 23.2 | 0 | 0 | 120 | 120 | 31.8 | 69.9 | 33.44 | 50.1 | 0 | 0 | 0 | Normal
2025-07-19 16:00 | 200 | 7 | Winter | 16 | 0 | -23.4 | 5.26 | 40.6 | 0 | 0 | 0.76 | 0.76 | 23.4 | 72.75 | 15 | -46.09 | 25.9 | 8.921 | 0 | Diesel-backup
2025-07-19 17:00 | 200 | 7 | Winter | 17 | 0 | -25.2 | 14.09 | 17.4 | 0 | 0 | 120 | 120 | 25.2 | 74.55 | 31.73 | 45.45 | 0 | 0 | 0 | Normal
2025-07-19 18:00 | 200 | 7 | Winter | 18 | 0 | -22.5 | 14.14 | 61.5 | 0 | 0 | 120 | 120 | 22.5 | 64.44 | 52.17 | 55.56 | 0 | 0 | 0 | Normal
2025-07-19 19:00 | 200 | 7 | Winter | 19 | 0 | -26.9 | 9.92 | 79.7 | 0 | 0 | 37.04 | 37.04 | 26.9 | 62.44 | 42.01 | -25.4 | 0 | 0 | 0 | Battery-supported
2025-07-19 20:00 | 200 | 7 | Winter | 20 | 0 | -24.2 | 16.73 | 53.1 | 0 | 0 | 120 | 120 | 24.2 | 69.71 | 60.52 | 50.29 | 0 | 0 | 0 | Normal
2025-07-19 21:00 | 200 | 7 | Winter | 21 | 0 | -23.1 | 5.62 | 45.7 | 0 | 0 | 1.33 | 1.33 | 23.1 | 57.83 | 37.92 | -56.5 | 0 | 0 | 0 | Battery-supported
2025-07-19 22:00 | 200 | 7 | Winter | 22 | 0 | -26 | 18.67 | 84.1 | 0 | 0 | 120 | 120 | 26 | 60.34 | 59.87 | 59.66 | 0 | 0 | 0 | Normal
2025-07-19 23:00 | 200 | 7 | Winter | 23 | 0 | -25.9 | 2.72 | 54.1 | 0 | 0 | 0 | 0 | 25.9 | 63.67 | 34.41 | -63.67 | 0 | 0 | 0 | Battery-supported
2025-07-20 | 201 | 7 | Winter | 0 | 0 | -24.9 | 5.24 | 53.5 | 0 | 0 | 0.74 | 0.74 | 24.9 | 60.04 | 15 | -48.51 | 10.79 | 3.924 | 0 | Diesel-backup
2025-07-20 01:00 | 201 | 7 | Winter | 1 | 0 | -23.8 | 2.77 | 45 | 0 | 0 | 0 | 0 | 23.8 | 52.55 | 15 | 0 | 52.55 | 16.816 | 0 | Diesel-backup
2025-07-20 02:00 | 201 | 7 | Winter | 2 | 0 | -25 | 5.83 | 53.5 | 0 | 0 | 1.77 | 1.77 | 25 | 59.63 | 15 | 0 | 57.86 | 18.515 | 0 | Diesel-backup
2025-07-20 03:00 | 201 | 7 | Winter | 3 | 0 | -22.8 | 14.29 | 52.5 | 0 | 0 | 120 | 120 | 22.8 | 59.34 | 37.32 | 60.66 | 0 | 0 | 0 | Normal
2025-07-20 04:00 | 201 | 7 | Winter | 4 | 0 | -26 | 12.19 | 81 | 0 | 0 | 91.85 | 91.85 | 26 | 63.06 | 47.92 | 28.79 | 0 | 0 | 0 | Normal
2025-07-20 05:00 | 201 | 7 | Winter | 5 | 0 | -27.9 | 11.11 | 81.1 | 0 | 0 | 61.68 | 61.68 | 27.9 | 68.1 | 45.35 | -6.42 | 0 | 0 | 0 | Battery-supported
2025-07-20 06:00 | 201 | 7 | Winter | 6 | 0 | -20.6 | 5.77 | 53.2 | 0 | 0 | 1.64 | 1.64 | 20.6 | 47.92 | 26.84 | -46.28 | 0 | 0 | 0 | Battery-supported
2025-07-20 07:00 | 201 | 7 | Winter | 7 | 0 | -26.3 | 9.45 | 55.2 | 0 | 0 | 29.48 | 29.48 | 26.3 | 65.43 | 15 | -29.59 | 6.36 | 2.348 | 0 | Diesel-backup
2025-07-20 08:00 | 201 | 7 | Winter | 8 | 0 | -26.2 | 18.78 | 53.1 | 0 | 0 | 120 | 120 | 26.2 | 67.75 | 34.23 | 52.25 | 0 | 0 | 0 | Normal
2025-07-20 09:00 | 201 | 7 | Winter | 9 | 0 | -25.1 | 5.94 | 30.5 | 0 | 0 | 2.03 | 2.03 | 25.1 | 68.93 | 15 | -48.07 | 18.83 | 6.656 | 0 | Diesel-backup
2025-07-20 10:00 | 201 | 7 | Winter | 10 | 0 | -24.8 | 6.12 | 29.4 | 0 | 0 | 2.52 | 2.52 | 24.8 | 71.36 | 15 | 0 | 68.84 | 22.029 | 0 | Diesel-backup
2025-07-20 11:00 | 201 | 7 | Winter | 11 | 0 | -25.8 | 6.3 | 66.1 | 0 | 0 | 3.07 | 3.07 | 25.8 | 65.84 | 15 | 0 | 62.77 | 20.086 | 0 | Diesel-backup
2025-07-20 12:00 | 201 | 7 | Winter | 12 | 0 | -25 | 10.76 | 85.6 | 0 | 0 | 53.56 | 53.56 | 25 | 66.54 | 15 | 0 | 12.98 | 4.686 | 0 | Diesel-backup
2025-07-20 13:00 | 201 | 7 | Winter | 13 | 0 | -25.1 | 13.55 | 12.6 | 0 | 0 | 120 | 120 | 25.1 | 70.43 | 33.24 | 49.57 | 0 | 0 | 0 | Normal
2025-07-20 14:00 | 201 | 7 | Winter | 14 | 0 | -24.6 | 15.38 | 64.2 | 0 | 0 | 120 | 120 | 24.6 | 65.31 | 53.37 | 54.69 | 0 | 0 | 0 | Normal
2025-07-20 15:00 | 201 | 7 | Winter | 15 | 0 | -30.2 | 8.13 | 42.2 | 0 | 0 | 13.89 | 13.89 | 30.2 | 74.6 | 29.08 | -60.71 | 0 | 0 | 0 | Battery-supported
2025-07-20 16:00 | 201 | 7 | Winter | 16 | 0 | -20.8 | 7.66 | 22 | 0 | 0 | 10.08 | 10.08 | 20.8 | 59.57 | 15 | -35.21 | 14.28 | 5.131 | 0 | Diesel-backup
2025-07-20 17:00 | 201 | 7 | Winter | 17 | 0 | -25.3 | 6.77 | 40.1 | 0 | 0 | 4.89 | 4.89 | 25.3 | 73.22 | 15 | 0 | 68.33 | 21.866 | 0 | Diesel-backup
2025-07-20 18:00 | 201 | 7 | Winter | 18 | 0 | -23.7 | 13.06 | 6.4 | 0 | 0 | 120 | 120 | 23.7 | 69.79 | 33.48 | 50.21 | 0 | 0 | 0 | Normal
2025-07-20 19:00 | 201 | 7 | Winter | 19 | 0 | -28 | 3.31 | 62.1 | 0 | 0 | 0 | 0 | 28 | 68.01 | 15 | -46.19 | 21.82 | 7.629 | 0 | Diesel-backup
2025-07-20 20:00 | 201 | 7 | Winter | 20 | 0 | -26 | 8.82 | 34.3 | 0 | 0 | 21.07 | 21.07 | 26 | 73.43 | 15 | 0 | 52.36 | 16.755 | 0 | Diesel-backup
2025-07-20 21:00 | 201 | 7 | Winter | 21 | 0 | -26.5 | 8.86 | 19 | 0 | 0 | 21.55 | 21.55 | 26.5 | 63.26 | 15 | 0 | 41.71 | 13.523 | 0 | Diesel-backup
2025-07-20 22:00 | 201 | 7 | Winter | 22 | 0 | -21.7 | 14.25 | 49.3 | 0 | 0 | 120 | 120 | 21.7 | 52.95 | 39.67 | 67.05 | 0 | 0 | 0 | Normal
2025-07-20 23:00 | 201 | 7 | Winter | 23 | 0 | -26.3 | 4.04 | 36.5 | 0 | 0 | 0.02 | 0.02 | 26.3 | 64.11 | 15 | -61.69 | 2.4 | 0.9 | 0 | Diesel-backup
2025-07-21 | 202 | 7 | Winter | 0 | 0 | -23.3 | 14.89 | 46.8 | 0 | 0 | 120 | 120 | 23.3 | 61.22 | 36.63 | 58.78 | 0 | 0 | 0 | Normal
2025-07-21 01:00 | 202 | 7 | Winter | 1 | 0 | -26.4 | 12.59 | 58.5 | 0 | 0 | 105.12 | 105.12 | 26.4 | 55.12 | 55.03 | 50 | 0 | 0 | 0 | Normal
2025-07-21 02:00 | 202 | 7 | Winter | 2 | 0 | -26 | 25.3 | 14.9 | 0 | 0 | 120 | 120 | 26 | 51.34 | 80.3 | 68.66 | 0 | 0 | 0 | Normal
2025-07-21 03:00 | 202 | 7 | Winter | 3 | 0 | -25.5 | 22.63 | 48.6 | 0 | 0 | 120 | 120 | 25.5 | 58.94 | 95 | 39.95 | 0 | 0 | 0 | Normal
2025-07-21 04:00 | 202 | 7 | Winter | 4 | 0 | -22.1 | 18.02 | 22.1 | 0 | 0 | 120 | 120 | 22.1 | 54.21 | 95 | 0 | 0 | 0 | 0 | Normal
2025-07-21 05:00 | 202 | 7 | Winter | 5 | 0 | -29.1 | 2.17 | 60.1 | 0 | 0 | 0 | 0 | 29.1 | 66.7 | 68.32 | -66.7 | 0 | 0 | 0 | Battery-supported
2025-07-21 06:00 | 202 | 7 | Winter | 6 | 0 | -27.9 | 4.32 | 29.9 | 0 | 0 | 0.08 | 0.08 | 27.9 | 60.29 | 44.24 | -60.21 | 0 | 0 | 0 | Battery-supported
2025-07-21 07:00 | 202 | 7 | Winter | 7 | 0 | -29.2 | 16.76 | 11.8 | 0 | 0 | 120 | 120 | 29.2 | 61.85 | 65.64 | 58.15 | 0 | 0 | 0 | Normal
2025-07-21 08:00 | 202 | 7 | Winter | 8 | 0 | -27.4 | 8.69 | 9.9 | 0 | 0 | 19.57 | 19.57 | 27.4 | 77.71 | 42.38 | -58.14 | 0 | 0 | 0 | Battery-supported
2025-07-21 09:00 | 202 | 7 | Winter | 9 | 0 | -26.7 | 22.6 | 56.6 | 0 | 0 | 120 | 120 | 26.7 | 74.8 | 59.01 | 45.2 | 0 | 0 | 0 | Normal
2025-07-21 10:00 | 202 | 7 | Winter | 10 | 0 | -28.5 | 10.06 | 84 | 0 | 0 | 39.51 | 39.51 | 28.5 | 65.47 | 48.63 | -25.96 | 0 | 0 | 0 | Battery-supported
2025-07-21 11:00 | 202 | 7 | Winter | 11 | 0 | -26.6 | 13.96 | 26.5 | 0 | 0 | 120 | 120 | 26.6 | 75.07 | 65.16 | 44.93 | 0 | 0 | 0 | Normal
2025-07-21 12:00 | 202 | 7 | Winter | 12 | 0 | -29.4 | 13.39 | 32.2 | 0 | 0 | 120 | 120 | 29.4 | 78.74 | 80.35 | 41.26 | 0 | 0 | 0 | Normal
2025-07-21 13:00 | 202 | 7 | Winter | 13 | 0 | -27.2 | 9.9 | 67.7 | 0 | 0 | 36.69 | 36.69 | 27.2 | 69.72 | 67.13 | -33.03 | 0 | 0 | 0 | Battery-supported
2025-07-21 14:00 | 202 | 7 | Winter | 14 | 0 | -22.3 | 16.93 | 76.8 | 0 | 0 | 120 | 120 | 22.3 | 63.81 | 87.81 | 56.19 | 0 | 0 | 0 | Normal
2025-07-21 15:00 | 202 | 7 | Winter | 15 | 0 | -24.1 | 14.6 | 49.7 | 0 | 0 | 120 | 120 | 24.1 | 59.62 | 95 | 19.53 | 0 | 0 | 0 | Normal
2025-07-21 16:00 | 202 | 7 | Winter | 16 | 0 | -24.6 | 4.61 | 26.8 | 0 | 0 | 0.19 | 0.19 | 24.6 | 62.31 | 70.15 | -62.12 | 0 | 0 | 0 | Battery-supported
2025-07-21 17:00 | 202 | 7 | Winter | 17 | 0 | -27.2 | 30.07 | 25.2 | 0 | 0 | 0 | 0 | 27.2 | 69.84 | 42.22 | -69.84 | 0 | 0 | 0 | Battery-supported
2025-07-21 18:00 | 202 | 7 | Winter | 18 | 0 | -28.3 | 4.33 | 6.1 | 0 | 0 | 0.08 | 0.08 | 28.3 | 69.5 | 15 | -68.04 | 1.38 | 0.519 | 0 | Diesel-backup
2025-07-21 19:00 | 202 | 7 | Winter | 19 | 0 | -27.5 | 6.1 | 36.3 | 0 | 0 | 2.46 | 2.46 | 27.5 | 69.21 | 15 | 0 | 66.75 | 21.36 | 0 | Diesel-backup
2025-07-21 20:00 | 202 | 7 | Winter | 20 | 0 | -25.1 | 13.83 | 85.3 | 0 | 0 | 120 | 120 | 25.1 | 69.62 | 33.54 | 50.38 | 0 | 0 | 0 | Normal
2025-07-21 21:00 | 202 | 7 | Winter | 21 | 0 | -23.1 | 12.36 | 55.1 | 0 | 0 | 97.34 | 97.34 | 23.1 | 65.29 | 45.33 | 32.05 | 0 | 0 | 0 | Normal
2025-07-21 22:00 | 202 | 7 | Winter | 22 | 0 | -23 | 15.31 | 37 | 0 | 0 | 120 | 120 | 23 | 55.73 | 68.99 | 64.27 | 0 | 0 | 0 | Normal
2025-07-21 23:00 | 202 | 7 | Winter | 23 | 0 | -23.6 | 8.51 | 56.4 | 0 | 0 | 17.6 | 17.6 | 23.6 | 56.33 | 53.49 | -38.73 | 0 | 0 | 0 | Battery-supported
2025-07-22 | 203 | 7 | Winter | 0 | 0 | -26.6 | 12.89 | 51.2 | 0 | 0 | 115.88 | 115.88 | 26.6 | 61.15 | 73.63 | 54.73 | 0 | 0 | 0 | Normal
2025-07-22 01:00 | 203 | 7 | Winter | 1 | 0 | -24.9 | 6.38 | 60.8 | 0 | 0 | 3.34 | 3.34 | 24.9 | 58.94 | 51.39 | -55.6 | 0 | 0 | 0 | Battery-supported
2025-07-22 02:00 | 203 | 7 | Winter | 2 | 0 | -25.7 | 10.05 | 30.5 | 0 | 0 | 39.33 | 39.33 | 25.7 | 67.57 | 40.1 | -28.24 | 0 | 0 | 0 | Battery-supported
2025-07-22 03:00 | 203 | 7 | Winter | 3 | 0 | -25.4 | 21.08 | 48 | 0 | 0 | 120 | 120 | 25.4 | 59.7 | 62.29 | 60.3 | 0 | 0 | 0 | Normal
2025-07-22 04:00 | 203 | 7 | Winter | 4 | 0 | -20.5 | 4.31 | 48.6 | 0 | 0 | 0.07 | 0.07 | 20.5 | 59.23 | 38.62 | -59.16 | 0 | 0 | 0 | Battery-supported
2025-07-22 05:00 | 203 | 7 | Winter | 5 | 0 | -28.8 | 17.52 | 87.8 | 0 | 0 | 120 | 120 | 28.8 | 74.24 | 55.46 | 45.76 | 0 | 0 | 0 | Normal
2025-07-22 06:00 | 203 | 7 | Winter | 6 | 0 | -25.5 | 8.89 | 65.1 | 0 | 0 | 21.92 | 21.92 | 25.5 | 67.54 | 37.22 | -45.62 | 0 | 0 | 0 | Battery-supported
2025-07-22 07:00 | 203 | 7 | Winter | 7 | 0 | -22.3 | 5.49 | 40.8 | 0 | 0 | 1.1 | 1.1 | 22.3 | 56.66 | 15 | -55.54 | 0.02 | 0.007 | 0 | Diesel-backup
2025-07-22 08:00 | 203 | 7 | Winter | 8 | 0 | -28.2 | 5.75 | 36.2 | 0 | 0 | 1.59 | 1.59 | 28.2 | 69.42 | 15 | 0 | 67.83 | 21.706 | 0 | Diesel-backup
2025-07-22 09:00 | 203 | 7 | Winter | 9 | 0 | -26.4 | 8.73 | 58.7 | 0 | 0 | 20.02 | 20.02 | 26.4 | 65.66 | 15 | 0 | 45.64 | 14.605 | 0 | Diesel-backup
2025-07-22 10:00 | 203 | 7 | Winter | 10 | 0 | -26.1 | 17.98 | 75.6 | 0 | 0 | 120 | 120 | 26.1 | 69.6 | 33.55 | 50.4 | 0 | 0 | 0 | Normal
2025-07-22 11:00 | 203 | 7 | Winter | 11 | 0 | -25.4 | 12.85 | 38.3 | 0 | 0 | 114.41 | 114.41 | 25.4 | 62.18 | 52.77 | 52.23 | 0 | 0 | 0 | Normal
2025-07-22 12:00 | 203 | 7 | Winter | 12 | 0 | -28.5 | 4.05 | 60.8 | 0 | 0 | 0.02 | 0.02 | 28.5 | 80.55 | 20.56 | -80.53 | 0 | 0 | 0 | Battery-supported
2025-07-22 13:00 | 203 | 7 | Winter | 13 | 0 | -23.6 | 17.01 | 29.6 | 0 | 0 | 120 | 120 | 23.6 | 64.51 | 40.98 | 55.49 | 0 | 0 | 0 | Normal
2025-07-22 14:00 | 203 | 7 | Winter | 14 | 0 | -23.5 | 15.42 | 80 | 0 | 0 | 120 | 120 | 23.5 | 66.75 | 60.57 | 53.25 | 0 | 0 | 0 | Normal
2025-07-22 15:00 | 203 | 7 | Winter | 15 | 0 | -23.8 | 2.75 | 74.9 | 0 | 0 | 0 | 0 | 23.8 | 67.98 | 33.38 | -67.98 | 0 | 0 | 0 | Battery-supported
2025-07-22 16:00 | 203 | 7 | Winter | 16 | 0 | -26.9 | 5.32 | 73.4 | 0 | 0 | 0.84 | 0.84 | 26.9 | 65.19 | 15 | -45.95 | 18.4 | 6.514 | 0 | Diesel-backup
2025-07-22 17:00 | 203 | 7 | Winter | 17 | 0 | -24.8 | 19.04 | 88.2 | 0 | 0 | 120 | 120 | 24.8 | 71.9 | 32.7 | 48.1 | 0 | 0 | 0 | Normal
2025-07-22 18:00 | 203 | 7 | Winter | 18 | 0 | -26.9 | 9.93 | 55.4 | 0 | 0 | 37.21 | 37.21 | 26.9 | 71.89 | 18.83 | -34.68 | 0 | 0 | 0 | Battery-supported
2025-07-22 19:00 | 203 | 7 | Winter | 19 | 0 | -25.7 | 16.95 | 39.5 | 0 | 0 | 120 | 120 | 25.7 | 67.7 | 38.08 | 52.3 | 0 | 0 | 0 | Normal
2025-07-22 20:00 | 203 | 7 | Winter | 20 | 0 | -20.2 | 1.69 | 46.3 | 0 | 0 | 0 | 0 | 20.2 | 64.82 | 15 | -57.69 | 7.13 | 2.628 | 0 | Diesel-backup
2025-07-22 21:00 | 203 | 7 | Winter | 21 | 0 | -24.7 | 1.15 | 10.8 | 0 | 0 | 0 | 0 | 24.7 | 59.47 | 15 | 0 | 59.47 | 19.03 | 0 | Diesel-backup
2025-07-22 22:00 | 203 | 7 | Winter | 22 | 0 | -27.6 | 14.38 | 67 | 0 | 0 | 120 | 120 | 27.6 | 62.65 | 36.1 | 57.35 | 0 | 0 | 0 | Normal
2025-07-22 23:00 | 203 | 7 | Winter | 23 | 0 | -24.5 | 6.79 | 19.4 | 0 | 0 | 4.98 | 4.98 | 24.5 | 56.92 | 15.33 | -51.94 | 0 | 0 | 0 | Battery-supported
2025-07-23 | 204 | 7 | Winter | 0 | 0 | -27.9 | 14.85 | 28.1 | 0 | 0 | 120 | 120 | 27.9 | 63.48 | 36.13 | 56.52 | 0 | 0 | 0 | Normal
2025-07-23 01:00 | 204 | 7 | Winter | 1 | 0 | -27.6 | 17.07 | 59.5 | 0 | 0 | 120 | 120 | 27.6 | 64.39 | 56.59 | 55.61 | 0 | 0 | 0 | Normal
2025-07-23 02:00 | 204 | 7 | Winter | 2 | 0 | -27.2 | 6.87 | 49.2 | 0 | 0 | 5.36 | 5.36 | 27.2 | 59 | 35.14 | -53.64 | 0 | 0 | 0 | Battery-supported
2025-07-23 03:00 | 204 | 7 | Winter | 3 | 0 | -25.9 | 9.36 | 32.5 | 0 | 0 | 28.16 | 28.16 | 25.9 | 62.15 | 21.54 | -33.99 | 0 | 0 | 0 | Battery-supported
2025-07-23 04:00 | 204 | 7 | Winter | 4 | 0 | -22.9 | 8.12 | 57.1 | 0 | 0 | 13.8 | 13.8 | 22.9 | 50.29 | 15 | -16.35 | 20.14 | 7.085 | 0 | Diesel-backup
2025-07-23 05:00 | 204 | 7 | Winter | 5 | 0 | -23.7 | 6.8 | 33.5 | 0 | 0 | 5.03 | 5.03 | 23.7 | 63.77 | 15 | 0 | 58.74 | 18.797 | 0 | Diesel-backup
2025-07-23 06:00 | 204 | 7 | Winter | 6 | 0 | -23.8 | 11.32 | 71 | 0 | 0 | 66.93 | 66.93 | 23.8 | 54.01 | 19.75 | 12.92 | 0 | 0 | 0 | Normal
2025-07-23 07:00 | 204 | 7 | Winter | 7 | 0 | -27.3 | 16.08 | 39.8 | 0 | 0 | 120 | 120 | 27.3 | 55.51 | 43.49 | 64.49 | 0 | 0 | 0 | Normal
2025-07-23 08:00 | 204 | 7 | Winter | 8 | 0 | -26.1 | 6.14 | 21.5 | 0 | 0 | 2.58 | 2.58 | 26.1 | 67.2 | 17.64 | -64.62 | 0 | 0 | 0 | Battery-supported
2025-07-23 09:00 | 204 | 7 | Winter | 9 | 0 | -24.3 | 6.11 | 26.9 | 0 | 0 | 2.49 | 2.49 | 24.3 | 68.32 | 15 | -6.6 | 59.23 | 18.954 | 0 | Diesel-backup
2025-07-23 10:00 | 204 | 7 | Winter | 10 | 0 | -26.3 | 6.91 | 73.1 | 0 | 0 | 5.55 | 5.55 | 26.3 | 68.23 | 15 | 0 | 62.68 | 20.058 | 0 | Diesel-backup
2025-07-23 11:00 | 204 | 7 | Winter | 11 | 0 | -25.5 | 13.83 | 46.7 | 0 | 0 | 120 | 120 | 25.5 | 71.87 | 32.71 | 48.13 | 0 | 0 | 0 | Normal
2025-07-23 12:00 | 204 | 7 | Winter | 12 | 0 | -24 | 17 | 32.4 | 0 | 0 | 120 | 120 | 24 | 66.18 | 52.52 | 53.82 | 0 | 0 | 0 | Normal
2025-07-23 13:00 | 204 | 7 | Winter | 13 | 0 | -25.7 | 8.03 | 43 | 0 | 0 | 13.01 | 13.01 | 25.7 | 68.04 | 30.51 | -55.03 | 0 | 0 | 0 | Battery-supported
2025-07-23 14:00 | 204 | 7 | Winter | 14 | 0 | -24.4 | 2.27 | 14.9 | 0 | 0 | 0 | 0 | 24.4 | 67.02 | 15 | -38.76 | 28.26 | 9.648 | 0 | Diesel-backup
2025-07-23 15:00 | 204 | 7 | Winter | 15 | 0 | -21.4 | 4.87 | 39.6 | 0 | 0 | 0.36 | 0.36 | 21.4 | 71.41 | 15 | 0 | 71.05 | 22.736 | 0 | Diesel-backup
2025-07-23 16:00 | 204 | 7 | Winter | 16 | 0 | -25.3 | 7.73 | 73.7 | 0 | 0 | 10.59 | 10.59 | 25.3 | 66.83 | 15 | 0 | 56.24 | 17.997 | 0 | Diesel-backup
2025-07-23 17:00 | 204 | 7 | Winter | 17 | 0 | -22.3 | 5.61 | 55 | 0 | 0 | 1.31 | 1.31 | 22.3 | 75.56 | 15 | 0 | 74.25 | 23.76 | 0 | Diesel-backup
2025-07-23 18:00 | 204 | 7 | Winter | 18 | 0 | -23.7 | 4.03 | 34.8 | 0 | 0 | 0.02 | 0.02 | 23.7 | 74.86 | 15 | 0 | 74.84 | 23.949 | 0 | Diesel-backup
2025-07-23 19:00 | 204 | 7 | Winter | 19 | 0 | -28.2 | 10.21 | 74.4 | 0 | 0 | 42.28 | 42.28 | 28.2 | 66.69 | 15 | 0 | 24.41 | 8.455 | 0 | Diesel-backup
2025-07-23 20:00 | 204 | 7 | Winter | 20 | 0 | -27.3 | 34.23 | 91.3 | 0 | 0 | 0 | 0 | 27.3 | 74.25 | 15 | 0 | 74.25 | 23.76 | 0 | Diesel-backup
2025-07-23 21:00 | 204 | 7 | Winter | 21 | 0 | -26.8 | 5.1 | 59.6 | 0 | 0 | 0.57 | 0.57 | 26.8 | 59.58 | 15 | 0 | 59.01 | 18.883 | 0 | Diesel-backup
2025-07-23 22:00 | 204 | 7 | Winter | 22 | 0 | -26.8 | 11.39 | 51.2 | 0 | 0 | 68.75 | 68.75 | 26.8 | 62.64 | 17.25 | 6.11 | 0 | 0 | 0 | Normal
2025-07-23 23:00 | 204 | 7 | Winter | 23 | 0 | -25.1 | 13.44 | 83.6 | 0 | 0 | 120 | 120 | 25.1 | 53.95 | 41.55 | 66.05 | 0 | 0 | 0 | Normal
2025-07-24 | 205 | 7 | Winter | 0 | 0 | -23.5 | 14.07 | 32 | 0 | 0 | 120 | 120 | 23.5 | 58.41 | 64.22 | 61.59 | 0 | 0 | 0 | Normal
2025-07-24 01:00 | 205 | 7 | Winter | 1 | 0 | -22.1 | 9.54 | 58.1 | 0 | 0 | 30.84 | 30.84 | 22.1 | 68.52 | 49.15 | -37.68 | 0 | 0 | 0 | Battery-supported
2025-07-24 02:00 | 205 | 7 | Winter | 2 | 0 | -24.2 | 4.18 | 56.1 | 0 | 0 | 0.04 | 0.04 | 24.2 | 56.36 | 26.62 | -56.32 | 0 | 0 | 0 | Battery-supported
2025-07-24 03:00 | 205 | 7 | Winter | 3 | 0 | -25.9 | 16.02 | 95.7 | 0 | 0 | 120 | 120 | 25.9 | 64.24 | 47.14 | 55.76 | 0 | 0 | 0 | Normal
2025-07-24 04:00 | 205 | 7 | Winter | 4 | 0 | -29.5 | 3.08 | 69.8 | 0 | 0 | 0 | 0 | 29.5 | 65.38 | 20.99 | -65.38 | 0 | 0 | 0 | Battery-supported
2025-07-24 05:00 | 205 | 7 | Winter | 5 | 0 | -24.7 | 8.94 | 59.9 | 0 | 0 | 22.53 | 22.53 | 24.7 | 57.96 | 15 | -14.97 | 20.46 | 7.19 | 0 | Diesel-backup
2025-07-24 06:00 | 205 | 7 | Winter | 6 | 0 | -24.8 | 8.39 | 34.1 | 0 | 0 | 16.37 | 16.37 | 24.8 | 65.05 | 15 | 0 | 48.68 | 15.578 | 0 | Diesel-backup
2025-07-24 07:00 | 205 | 7 | Winter | 7 | 0 | -24.5 | 4.43 | 99.2 | 0 | 0 | 0.11 | 0.11 | 24.5 | 58.06 | 15 | 0 | 57.95 | 18.544 | 0 | Diesel-backup
2025-07-24 08:00 | 205 | 7 | Winter | 8 | 0 | -20.3 | 6.91 | 72 | 0 | 0 | 5.55 | 5.55 | 20.3 | 63.55 | 15 | 0 | 58 | 18.56 | 0 | Diesel-backup
2025-07-24 09:00 | 205 | 7 | Winter | 9 | 0 | -22.2 | 13.8 | 42 | 0 | 0 | 120 | 120 | 22.2 | 66.55 | 34.67 | 53.45 | 0 | 0 | 0 | Normal
2025-07-24 10:00 | 205 | 7 | Winter | 10 | 0 | -23.2 | 8.94 | 50.1 | 0 | 0 | 22.53 | 22.53 | 23.2 | 71.48 | 15.09 | -48.95 | 0 | 0 | 0 | Battery-supported
2025-07-24 11:00 | 205 | 7 | Winter | 11 | 0 | -27 | 3.5 | 73.8 | 0 | 0 | 0 | 0 | 27 | 68.84 | 15 | -0.22 | 68.62 | 21.957 | 0 | Diesel-backup
2025-07-24 12:00 | 205 | 7 | Winter | 12 | 0 | -26 | 14.93 | 44.8 | 0 | 0 | 120 | 120 | 26 | 78.45 | 30.29 | 41.55 | 0 | 0 | 0 | Normal
2025-07-24 13:00 | 205 | 7 | Winter | 13 | 0 | -25.1 | 24.87 | 48.2 | 0 | 0 | 120 | 120 | 25.1 | 61.33 | 51.88 | 58.67 | 0 | 0 | 0 | Normal
2025-07-24 14:00 | 205 | 7 | Winter | 14 | 0 | -26.6 | 3.88 | 72.4 | 0 | 0 | 0.01 | 0.01 | 26.6 | 67.6 | 24.84 | -67.59 | 0 | 0 | 0 | Battery-supported
2025-07-24 15:00 | 205 | 7 | Winter | 15 | 0 | -23.8 | 9.4 | 12.2 | 0 | 0 | 28.75 | 28.75 | 23.8 | 72.15 | 15 | -24.61 | 18.79 | 6.642 | 0 | Diesel-backup
2025-07-24 16:00 | 205 | 7 | Winter | 16 | 0 | -24.1 | 9.62 | 28.9 | 0 | 0 | 32.08 | 32.08 | 24.1 | 65.22 | 15 | 0 | 33.14 | 11.108 | 0 | Diesel-backup
2025-07-24 17:00 | 205 | 7 | Winter | 17 | 0 | -27.3 | 3.8 | 73.9 | 0 | 0 | 0 | 0 | 27.3 | 71.38 | 15 | 0 | 71.38 | 22.842 | 0 | Diesel-backup
2025-07-24 18:00 | 205 | 7 | Winter | 18 | 0 | -22.3 | 19.39 | 53.2 | 0 | 0 | 120 | 120 | 22.3 | 61.84 | 36.4 | 58.16 | 0 | 0 | 0 | Normal
2025-07-24 19:00 | 205 | 7 | Winter | 19 | 0 | -24.7 | 9.74 | 38.6 | 0 | 0 | 34.01 | 34.01 | 24.7 | 62.41 | 25.04 | -28.4 | 0 | 0 | 0 | Battery-supported
2025-07-24 20:00 | 205 | 7 | Winter | 20 | 0 | -28.7 | 16.33 | 39 | 0 | 0 | 120 | 120 | 28.7 | 70.02 | 43.44 | 49.98 | 0 | 0 | 0 | Normal
2025-07-24 21:00 | 205 | 7 | Winter | 21 | 0 | -25 | 11.8 | 68.5 | 0 | 0 | 80.03 | 80.03 | 25 | 63.41 | 49.55 | 16.62 | 0 | 0 | 0 | Normal
2025-07-24 22:00 | 205 | 7 | Winter | 22 | 0 | -24.3 | 18.98 | 21.3 | 0 | 0 | 120 | 120 | 24.3 | 57.27 | 72.64 | 62.73 | 0 | 0 | 0 | Normal
2025-07-24 23:00 | 205 | 7 | Winter | 23 | 0 | -22.8 | 11.7 | 52.2 | 0 | 0 | 77.17 | 77.17 | 22.8 | 57.83 | 79.75 | 19.34 | 0 | 0 | 0 | Normal
2025-07-25 | 206 | 7 | Winter | 0 | 0 | -25.6 | 7.4 | 82.7 | 0 | 0 | 8.3 | 8.3 | 25.6 | 58.98 | 59.48 | -50.68 | 0 | 0 | 0 | Battery-supported
2025-07-25 01:00 | 206 | 7 | Winter | 1 | 0 | -23.1 | 13.19 | 84 | 0 | 0 | 120 | 120 | 23.1 | 61.21 | 81.12 | 58.79 | 0 | 0 | 0 | Normal
2025-07-25 02:00 | 206 | 7 | Winter | 2 | 0 | -24.5 | 5.71 | 77.5 | 0 | 0 | 1.51 | 1.51 | 24.5 | 53.48 | 60.33 | -51.97 | 0 | 0 | 0 | Battery-supported
2025-07-25 03:00 | 206 | 7 | Winter | 3 | 0 | -27.8 | 13.94 | 51.5 | 0 | 0 | 120 | 120 | 27.8 | 62.74 | 81.4 | 57.26 | 0 | 0 | 0 | Normal
2025-07-25 04:00 | 206 | 7 | Winter | 4 | 0 | -28 | 5.09 | 48.1 | 0 | 0 | 0.56 | 0.56 | 28 | 61.99 | 56.83 | -61.43 | 0 | 0 | 0 | Battery-supported
2025-07-25 05:00 | 206 | 7 | Winter | 5 | 0 | -22.4 | 9.2 | 14.9 | 0 | 0 | 25.92 | 25.92 | 22.4 | 54.15 | 45.54 | -28.23 | 0 | 0 | 0 | Battery-supported
2025-07-25 06:00 | 206 | 7 | Winter | 6 | 0 | -22.2 | 8.12 | 61.3 | 0 | 0 | 13.8 | 13.8 | 22.2 | 62.45 | 26.08 | -48.65 | 0 | 0 | 0 | Battery-supported
2025-07-25 07:00 | 206 | 7 | Winter | 7 | 0 | -24.2 | 11.21 | 30.3 | 0 | 0 | 64.15 | 64.15 | 24.2 | 52.65 | 30.31 | 11.5 | 0 | 0 | 0 | Normal
2025-07-25 08:00 | 206 | 7 | Winter | 8 | 0 | -21.6 | 20.73 | 88.4 | 0 | 0 | 120 | 120 | 21.6 | 66.44 | 50.02 | 53.56 | 0 | 0 | 0 | Normal
2025-07-25 09:00 | 206 | 7 | Winter | 9 | 0 | -22.5 | 6.76 | 16.4 | 0 | 0 | 4.85 | 4.85 | 22.5 | 67.7 | 24.88 | -62.85 | 0 | 0 | 0 | Battery-supported
2025-07-25 10:00 | 206 | 7 | Winter | 10 | 0 | -23.4 | 15.73 | 69 | 0 | 0 | 120 | 120 | 23.4 | 65.21 | 45.04 | 54.79 | 0 | 0 | 0 | Normal
2025-07-25 11:00 | 206 | 7 | Winter | 11 | 0 | -26.9 | 19.33 | 58 | 0 | 0 | 120 | 120 | 26.9 | 78.07 | 60.47 | 41.93 | 0 | 0 | 0 | Normal
2025-07-25 12:00 | 206 | 7 | Winter | 12 | 0 | -21.1 | 15.46 | 63.5 | 0 | 0 | 120 | 120 | 21.1 | 66.21 | 80.27 | 53.79 | 0 | 0 | 0 | Normal
2025-07-25 13:00 | 206 | 7 | Winter | 13 | 0 | -23.7 | 11.16 | 45.4 | 0 | 0 | 62.91 | 62.91 | 23.7 | 64.21 | 79.75 | -1.3 | 0 | 0 | 0 | Battery-supported
2025-07-25 14:00 | 206 | 7 | Winter | 14 | 0 | -25.7 | 10.83 | 29.9 | 0 | 0 | 55.12 | 55.12 | 25.7 | 71.54 | 73.18 | -16.42 | 0 | 0 | 0 | Battery-supported
2025-07-25 15:00 | 206 | 7 | Winter | 15 | 0 | -26.3 | 6.49 | 22.5 | 0 | 0 | 3.74 | 3.74 | 26.3 | 67.8 | 47.55 | -64.06 | 0 | 0 | 0 | Battery-supported
2025-07-25 16:00 | 206 | 7 | Winter | 16 | 0 | -24.3 | 3.12 | 55.5 | 0 | 0 | 0 | 0 | 24.3 | 66.06 | 21.13 | -66.06 | 0 | 0 | 0 | Battery-supported
2025-07-25 17:00 | 206 | 7 | Winter | 17 | 0 | -28.5 | 9.95 | 27 | 0 | 0 | 37.56 | 37.56 | 28.5 | 76.39 | 15 | -15.32 | 23.51 | 8.169 | 0 | Diesel-backup
2025-07-25 18:00 | 206 | 7 | Winter | 18 | 0 | -23.3 | 20.28 | 54.8 | 0 | 0 | 120 | 120 | 23.3 | 68.85 | 33.82 | 51.15 | 0 | 0 | 0 | Normal
2025-07-25 19:00 | 206 | 7 | Winter | 19 | 0 | -27 | 21.88 | 28.8 | 0 | 0 | 120 | 120 | 27 | 74.68 | 50.5 | 45.32 | 0 | 0 | 0 | Normal
2025-07-25 20:00 | 206 | 7 | Winter | 20 | 0 | -24.1 | 3.62 | 55.3 | 0 | 0 | 0 | 0 | 24.1 | 57.55 | 27.48 | -57.55 | 0 | 0 | 0 | Battery-supported
2025-07-25 21:00 | 206 | 7 | Winter | 21 | 0 | -26 | 21.5 | 69.5 | 0 | 0 | 120 | 120 | 26 | 62.82 | 48.52 | 57.18 | 0 | 0 | 0 | Normal
2025-07-25 22:00 | 206 | 7 | Winter | 22 | 0 | -25.5 | 13.54 | 19.6 | 0 | 0 | 120 | 120 | 25.5 | 66.98 | 68.03 | 53.02 | 0 | 0 | 0 | Normal
2025-07-25 23:00 | 206 | 7 | Winter | 23 | 0 | -26.5 | 12.66 | 87.4 | 0 | 0 | 107.57 | 107.57 | 26.5 | 57.43 | 86.49 | 50.14 | 0 | 0 | 0 | Normal
2025-07-26 | 207 | 7 | Winter | 0 | 0 | -25.2 | 20.19 | 52.9 | 0 | 0 | 120 | 120 | 25.2 | 61.3 | 95 | 23.14 | 0 | 0 | 0 | Normal
2025-07-26 01:00 | 207 | 7 | Winter | 1 | 0 | -20.7 | 17 | 90 | 0 | 0 | 120 | 120 | 20.7 | 55.22 | 95 | 0 | 0 | 0 | 0 | Normal
2025-07-26 02:00 | 207 | 7 | Winter | 2 | 0 | -21.8 | 5.03 | 20.8 | 0 | 0 | 0.5 | 0.5 | 21.8 | 60.1 | 71.16 | -59.6 | 0 | 0 | 0 | Battery-supported
2025-07-26 03:00 | 207 | 7 | Winter | 3 | 0 | -24.1 | 6.01 | 52.9 | 0 | 0 | 2.21 | 2.21 | 24.1 | 57.35 | 49.1 | -55.14 | 0 | 0 | 0 | Battery-supported
2025-07-26 04:00 | 207 | 7 | Winter | 4 | 0 | -24.9 | 2.83 | 49.3 | 0 | 0 | 0 | 0 | 24.9 | 63.51 | 23.7 | -63.51 | 0 | 0 | 0 | Battery-supported
2025-07-26 05:00 | 207 | 7 | Winter | 5 | 0 | -23 | 12.33 | 20 | 0 | 0 | 96.36 | 96.36 | 23 | 57.28 | 38.08 | 39.08 | 0 | 0 | 0 | Normal
2025-07-26 06:00 | 207 | 7 | Winter | 6 | 0 | -22.4 | 5.44 | 44.8 | 0 | 0 | 1.02 | 1.02 | 22.4 | 68.71 | 15 | -57.7 | 9.99 | 3.643 | 0 | Diesel-backup
2025-07-26 07:00 | 207 | 7 | Winter | 7 | 0 | -26.7 | 7.23 | 59.6 | 0 | 0 | 7.26 | 7.26 | 26.7 | 63.6 | 15 | 0 | 56.34 | 18.029 | 0 | Diesel-backup
2025-07-26 08:00 | 207 | 7 | Winter | 8 | 0 | -25 | 18.84 | 51.5 | 0 | 0 | 120 | 120 | 25 | 77.61 | 30.6 | 42.39 | 0 | 0 | 0 | Normal
2025-07-26 09:00 | 207 | 7 | Winter | 9 | 0 | -28.8 | 13.3 | 38.7 | 0 | 0 | 120 | 120 | 28.8 | 74.84 | 47.22 | 45.16 | 0 | 0 | 0 | Normal
2025-07-26 10:00 | 207 | 7 | Winter | 10 | 0 | -22.4 | 13.5 | 27.3 | 0 | 0 | 120 | 120 | 22.4 | 64.34 | 67.7 | 55.66 | 0 | 0 | 0 | Normal
2025-07-26 11:00 | 207 | 7 | Winter | 11 | 0 | -20.3 | 29.68 | 29.8 | 0 | 0 | 0 | 0 | 20.3 | 63.92 | 42.13 | -63.92 | 0 | 0 | 0 | Battery-supported
2025-07-26 12:00 | 207 | 7 | Winter | 12 | 0 | -24.7 | 0.81 | 57.7 | 0 | 0 | 0 | 0 | 24.7 | 69.71 | 15 | -67.83 | 1.88 | 0.704 | 0 | Diesel-backup
2025-07-26 13:00 | 207 | 7 | Winter | 13 | 0 | -29.5 | 5.65 | 11.2 | 0 | 0 | 1.39 | 1.39 | 29.5 | 63.77 | 15 | 0 | 62.38 | 19.962 | 0 | Diesel-backup
2025-07-26 14:00 | 207 | 7 | Winter | 14 | 0 | -23.5 | 8.09 | 62.4 | 0 | 0 | 13.53 | 13.53 | 23.5 | 70.8 | 15 | 0 | 57.27 | 18.326 | 0 | Diesel-backup
2025-07-26 15:00 | 207 | 7 | Winter | 15 | 0 | -26.8 | 5.9 | 35 | 0 | 0 | 1.93 | 1.93 | 26.8 | 70.93 | 15 | 0 | 69 | 22.08 | 0 | Diesel-backup
2025-07-26 16:00 | 207 | 7 | Winter | 16 | 0 | -26.3 | 16.24 | 89 | 0 | 0 | 120 | 120 | 26.3 | 71.94 | 32.69 | 48.06 | 0 | 0 | 0 | Normal
2025-07-26 17:00 | 207 | 7 | Winter | 17 | 0 | -23.5 | 8.69 | 41.7 | 0 | 0 | 19.57 | 19.57 | 23.5 | 69.43 | 15 | -44.22 | 5.64 | 2.091 | 0 | Diesel-backup
2025-07-26 18:00 | 207 | 7 | Winter | 18 | 0 | -24.3 | 4.66 | 19.3 | 0 | 0 | 0.22 | 0.22 | 24.3 | 62.58 | 15 | 0 | 62.36 | 19.955 | 0 | Diesel-backup
2025-07-26 19:00 | 207 | 7 | Winter | 19 | 0 | -25.9 | 11.7 | 66.2 | 0 | 0 | 77.17 | 77.17 | 25.9 | 69.7 | 17.75 | 7.47 | 0 | 0 | 0 | Normal
2025-07-26 20:00 | 207 | 7 | Winter | 20 | 0 | -26.3 | 12.88 | 66.7 | 0 | 0 | 115.51 | 115.51 | 26.3 | 69.78 | 34.58 | 45.73 | 0 | 0 | 0 | Normal
2025-07-26 21:00 | 207 | 7 | Winter | 21 | 0 | -24.6 | 4.93 | 17.7 | 0 | 0 | 0.41 | 0.41 | 24.6 | 55.07 | 15 | -48.94 | 5.72 | 2.117 | 0 | Diesel-backup
2025-07-26 22:00 | 207 | 7 | Winter | 22 | 0 | -25.7 | 8.96 | 58.8 | 0 | 0 | 22.78 | 22.78 | 25.7 | 66.95 | 15 | 0 | 44.17 | 14.181 | 0 | Diesel-backup
2025-07-26 23:00 | 207 | 7 | Winter | 23 | 0 | -27.3 | 13.06 | 12 | 0 | 0 | 120 | 120 | 27.3 | 70.24 | 33.31 | 49.76 | 0 | 0 | 0 | Normal
2025-07-27 | 208 | 7 | Winter | 0 | 0.59 | -24.8 | 19.43 | 57.4 | 0 | 0 | 120 | 120 | 24.8 | 58.7 | 55.87 | 61.3 | 0 | 0 | 0 | Normal
2025-07-27 01:00 | 208 | 7 | Winter | 1 | 0.59 | -23.7 | 6.31 | 74.5 | 0 | 0 | 3.11 | 3.11 | 23.7 | 61.18 | 32.64 | -58.07 | 0 | 0 | 0 | Battery-supported
2025-07-27 02:00 | 208 | 7 | Winter | 2 | 0.59 | -25.2 | 13.9 | 92 | 0 | 0 | 120 | 120 | 25.2 | 60.4 | 54.57 | 59.6 | 0 | 0 | 0 | Normal
2025-07-27 03:00 | 208 | 7 | Winter | 3 | 0.59 | -28.3 | 6.94 | 39.8 | 0 | 0 | 5.7 | 5.7 | 28.3 | 62.28 | 31.94 | -56.58 | 0 | 0 | 0 | Battery-supported
2025-07-27 04:00 | 208 | 7 | Winter | 4 | 0.59 | -23.4 | 10.44 | 42.2 | 232.6 | 11.86 | 46.78 | 58.64 | 23.4 | 57.03 | 32.54 | 1.61 | 0 | 0 | 0 | Normal
2025-07-27 05:00 | 208 | 7 | Winter | 5 | 0.59 | -31.9 | 5.24 | 28.5 | 512.8 | 26.15 | 0.74 | 26.89 | 31.9 | 62.27 | 18.38 | -35.38 | 0 | 0 | 0 | Battery-supported
2025-07-27 06:00 | 208 | 7 | Winter | 6 | 0.59 | -27.1 | 13.65 | 48.7 | 289.6 | 14.77 | 120 | 134.77 | 27.1 | 63.96 | 44.44 | 70.81 | 0 | 0 | 0 | Normal
2025-07-27 07:00 | 208 | 7 | Winter | 7 | 0.59 | -27.6 | 17.59 | 61.5 | 0 | 0 | 120 | 120 | 27.6 | 60.45 | 66.36 | 59.55 | 0 | 0 | 0 | Normal
2025-07-27 08:00 | 208 | 7 | Winter | 8 | 0.59 | -26 | 9.2 | 40.9 | 0 | 0 | 25.92 | 25.92 | 26 | 71.79 | 48.01 | -45.87 | 0 | 0 | 0 | Battery-supported
2025-07-27 09:00 | 208 | 7 | Winter | 9 | 0.59 | -25 | 8.48 | 97.4 | 0 | 0 | 17.29 | 17.29 | 25 | 66.59 | 28.29 | -49.3 | 0 | 0 | 0 | Battery-supported
2025-07-27 10:00 | 208 | 7 | Winter | 10 | 0.59 | -23.6 | 7.99 | 16.8 | 0 | 0 | 12.67 | 12.67 | 23.6 | 62.26 | 15 | -33.22 | 16.37 | 5.838 | 0 | Diesel-backup
2025-07-27 11:00 | 208 | 7 | Winter | 11 | 0.59 | -27.4 | 4.29 | 14 | 358.6 | 18.29 | 0.07 | 18.36 | 27.4 | 68 | 15 | 0 | 49.64 | 15.885 | 0 | Diesel-backup
2025-07-27 12:00 | 208 | 7 | Winter | 12 | 0.59 | -24.3 | 15.23 | 62.9 | 346.5 | 17.67 | 120 | 137.67 | 24.3 | 69.05 | 40.25 | 68.62 | 0 | 0 | 0 | Normal
2025-07-27 13:00 | 208 | 7 | Winter | 13 | 0.59 | -24.8 | 19.15 | 66.9 | 199.8 | 10.19 | 120 | 130.19 | 24.8 | 66.73 | 63.61 | 63.46 | 0 | 0 | 0 | Normal
2025-07-27 14:00 | 208 | 7 | Winter | 14 | 0.59 | -28.6 | 6.08 | 75.7 | 0 | 0 | 2.4 | 2.4 | 28.6 | 68.21 | 37.28 | -65.81 | 0 | 0 | 0 | Battery-supported
2025-07-27 15:00 | 208 | 7 | Winter | 15 | 0.59 | -20.2 | 11.29 | 49.8 | 0 | 0 | 66.16 | 66.16 | 20.2 | 69.93 | 35.77 | -3.77 | 0 | 0 | 0 | Battery-supported
2025-07-27 16:00 | 208 | 7 | Winter | 16 | 0.59 | -27.2 | 13.44 | 48.9 | 0 | 0 | 120 | 120 | 27.2 | 65.06 | 55.99 | 54.94 | 0 | 0 | 0 | Normal
2025-07-27 17:00 | 208 | 7 | Winter | 17 | 0.59 | -22.8 | 6.86 | 68.6 | 0 | 0 | 5.31 | 5.31 | 22.8 | 71.3 | 29.6 | -65.99 | 0 | 0 | 0 | Battery-supported
2025-07-27 18:00 | 208 | 7 | Winter | 18 | 0.59 | -22.6 | 21.81 | 51.1 | 281.2 | 14.34 | 120 | 134.34 | 22.6 | 70.4 | 53.13 | 63.94 | 0 | 0 | 0 | Normal
2025-07-27 19:00 | 208 | 7 | Winter | 19 | 0.59 | -22.7 | 11.41 | 74.5 | 287.4 | 14.66 | 69.27 | 83.93 | 22.7 | 69.53 | 58.42 | 14.4 | 0 | 0 | 0 | Normal
2025-07-27 20:00 | 208 | 7 | Winter | 20 | 0.59 | -24.4 | 3.61 | 39 | 240.8 | 12.28 | 0 | 12.28 | 24.4 | 70.74 | 35.04 | -58.46 | 0 | 0 | 0 | Battery-supported
2025-07-27 21:00 | 208 | 7 | Winter | 21 | 0.59 | -21.5 | 18.13 | 41.9 | 0 | 0 | 120 | 120 | 21.5 | 53.7 | 59.44 | 66.3 | 0 | 0 | 0 | Normal
2025-07-27 22:00 | 208 | 7 | Winter | 22 | 0.59 | -26.9 | 9.42 | 19.2 | 0 | 0 | 29.04 | 29.04 | 26.9 | 59.98 | 47.06 | -30.94 | 0 | 0 | 0 | Battery-supported
2025-07-27 23:00 | 208 | 7 | Winter | 23 | 0.59 | -23.9 | 7.63 | 81.4 | 0 | 0 | 9.86 | 9.86 | 23.9 | 66.88 | 24.25 | -57.02 | 0 | 0 | 0 | Battery-supported
2025-07-28 | 209 | 7 | Winter | 0 | 1.37 | -25.3 | 14.56 | 24.7 | 0 | 0 | 120 | 120 | 25.3 | 64.82 | 44.56 | 55.18 | 0 | 0 | 0 | Normal
2025-07-28 01:00 | 209 | 7 | Winter | 1 | 1.37 | -25.9 | 7.01 | 54.7 | 385.6 | 19.67 | 6.05 | 25.72 | 25.9 | 63.2 | 29.57 | -37.48 | 0 | 0 | 0 | Battery-supported
2025-07-28 02:00 | 209 | 7 | Winter | 2 | 1.37 | -23.8 | 21.03 | 73.7 | 0 | 0 | 120 | 120 | 23.8 | 56.83 | 52.82 | 63.17 | 0 | 0 | 0 | Normal
2025-07-28 03:00 | 209 | 7 | Winter | 3 | 1.37 | -22.8 | 18.48 | 28.6 | 0 | 0 | 120 | 120 | 22.8 | 54.57 | 76.89 | 65.43 | 0 | 0 | 0 | Normal
2025-07-28 04:00 | 209 | 7 | Winter | 4 | 1.37 | -26.3 | 22.65 | 88.9 | 191.1 | 9.75 | 120 | 129.75 | 26.3 | 56.97 | 95 | 49.2 | 0 | 0 | 0 | Normal
2025-07-28 05:00 | 209 | 7 | Winter | 5 | 1.37 | -24.1 | 28.73 | 42.5 | 0 | 0 | 0 | 0 | 24.1 | 56.64 | 72.34 | -56.64 | 0 | 0 | 0 | Battery-supported
2025-07-28 06:00 | 209 | 7 | Winter | 6 | 1.37 | -26 | 13.31 | 24.8 | 199 | 10.15 | 120 | 130.15 | 26 | 60.25 | 95 | 61.57 | 0 | 0 | 0 | Normal
2025-07-28 07:00 | 209 | 7 | Winter | 7 | 1.37 | -28.2 | 9.95 | 77.9 | 122.9 | 6.27 | 37.56 | 43.83 | 28.2 | 64.2 | 86.85 | -20.37 | 0 | 0 | 0 | Battery-supported
2025-07-28 08:00 | 209 | 7 | Winter | 8 | 1.37 | -26.8 | 6.83 | 36 | 0 | 0 | 5.17 | 5.17 | 26.8 | 74.95 | 58.94 | -69.78 | 0 | 0 | 0 | Battery-supported
2025-07-28 09:00 | 209 | 7 | Winter | 9 | 1.37 | -26.9 | 14.06 | 25 | 441.6 | 22.52 | 120 | 142.52 | 26.9 | 78.79 | 82.39 | 63.73 | 0 | 0 | 0 | Normal
2025-07-28 10:00 | 209 | 7 | Winter | 10 | 1.37 | -27.6 | 28.29 | 52.9 | 0 | 0 | 0 | 0 | 27.6 | 76.96 | 51.61 | -76.96 | 0 | 0 | 0 | Battery-supported
2025-07-28 11:00 | 209 | 7 | Winter | 11 | 1.37 | -24.9 | 4.31 | 80.2 | 0 | 0 | 0.07 | 0.07 | 24.9 | 63.19 | 26.36 | -63.12 | 0 | 0 | 0 | Battery-supported
2025-07-28 12:00 | 209 | 7 | Winter | 12 | 1.37 | -25 | 11.98 | 77.8 | 273.1 | 13.93 | 85.35 | 99.28 | 25 | 65.31 | 38.86 | 33.97 | 0 | 0 | 0 | Normal
2025-07-28 13:00 | 209 | 7 | Winter | 13 | 1.37 | -28.7 | 3.57 | 92.3 | 0 | 0 | 0 | 0 | 28.7 | 68.23 | 15 | -59.65 | 8.58 | 3.144 | 0 | Diesel-backup
2025-07-28 14:00 | 209 | 7 | Winter | 14 | 1.37 | -28.4 | 3.46 | 100 | 0 | 0 | 0 | 0 | 28.4 | 76.15 | 15 | 0 | 76.15 | 24.368 | 0 | Diesel-backup
2025-07-28 15:00 | 209 | 7 | Winter | 15 | 1.37 | -23.4 | 19.5 | 73.6 | 243.3 | 12.41 | 120 | 132.41 | 23.4 | 69.94 | 37.99 | 62.47 | 0 | 0 | 0 | Normal
2025-07-28 16:00 | 209 | 7 | Winter | 16 | 1.37 | -25.8 | 17.75 | 69.1 | 0 | 0 | 120 | 120 | 25.8 | 67.26 | 57.4 | 52.74 | 0 | 0 | 0 | Normal
2025-07-28 17:00 | 209 | 7 | Winter | 17 | 1.37 | -23 | 6.6 | 64.3 | 153 | 7.8 | 4.17 | 11.97 | 23 | 66 | 35.79 | -54.03 | 0 | 0 | 0 | Battery-supported
2025-07-28 18:00 | 209 | 7 | Winter | 18 | 1.37 | -21.7 | 4.86 | 44.9 | 162.2 | 8.27 | 0.35 | 8.62 | 21.7 | 66.05 | 15 | -51.96 | 5.47 | 2.026 | 0 | Diesel-backup
2025-07-28 19:00 | 209 | 7 | Winter | 19 | 1.37 | -26.1 | 23.15 | 31.2 | 0 | 0 | 120 | 120 | 26.1 | 71.78 | 32.74 | 48.22 | 0 | 0 | 0 | Normal
2025-07-28 20:00 | 209 | 7 | Winter | 20 | 1.37 | -26.4 | 5.11 | 96 | 160.2 | 8.17 | 0.58 | 8.75 | 26.4 | 74.86 | 15 | -44.36 | 21.75 | 7.607 | 0 | Diesel-backup
2025-07-28 21:00 | 209 | 7 | Winter | 21 | 1.37 | -19.6 | 4.05 | 42.7 | 0 | 0 | 0.02 | 0.02 | 19.6 | 55.93 | 15 | 0 | 55.91 | 17.891 | 0 | Diesel-backup
2025-07-28 22:00 | 209 | 7 | Winter | 22 | 1.37 | -22.7 | 5.22 | 75.2 | 0 | 0 | 0.71 | 0.71 | 22.7 | 57.37 | 15 | 0 | 56.66 | 18.131 | 0 | Diesel-backup
2025-07-28 23:00 | 209 | 7 | Winter | 23 | 1.37 | -24.6 | 12.71 | 36.3 | 475.4 | 24.25 | 109.34 | 133.59 | 24.6 | 61.75 | 41.44 | 71.84 | 0 | 0 | 0 | Normal
2025-07-29 | 210 | 7 | Winter | 0 | 1.86 | -26 | 30.95 | 48.8 | 54.7 | 2.79 | 0 | 2.79 | 26 | 60.67 | 18.29 | -57.88 | 0 | 0 | 0 | Battery-supported
2025-07-29 01:00 | 210 | 7 | Winter | 1 | 1.86 | -25.5 | 6.9 | 64.8 | 326.4 | 16.65 | 5.5 | 22.15 | 25.5 | 62.61 | 15 | -8.21 | 32.25 | 10.845 | 0 | Diesel-backup
2025-07-29 02:00 | 210 | 7 | Winter | 2 | 1.86 | -27.3 | 19.35 | 87.2 | 0 | 0 | 120 | 120 | 27.3 | 62.06 | 36.32 | 57.94 | 0 | 0 | 0 | Normal
2025-07-29 03:00 | 210 | 7 | Winter | 3 | 1.86 | -23.2 | 10.74 | 6 | 0 | 0 | 53.12 | 53.12 | 23.2 | 63.47 | 32.18 | -10.35 | 0 | 0 | 0 | Battery-supported
2025-07-29 04:00 | 210 | 7 | Winter | 4 | 1.86 | -27.2 | 2.28 | 47.3 | 243.1 | 12.4 | 0 | 12.4 | 27.2 | 67.82 | 15 | -42.95 | 12.47 | 4.508 | 0 | Diesel-backup
2025-07-29 05:00 | 210 | 7 | Winter | 5 | 1.86 | -23.4 | 7.04 | 66.9 | 243.4 | 12.41 | 6.21 | 18.62 | 23.4 | 58.12 | 15 | 0 | 39.5 | 12.918 | 0 | Diesel-backup
2025-07-29 06:00 | 210 | 7 | Winter | 6 | 1.86 | -26.9 | 17.85 | 78.8 | 0 | 0 | 120 | 120 | 26.9 | 70.72 | 33.14 | 49.28 | 0 | 0 | 0 | Normal
2025-07-29 07:00 | 210 | 7 | Winter | 7 | 1.86 | -28.5 | 17.31 | 13.9 | 0 | 0 | 120 | 120 | 28.5 | 64.81 | 53.44 | 55.19 | 0 | 0 | 0 | Normal
2025-07-29 08:00 | 210 | 7 | Winter | 8 | 1.86 | -27.2 | 6.39 | 35.4 | 427.2 | 21.79 | 3.38 | 25.17 | 27.2 | 72.38 | 34.56 | -47.21 | 0 | 0 | 0 | Battery-supported
2025-07-29 09:00 | 210 | 7 | Winter | 9 | 1.86 | -31.9 | 15.16 | 77.6 | 96.6 | 4.93 | 120 | 124.93 | 31.9 | 81.15 | 50.67 | 43.78 | 0 | 0 | 0 | Normal
2025-07-29 10:00 | 210 | 7 | Winter | 10 | 1.86 | -26.3 | 9.29 | 56.3 | 0 | 0 | 27.17 | 27.17 | 26.3 | 77.89 | 30.38 | -50.72 | 0 | 0 | 0 | Battery-supported
2025-07-29 11:00 | 210 | 7 | Winter | 11 | 1.86 | -26.2 | 12.42 | 91.3 | 0 | 0 | 99.34 | 99.34 | 26.2 | 74.41 | 39.56 | 24.93 | 0 | 0 | 0 | Normal
2025-07-29 12:00 | 210 | 7 | Winter | 12 | 1.86 | -23.7 | 19.96 | 67.7 | 323 | 16.47 | 120 | 136.47 | 23.7 | 68.51 | 64.57 | 67.96 | 0 | 0 | 0 | Normal
2025-07-29 13:00 | 210 | 7 | Winter | 13 | 1.86 | -29.3 | 6.56 | 47.2 | 0 | 0 | 4.01 | 4.01 | 29.3 | 71.28 | 37.66 | -67.27 | 0 | 0 | 0 | Battery-supported
2025-07-29 14:00 | 210 | 7 | Winter | 14 | 1.86 | -22.2 | 7.85 | 8.7 | 0 | 0 | 11.52 | 11.52 | 22.2 | 66.96 | 15.48 | -55.44 | 0 | 0 | 0 | Battery-supported
2025-07-29 15:00 | 210 | 7 | Winter | 15 | 1.86 | -22.5 | 20.17 | 47.5 | 148.7 | 7.58 | 120 | 127.58 | 22.5 | 68.39 | 37.27 | 59.19 | 0 | 0 | 0 | Normal
2025-07-29 16:00 | 210 | 7 | Winter | 16 | 1.86 | -21.2 | 29.13 | 41.7 | 400.1 | 20.41 | 0 | 20.41 | 21.2 | 66.36 | 18.89 | -45.95 | 0 | 0 | 0 | Battery-supported
2025-07-29 17:00 | 210 | 7 | Winter | 17 | 1.86 | -23.8 | 16.6 | 84.9 | 0 | 0 | 120 | 120 | 23.8 | 66.38 | 38.62 | 53.62 | 0 | 0 | 0 | Normal
2025-07-29 18:00 | 210 | 7 | Winter | 18 | 1.86 | -21.2 | 11.97 | 17 | 0 | 0 | 85.05 | 85.05 | 21.2 | 61.66 | 47.23 | 23.39 | 0 | 0 | 0 | Normal
2025-07-29 19:00 | 210 | 7 | Winter | 19 | 1.86 | -26.5 | 16.51 | 52 | 297.6 | 15.18 | 120 | 135.18 | 26.5 | 70.78 | 70.92 | 64.4 | 0 | 0 | 0 | Normal
2025-07-29 20:00 | 210 | 7 | Winter | 20 | 1.86 | -21.7 | 7.01 | 59.5 | 208.6 | 10.64 | 6.05 | 16.69 | 21.7 | 62.51 | 52.6 | -45.82 | 0 | 0 | 0 | Battery-supported
2025-07-29 21:00 | 210 | 7 | Winter | 21 | 1.86 | -25 | 10.37 | 89.1 | 0 | 0 | 45.38 | 45.38 | 25 | 53.69 | 49.27 | -8.31 | 0 | 0 | 0 | Battery-supported
2025-07-29 22:00 | 210 | 7 | Winter | 22 | 1.86 | -27.1 | 3.43 | 65.3 | 0 | 0 | 0 | 0 | 27.1 | 58.94 | 25.7 | -58.94 | 0 | 0 | 0 | Battery-supported
2025-07-29 23:00 | 210 | 7 | Winter | 23 | 1.86 | -26.1 | 7.11 | 53.5 | 380.3 | 19.4 | 6.58 | 25.98 | 26.1 | 59.67 | 15 | -26.74 | 6.95 | 2.562 | 0 | Diesel-backup
2025-07-30 | 211 | 7 | Winter | 0 | 2.25 | -23.9 | 12.87 | 65.3 | 0 | 0 | 115.14 | 115.14 | 23.9 | 56.09 | 36.73 | 59.05 | 0 | 0 | 0 | Normal
2025-07-30 01:00 | 211 | 7 | Winter | 1 | 2.25 | -26.1 | 11.27 | 53.7 | 0 | 0 | 65.66 | 65.66 | 26.1 | 62.29 | 37.97 | 3.37 | 0 | 0 | 0 | Normal
2025-07-30 02:00 | 211 | 7 | Winter | 2 | 2.25 | -23.9 | 1.72 | 61 | 63.8 | 3.25 | 0 | 3.25 | 23.9 | 54.15 | 17.61 | -50.9 | 0 | 0 | 0 | Battery-supported
2025-07-30 03:00 | 211 | 7 | Winter | 3 | 2.25 | -29 | 8.61 | 61.3 | 354.4 | 18.07 | 18.68 | 36.75 | 29 | 59.67 | 15 | -6.53 | 16.39 | 5.846 | 0 | Diesel-backup
2025-07-30 04:00 | 211 | 7 | Winter | 4 | 2.25 | -30.1 | 11.13 | 30.6 | 85.4 | 4.36 | 62.17 | 66.53 | 30.1 | 70.39 | 15 | 0 | 3.86 | 1.438 | 0 | Diesel-backup
2025-07-30 05:00 | 211 | 7 | Winter | 5 | 2.25 | -22.7 | 11.39 | 26.6 | 0 | 0 | 68.75 | 68.75 | 22.7 | 61.67 | 17.61 | 7.08 | 0 | 0 | 0 | Normal
2025-07-30 06:00 | 211 | 7 | Winter | 6 | 2.25 | -24 | 3.99 | 65.8 | 0 | 0 | 0.02 | 0.02 | 24 | 60.46 | 15 | -6.51 | 53.93 | 17.256 | 0 | Diesel-backup
2025-07-30 07:00 | 211 | 7 | Winter | 7 | 2.25 | -28.4 | 15.32 | 54 | 299.9 | 15.29 | 120 | 135.29 | 28.4 | 69.22 | 39.31 | 66.07 | 0 | 0 | 0 | Normal
2025-07-30 08:00 | 211 | 7 | Winter | 8 | 2.25 | -26.2 | 26.81 | 63.4 | 262.9 | 13.41 | 120 | 133.41 | 26.2 | 66.56 | 63.91 | 66.85 | 0 | 0 | 0 | Normal
2025-07-30 09:00 | 211 | 7 | Winter | 9 | 2.25 | -23.9 | 16.39 | 45.6 | 0 | 0 | 120 | 120 | 23.9 | 70.05 | 82.3 | 49.95 | 0 | 0 | 0 | Normal
2025-07-30 10:00 | 211 | 7 | Winter | 10 | 2.25 | -25.1 | 10.36 | 63.6 | 0 | 0 | 45.18 | 45.18 | 25.1 | 67.52 | 73.36 | -22.34 | 0 | 0 | 0 | Battery-supported
2025-07-30 11:00 | 211 | 7 | Winter | 11 | 2.25 | -25.4 | 23.43 | 34.8 | 84.5 | 4.31 | 120 | 124.31 | 25.4 | 74.53 | 91.68 | 49.78 | 0 | 0 | 0 | Normal
2025-07-30 12:00 | 211 | 7 | Winter | 12 | 2.25 | -23 | 7.02 | 29.2 | 512.5 | 26.14 | 6.1 | 32.24 | 23 | 67.09 | 77.74 | -34.85 | 0 | 0 | 0 | Battery-supported
2025-07-30 13:00 | 211 | 7 | Winter | 13 | 2.25 | -26.7 | 14.18 | 85.8 | 40.7 | 2.08 | 120 | 122.08 | 26.7 | 66.34 | 95 | 46.9 | 0 | 0 | 0 | Normal
2025-07-30 14:00 | 211 | 7 | Winter | 14 | 2.25 | -24.6 | 9.7 | 65.4 | 0 | 0 | 33.36 | 33.36 | 24.6 | 73.21 | 79.06 | -39.85 | 0 | 0 | 0 | Battery-supported
2025-07-30 15:00 | 211 | 7 | Winter | 15 | 2.25 | -24.3 | 23.58 | 80.5 | 0 | 0 | 120 | 120 | 24.3 | 65.87 | 95 | 43.32 | 0 | 0 | 0 | Normal
2025-07-30 16:00 | 211 | 7 | Winter | 16 | 2.25 | -24.5 | 5.36 | 28.9 | 392.8 | 20.03 | 0.9 | 20.93 | 24.5 | 62.94 | 78.2 | -42.01 | 0 | 0 | 0 | Battery-supported
2025-07-30 17:00 | 211 | 7 | Winter | 17 | 2.25 | -24.5 | 5.36 | 34.7 | 372.8 | 19.01 | 0.9 | 19.91 | 24.5 | 73.74 | 56.66 | -53.83 | 0 | 0 | 0 | Battery-supported
2025-07-30 18:00 | 211 | 7 | Winter | 18 | 2.25 | -23.2 | 20.42 | 41.4 | 0 | 0 | 120 | 120 | 23.2 | 68.9 | 75.47 | 51.1 | 0 | 0 | 0 | Normal
2025-07-30 19:00 | 211 | 7 | Winter | 19 | 2.25 | -23.2 | 13.59 | 29.2 | 0 | 0 | 120 | 120 | 23.2 | 62.88 | 95 | 53.07 | 0 | 0 | 0 | Normal
2025-07-30 20:00 | 211 | 7 | Winter | 20 | 2.25 | -25.5 | 21.37 | 49.1 | 70 | 3.57 | 120 | 123.57 | 25.5 | 68.22 | 95 | 0 | 0 | 0 | 0 | Normal
2025-07-30 21:00 | 211 | 7 | Winter | 21 | 2.25 | -21.5 | 5.72 | 70.8 | 307.7 | 15.69 | 1.53 | 17.22 | 21.5 | 56.11 | 79.44 | -38.89 | 0 | 0 | 0 | Battery-supported
2025-07-30 22:00 | 211 | 7 | Winter | 22 | 2.25 | -25.5 | 6.44 | 29.4 | 91.7 | 4.68 | 3.56 | 8.24 | 25.5 | 57.06 | 59.92 | -48.82 | 0 | 0 | 0 | Battery-supported
2025-07-30 23:00 | 211 | 7 | Winter | 23 | 2.25 | -24.1 | 12.23 | 43.5 | 0 | 0 | 93.12 | 93.12 | 24.1 | 55.8 | 73.65 | 37.32 | 0 | 0 | 0 | Normal
2025-07-31 | 212 | 7 | Winter | 0 | 2.59 | -24.5 | 3.53 | 70.8 | 0 | 0 | 0 | 0 | 24.5 | 59.24 | 49.95 | -59.24 | 0 | 0 | 0 | Battery-supported
2025-07-31 01:00 | 212 | 7 | Winter | 1 | 2.59 | -23.5 | 11.72 | 68.3 | 230.7 | 11.77 | 77.74 | 89.51 | 23.5 | 62.57 | 59.87 | 26.94 | 0 | 0 | 0 | Normal
2025-07-31 02:00 | 212 | 7 | Winter | 2 | 2.59 | -29.3 | 7.76 | 83.3 | 221.8 | 11.31 | 10.82 | 22.13 | 29.3 | 67.77 | 41.61 | -45.64 | 0 | 0 | 0 | Battery-supported
2025-07-31 03:00 | 212 | 7 | Winter | 3 | 2.59 | -23.1 | 9.66 | 58 | 0 | 0 | 32.72 | 32.72 | 23.1 | 56.03 | 32.29 | -23.31 | 0 | 0 | 0 | Battery-supported
2025-07-31 04:00 | 212 | 7 | Winter | 4 | 2.59 | -26.9 | 15.26 | 36.6 | 0 | 0 | 120 | 120 | 26.9 | 65.36 | 52.4 | 54.64 | 0 | 0 | 0 | Normal
2025-07-31 05:00 | 212 | 7 | Winter | 5 | 2.59 | -23 | 15.71 | 55.8 | 0 | 0 | 120 | 120 | 23 | 64.09 | 72.97 | 55.91 | 0 | 0 | 0 | Normal
2025-07-31 06:00 | 212 | 7 | Winter | 6 | 2.59 | -27 | 26.04 | 22.4 | 300.1 | 15.31 | 120 | 135.31 | 27 | 58.7 | 95 | 59.86 | 0 | 0 | 0 | Normal
2025-07-31 07:00 | 212 | 7 | Winter | 7 | 2.59 | -26.2 | 18.66 | 52.7 | 386.8 | 19.73 | 120 | 139.73 | 26.2 | 64.27 | 95 | 0 | 0 | 0 | 0 | Normal
2025-07-31 08:00 | 212 | 7 | Winter | 8 | 2.59 | -21.9 | 2.33 | 37.8 | 63.4 | 3.23 | 0 | 3.23 | 21.9 | 65.09 | 70.26 | -61.86 | 0 | 0 | 0 | Battery-supported
2025-07-31 09:00 | 212 | 7 | Winter | 9 | 2.59 | -26.7 | 5.67 | 29.7 | 0 | 0 | 1.43 | 1.43 | 26.7 | 68.74 | 43.33 | -67.31 | 0 | 0 | 0 | Battery-supported
2025-07-31 10:00 | 212 | 7 | Winter | 10 | 2.59 | -23.2 | 5.99 | 46.1 | 0 | 0 | 2.16 | 2.16 | 23.2 | 66.39 | 17.64 | -64.23 | 0 | 0 | 0 | Battery-supported
2025-07-31 11:00 | 212 | 7 | Winter | 11 | 2.59 | -25.6 | 17.58 | 30.8 | 177.1 | 9.03 | 120 | 129.03 | 25.6 | 71.98 | 38.63 | 57.05 | 0 | 0 | 0 | Normal
2025-07-31 12:00 | 212 | 7 | Winter | 12 | 2.59 | -24.5 | 23.95 | 45.1 | 434 | 22.13 | 120 | 142.13 | 24.5 | 62.58 | 67.91 | 79.55 | 0 | 0 | 0 | Normal
2025-07-31 13:00 | 212 | 7 | Winter | 13 | 2.59 | -24.9 | 4.38 | 82.2 | 88.3 | 4.5 | 0.1 | 4.6 | 24.9 | 68.03 | 42.54 | -63.43 | 0 | 0 | 0 | Battery-supported
2025-07-31 14:00 | 212 | 7 | Winter | 14 | 2.59 | -22.8 | 17.84 | 52.3 | 0 | 0 | 120 | 120 | 22.8 | 64.47 | 62.97 | 55.53 | 0 | 0 | 0 | Normal
2025-07-31 15:00 | 212 | 7 | Winter | 15 | 2.59 | -25.7 | 10.37 | 82.1 | 0 | 0 | 45.38 | 45.38 | 25.7 | 68.91 | 53.56 | -23.53 | 0 | 0 | 0 | Battery-supported
2025-07-31 16:00 | 212 | 7 | Winter | 16 | 2.59 | -26 | 9.49 | 80.1 | 35.3 | 1.8 | 30.08 | 31.88 | 26 | 68.39 | 38.96 | -36.51 | 0 | 0 | 0 | Battery-supported
2025-07-31 17:00 | 212 | 7 | Winter | 17 | 2.59 | -25 | 6.94 | 41.3 | 441.6 | 22.52 | 5.7 | 28.22 | 25 | 65.12 | 24.2 | -36.9 | 0 | 0 | 0 | Battery-supported
2025-07-31 18:00 | 212 | 7 | Winter | 18 | 2.59 | -23.1 | 8.68 | 49.9 | 225.9 | 11.52 | 19.45 | 30.97 | 23.1 | 73.77 | 15 | -22.99 | 19.81 | 6.978 | 0 | Diesel-backup
2025-07-31 19:00 | 212 | 7 | Winter | 19 | 2.59 | -23.7 | 11.75 | 45 | 0 | 0 | 78.59 | 78.59 | 23.7 | 56.36 | 23.18 | 22.23 | 0 | 0 | 0 | Normal
2025-07-31 20:00 | 212 | 7 | Winter | 20 | 2.59 | -21.6 | 7.48 | 10 | 0 | 0 | 8.82 | 8.82 | 21.6 | 67.01 | 15 | -20.45 | 37.74 | 12.427 | 0 | Diesel-backup
2025-07-31 21:00 | 212 | 7 | Winter | 21 | 2.59 | -20.3 | 13.19 | 32.5 | 0 | 0 | 120 | 120 | 20.3 | 57.74 | 37.91 | 62.26 | 0 | 0 | 0 | Normal
2025-07-31 22:00 | 212 | 7 | Winter | 22 | 2.59 | -25.5 | 9.51 | 73.6 | 265.2 | 13.53 | 30.38 | 43.91 | 25.5 | 60.94 | 31.1 | -17.03 | 0 | 0 | 0 | Battery-supported
2025-07-31 23:00 | 212 | 7 | Winter | 23 | 2.59 | -25.2 | 8.87 | 26.3 | 379.9 | 19.37 | 21.67 | 41.04 | 25.2 | 61.44 | 22.94 | -20.4 | 0 | 0 | 0 | Battery-supported
2025-08-01 | 213 | 8 | Winter | 0 | 2.9 | -27 | 14.64 | 45.8 | 391 | 19.94 | 120 | 139.94 | 27 | 64.67 | 50.64 | 75.27 | 0 | 0 | 0 | Normal
2025-08-01 01:00 | 213 | 8 | Winter | 1 | 2.9 | -19.7 | 12.42 | 64.1 | 270.9 | 13.82 | 99.34 | 113.16 | 19.7 | 52.72 | 72.88 | 60.44 | 0 | 0 | 0 | Normal
2025-08-01 02:00 | 213 | 8 | Winter | 2 | 2.9 | -23.9 | 1.79 | 68.8 | 0 | 0 | 0 | 0 | 23.9 | 57.57 | 49.85 | -57.57 | 0 | 0 | 0 | Battery-supported
2025-08-01 03:00 | 213 | 8 | Winter | 3 | 2.9 | -23.9 | 13.51 | 71.8 | 0 | 0 | 120 | 120 | 23.9 | 57.77 | 72.75 | 62.23 | 0 | 0 | 0 | Normal
2025-08-01 04:00 | 213 | 8 | Winter | 4 | 2.9 | -28.3 | 12.01 | 54.8 | 0 | 0 | 86.26 | 86.26 | 28.3 | 65.34 | 80.45 | 20.92 | 0 | 0 | 0 | Normal
2025-08-01 05:00 | 213 | 8 | Winter | 5 | 2.9 | -25.6 | 19.33 | 61.2 | 95.2 | 4.86 | 120 | 124.86 | 25.6 | 62.79 | 95 | 39.53 | 0 | 0 | 0 | Normal
2025-08-01 06:00 | 213 | 8 | Winter | 6 | 2.9 | -24.8 | 12.29 | 21.4 | 537.7 | 27.42 | 95.06 | 122.48 | 24.8 | 55.74 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-01 07:00 | 213 | 8 | Winter | 7 | 2.9 | -26.6 | 8.37 | 26.3 | 340.6 | 17.37 | 16.17 | 33.54 | 26.6 | 61.5 | 83.82 | -27.96 | 0 | 0 | 0 | Battery-supported
2025-08-01 08:00 | 213 | 8 | Winter | 8 | 2.9 | -23.7 | 6.76 | 31.4 | 0 | 0 | 4.85 | 4.85 | 23.7 | 64.4 | 60 | -59.55 | 0 | 0 | 0 | Battery-supported
2025-08-01 09:00 | 213 | 8 | Winter | 9 | 2.9 | -20.9 | 3.08 | 67.2 | 0 | 0 | 0 | 0 | 20.9 | 60.31 | 35.87 | -60.31 | 0 | 0 | 0 | Battery-supported
2025-08-01 10:00 | 213 | 8 | Winter | 10 | 2.9 | -28 | 10.27 | 64.6 | 0 | 0 | 43.43 | 43.43 | 28 | 69.27 | 25.54 | -25.84 | 0 | 0 | 0 | Battery-supported
2025-08-01 11:00 | 213 | 8 | Winter | 11 | 2.9 | -27.9 | 6.04 | 43.4 | 207.2 | 10.57 | 2.29 | 12.86 | 27.9 | 66.59 | 15 | -26.34 | 27.39 | 9.382 | 0 | Diesel-backup
2025-08-01 12:00 | 213 | 8 | Winter | 12 | 2.9 | -27.3 | 20.99 | 58 | 370.4 | 18.89 | 120 | 138.89 | 27.3 | 63.26 | 42.83 | 75.63 | 0 | 0 | 0 | Normal
2025-08-01 13:00 | 213 | 8 | Winter | 13 | 2.9 | -21.4 | 10.54 | 66.6 | 153.8 | 7.84 | 48.83 | 56.67 | 21.4 | 64.91 | 39.54 | -8.24 | 0 | 0 | 0 | Battery-supported
2025-08-01 14:00 | 213 | 8 | Winter | 14 | 2.9 | -22.3 | 4.94 | 71.7 | 0 | 0 | 0.42 | 0.42 | 22.3 | 69.24 | 15 | -61.34 | 7.48 | 2.753 | 0 | Diesel-backup
2025-08-01 15:00 | 213 | 8 | Winter | 15 | 2.9 | -24.5 | 2.46 | 17.4 | 0 | 0 | 0 | 0 | 24.5 | 66.44 | 15 | 0 | 66.44 | 21.261 | 0 | Diesel-backup
2025-08-01 16:00 | 213 | 8 | Winter | 16 | 2.9 | -23.7 | 3.21 | 32.6 | 0 | 0 | 0 | 0 | 23.7 | 70.56 | 15 | 0 | 70.56 | 22.579 | 0 | Diesel-backup
2025-08-01 17:00 | 213 | 8 | Winter | 17 | 2.9 | -25.3 | 12.86 | 26 | 341.6 | 17.42 | 114.77 | 132.19 | 25.3 | 71.56 | 37.31 | 60.63 | 0 | 0 | 0 | Normal
2025-08-01 18:00 | 213 | 8 | Winter | 18 | 2.9 | -21.3 | 22.36 | 34.7 | 474.1 | 24.18 | 120 | 144.18 | 21.3 | 60.99 | 67.93 | 83.19 | 0 | 0 | 0 | Normal
2025-08-01 19:00 | 213 | 8 | Winter | 19 | 2.9 | -24 | 14.44 | 26.5 | 141 | 7.19 | 120 | 127.19 | 24 | 63.87 | 91.23 | 63.32 | 0 | 0 | 0 | Normal
2025-08-01 20:00 | 213 | 8 | Winter | 20 | 2.9 | -23.6 | 9.63 | 20.4 | 0 | 0 | 32.24 | 32.24 | 23.6 | 61.03 | 79.71 | -28.79 | 0 | 0 | 0 | Battery-supported
2025-08-01 21:00 | 213 | 8 | Winter | 21 | 2.9 | -21.8 | 29.4 | 67.7 | 0 | 0 | 0 | 0 | 21.8 | 57.91 | 56.55 | -57.91 | 0 | 0 | 0 | Battery-supported
2025-08-01 22:00 | 213 | 8 | Winter | 22 | 2.9 | -23.7 | 16.28 | 57.7 | 0 | 0 | 120 | 120 | 23.7 | 60.9 | 78.3 | 59.1 | 0 | 0 | 0 | Normal
2025-08-01 23:00 | 213 | 8 | Winter | 23 | 2.9 | -24 | 12.36 | 70.7 | 245.1 | 12.5 | 97.34 | 109.84 | 24 | 59.13 | 95 | 45.39 | 0 | 0 | 0 | Normal
2025-08-02 | 214 | 8 | Winter | 0 | 3.18 | -23.7 | 8.22 | 35 | 361 | 18.41 | 14.72 | 33.13 | 23.7 | 55.75 | 85.95 | -22.62 | 0 | 0 | 0 | Battery-supported
2025-08-02 01:00 | 214 | 8 | Winter | 1 | 3.18 | -22.4 | 22.99 | 78.8 | 0 | 0 | 120 | 120 | 22.4 | 57.22 | 95 | 24.59 | 0 | 0 | 0 | Normal
2025-08-02 02:00 | 214 | 8 | Winter | 2 | 3.18 | -20.9 | 8.72 | 85.2 | 0 | 0 | 19.91 | 19.91 | 20.9 | 58.81 | 79.44 | -38.9 | 0 | 0 | 0 | Battery-supported
2025-08-02 03:00 | 214 | 8 | Winter | 3 | 3.18 | -23.6 | 6.02 | 24.6 | 0 | 0 | 2.24 | 2.24 | 23.6 | 61.1 | 55.9 | -58.86 | 0 | 0 | 0 | Battery-supported
2025-08-02 04:00 | 214 | 8 | Winter | 4 | 3.18 | -23.5 | 9.88 | 68.7 | 0 | 0 | 36.35 | 36.35 | 23.5 | 60.69 | 46.16 | -24.34 | 0 | 0 | 0 | Battery-supported
2025-08-02 05:00 | 214 | 8 | Winter | 5 | 3.18 | -26 | 11.11 | 76 | 229.4 | 11.7 | 61.68 | 73.38 | 26 | 62.38 | 50.21 | 11 | 0 | 0 | 0 | Normal
2025-08-02 06:00 | 214 | 8 | Winter | 6 | 3.18 | -27.4 | 17.08 | 94.2 | 180 | 9.18 | 120 | 129.18 | 27.4 | 67.1 | 73.05 | 62.08 | 0 | 0 | 0 | Normal
2025-08-02 07:00 | 214 | 8 | Winter | 7 | 3.18 | -24.5 | 5.92 | 24.9 | 116.4 | 5.94 | 1.98 | 7.92 | 24.5 | 55.71 | 53.94 | -47.79 | 0 | 0 | 0 | Battery-supported
2025-08-02 08:00 | 214 | 8 | Winter | 8 | 3.18 | -25.6 | 6.67 | 25.8 | 0 | 0 | 4.46 | 4.46 | 25.6 | 66.29 | 29.21 | -61.83 | 0 | 0 | 0 | Battery-supported
2025-08-02 09:00 | 214 | 8 | Winter | 9 | 3.18 | -29.1 | 6.91 | 51.4 | 0 | 0 | 5.55 | 5.55 | 29.1 | 68.47 | 15 | -35.51 | 27.41 | 9.387 | 0 | Diesel-backup
2025-08-02 10:00 | 214 | 8 | Winter | 10 | 3.18 | -26.5 | 9.56 | 71.8 | 0 | 0 | 31.15 | 31.15 | 26.5 | 67.98 | 15 | 0 | 36.83 | 12.171 | 0 | Diesel-backup
2025-08-02 11:00 | 214 | 8 | Winter | 11 | 3.18 | -25.8 | 5.01 | 70.5 | 170.6 | 8.7 | 0.48 | 9.18 | 25.8 | 74.76 | 15 | 0 | 65.58 | 20.986 | 0 | Diesel-backup
2025-08-02 12:00 | 214 | 8 | Winter | 12 | 3.18 | -26.4 | 20.83 | 27.3 | 521.4 | 26.59 | 120 | 146.59 | 26.4 | 66.46 | 44.49 | 80.13 | 0 | 0 | 0 | Normal
2025-08-02 13:00 | 214 | 8 | Winter | 13 | 3.18 | -21.6 | 3.23 | 14.6 | 322.3 | 16.44 | 0 | 16.44 | 21.6 | 61.73 | 26.37 | -45.29 | 0 | 0 | 0 | Battery-supported
2025-08-02 14:00 | 214 | 8 | Winter | 14 | 3.18 | -23.5 | 23.37 | 21.8 | 0 | 0 | 120 | 120 | 23.5 | 59.78 | 48.53 | 60.22 | 0 | 0 | 0 | Normal
2025-08-02 15:00 | 214 | 8 | Winter | 15 | 3.18 | -21.1 | 16.11 | 10.4 | 0 | 0 | 120 | 120 | 21.1 | 66.73 | 68.14 | 53.27 | 0 | 0 | 0 | Normal
2025-08-02 16:00 | 214 | 8 | Winter | 16 | 3.18 | -23.2 | 5.68 | 9.6 | 0 | 0 | 1.45 | 1.45 | 23.2 | 66.13 | 42.26 | -64.68 | 0 | 0 | 0 | Battery-supported
2025-08-02 17:00 | 214 | 8 | Winter | 17 | 3.18 | -23.3 | 9.08 | 38.3 | 102 | 5.2 | 24.32 | 29.52 | 23.3 | 71.92 | 25.3 | -42.4 | 0 | 0 | 0 | Battery-supported
2025-08-02 18:00 | 214 | 8 | Winter | 18 | 3.18 | -25.3 | 6.3 | 53.6 | 366.6 | 18.7 | 3.07 | 21.77 | 25.3 | 73.95 | 15 | -25.76 | 26.42 | 9.083 | 0 | Diesel-backup
2025-08-02 19:00 | 214 | 8 | Winter | 19 | 3.18 | -23 | 16.27 | 65.8 | 270.1 | 13.78 | 120 | 133.78 | 23 | 61.59 | 41.57 | 72.19 | 0 | 0 | 0 | Normal
2025-08-02 20:00 | 214 | 8 | Winter | 20 | 3.18 | -23 | 22 | 35.4 | 0 | 0 | 120 | 120 | 23 | 65.76 | 61.53 | 54.24 | 0 | 0 | 0 | Normal
2025-08-02 21:00 | 214 | 8 | Winter | 21 | 3.18 | -26.1 | 44.33 | 15.2 | 0 | 0 | 0 | 0 | 26.1 | 66.22 | 35.04 | -66.22 | 0 | 0 | 0 | Battery-supported
2025-08-02 22:00 | 214 | 8 | Winter | 22 | 3.18 | -24.4 | 13.9 | 85.9 | 0 | 0 | 120 | 120 | 24.4 | 56.49 | 58.41 | 63.51 | 0 | 0 | 0 | Normal
2025-08-02 23:00 | 214 | 8 | Winter | 23 | 3.18 | -24.2 | 3.3 | 79.6 | 0 | 0 | 0 | 0 | 24.2 | 63.16 | 33.15 | -63.16 | 0 | 0 | 0 | Battery-supported
2025-08-03 | 215 | 8 | Winter | 0 | 3.45 | -22.8 | 5.38 | 34 | 0 | 0 | 0.93 | 0.93 | 22.8 | 47.88 | 15 | -45.36 | 1.59 | 0.595 | 0 | Diesel-backup
2025-08-03 01:00 | 215 | 8 | Winter | 1 | 3.45 | -23.1 | 13.48 | 80.9 | 0 | 0 | 120 | 120 | 23.1 | 57.89 | 37.86 | 62.11 | 0 | 0 | 0 | Normal
2025-08-03 02:00 | 215 | 8 | Winter | 2 | 3.45 | -25.7 | 9.32 | 80.1 | 0 | 0 | 27.59 | 27.59 | 25.7 | 58.22 | 25.6 | -30.63 | 0 | 0 | 0 | Battery-supported
2025-08-03 03:00 | 215 | 8 | Winter | 3 | 3.45 | -23.8 | 15.97 | 68.8 | 0 | 0 | 120 | 120 | 23.8 | 63.08 | 46.55 | 56.92 | 0 | 0 | 0 | Normal
2025-08-03 04:00 | 215 | 8 | Winter | 4 | 3.45 | -25.6 | 12.47 | 57.1 | 203 | 10.35 | 101.02 | 111.37 | 25.6 | 59.11 | 65.78 | 52.26 | 0 | 0 | 0 | Normal
2025-08-03 05:00 | 215 | 8 | Winter | 5 | 3.45 | -31.8 | 5.73 | 56.8 | 374.8 | 19.11 | 1.55 | 20.66 | 31.8 | 70.11 | 46 | -49.45 | 0 | 0 | 0 | Battery-supported
2025-08-03 06:00 | 215 | 8 | Winter | 6 | 3.45 | -26.8 | 8.41 | 24 | 366.2 | 18.68 | 16.57 | 35.25 | 26.8 | 63.92 | 34.53 | -28.67 | 0 | 0 | 0 | Battery-supported
2025-08-03 07:00 | 215 | 8 | Winter | 7 | 3.45 | -23.5 | 16.41 | 32.6 | 0 | 0 | 120 | 120 | 23.5 | 55.51 | 58.27 | 64.49 | 0 | 0 | 0 | Normal
2025-08-03 08:00 | 215 | 8 | Winter | 8 | 3.45 | -29.7 | 12.9 | 28.9 | 0 | 0 | 116.25 | 116.25 | 29.7 | 76.28 | 72.98 | 39.97 | 0 | 0 | 0 | Normal
2025-08-03 09:00 | 215 | 8 | Winter | 9 | 3.45 | -25.7 | 16.07 | 86.7 | 0 | 0 | 120 | 120 | 25.7 | 70.91 | 91.04 | 49.09 | 0 | 0 | 0 | Normal
2025-08-03 10:00 | 215 | 8 | Winter | 10 | 3.45 | -22.3 | 4.15 | 28.1 | 0 | 0 | 0.04 | 0.04 | 22.3 | 59.29 | 67.34 | -59.25 | 0 | 0 | 0 | Battery-supported
2025-08-03 11:00 | 215 | 8 | Winter | 11 | 3.45 | -27.2 | 6 | 98 | 106.6 | 5.44 | 2.19 | 7.63 | 27.2 | 72.32 | 41.47 | -64.69 | 0 | 0 | 0 | Battery-supported
2025-08-03 12:00 | 215 | 8 | Winter | 12 | 3.45 | -25.2 | 19.95 | 78.2 | 271.3 | 13.84 | 120 | 133.84 | 25.2 | 66.35 | 66.3 | 67.49 | 0 | 0 | 0 | Normal
2025-08-03 13:00 | 215 | 8 | Winter | 13 | 3.45 | -27.7 | 4.27 | 75.3 | 175.2 | 8.94 | 0.06 | 9 | 27.7 | 72.6 | 40.86 | -63.6 | 0 | 0 | 0 | Battery-supported
2025-08-03 14:00 | 215 | 8 | Winter | 14 | 3.45 | -20.9 | 15.52 | 86 | 0 | 0 | 120 | 120 | 20.9 | 64.95 | 61.12 | 55.05 | 0 | 0 | 0 | Normal
2025-08-03 15:00 | 215 | 8 | Winter | 15 | 3.45 | -24.3 | 3.92 | 65.4 | 0 | 0 | 0.01 | 0.01 | 24.3 | 71.38 | 32.57 | -71.37 | 0 | 0 | 0 | Battery-supported
2025-08-03 16:00 | 215 | 8 | Winter | 16 | 3.45 | -23.6 | 10.99 | 33.3 | 0 | 0 | 58.81 | 58.81 | 23.6 | 70.43 | 27.92 | -11.62 | 0 | 0 | 0 | Battery-supported
2025-08-03 17:00 | 215 | 8 | Winter | 17 | 3.45 | -20.4 | 7.65 | 7.8 | 0 | 0 | 10 | 10 | 20.4 | 60.3 | 15 | -32.31 | 17.99 | 6.379 | 0 | Diesel-backup
2025-08-03 18:00 | 215 | 8 | Winter | 18 | 3.45 | -21.7 | 5.68 | 30.9 | 343.2 | 17.5 | 1.45 | 18.95 | 21.7 | 62.67 | 15 | 0 | 43.72 | 14.062 | 0 | Diesel-backup
2025-08-03 19:00 | 215 | 8 | Winter | 19 | 3.45 | -24.9 | 11.53 | 28.3 | 514.7 | 26.25 | 72.47 | 98.72 | 24.9 | 66.93 | 26.7 | 31.79 | 0 | 0 | 0 | Normal
2025-08-03 20:00 | 215 | 8 | Winter | 20 | 3.45 | -24.4 | 19.4 | 80.4 | 140.8 | 7.18 | 120 | 127.18 | 24.4 | 71.7 | 47.12 | 55.48 | 0 | 0 | 0 | Normal
2025-08-03 21:00 | 215 | 8 | Winter | 21 | 3.45 | -21.9 | 6.57 | 40.2 | 0 | 0 | 4.05 | 4.05 | 21.9 | 55.32 | 26.61 | -51.27 | 0 | 0 | 0 | Battery-supported
2025-08-03 22:00 | 215 | 8 | Winter | 22 | 3.45 | -24.5 | 2.06 | 36.1 | 0 | 0 | 0 | 0 | 24.5 | 60.82 | 15 | -29.02 | 31.8 | 10.714 | 0 | Diesel-backup
2025-08-03 23:00 | 215 | 8 | Winter | 23 | 3.45 | -28.1 | 9.49 | 40.3 | 0 | 0 | 30.08 | 30.08 | 28.1 | 66.75 | 15 | 0 | 36.67 | 12.125 | 0 | Diesel-backup
2025-08-04 | 216 | 8 | Winter | 0 | 3.7 | -23.8 | 5.63 | 75.8 | 0 | 0 | 1.35 | 1.35 | 23.8 | 59.02 | 15 | 0 | 57.67 | 18.454 | 0 | Diesel-backup
2025-08-04 01:00 | 216 | 8 | Winter | 1 | 3.7 | -27.3 | 16.6 | 10 | 0 | 0 | 120 | 120 | 27.3 | 69.25 | 33.68 | 50.75 | 0 | 0 | 0 | Normal
2025-08-04 02:00 | 216 | 8 | Winter | 2 | 3.7 | -20.8 | 7.63 | 58.6 | 0 | 0 | 9.86 | 9.86 | 20.8 | 53.66 | 16.16 | -43.8 | 0 | 0 | 0 | Battery-supported
2025-08-04 03:00 | 216 | 8 | Winter | 3 | 3.7 | -24.4 | 6.72 | 51.1 | 88.3 | 4.5 | 4.67 | 9.17 | 24.4 | 61.58 | 15 | -2.89 | 49.52 | 15.846 | 0 | Diesel-backup
2025-08-04 04:00 | 216 | 8 | Winter | 4 | 3.7 | -27.1 | 8.18 | 3.6 | 559.4 | 28.53 | 14.35 | 42.88 | 27.1 | 63.7 | 15 | 0 | 20.82 | 7.307 | 0 | Diesel-backup
2025-08-04 05:00 | 216 | 8 | Winter | 5 | 3.7 | -27 | 19.37 | 39.9 | 432.6 | 22.06 | 120 | 142.06 | 27 | 62.52 | 44.27 | 79.54 | 0 | 0 | 0 | Normal
2025-08-04 06:00 | 216 | 8 | Winter | 6 | 3.7 | -29.9 | 13.27 | 23.5 | 198.8 | 10.14 | 120 | 130.14 | 29.9 | 56.38 | 71.41 | 73.76 | 0 | 0 | 0 | Normal
2025-08-04 07:00 | 216 | 8 | Winter | 7 | 3.7 | -28.3 | 5.08 | 53.3 | 0 | 0 | 0.55 | 0.55 | 28.3 | 62.21 | 46.75 | -61.66 | 0 | 0 | 0 | Battery-supported
2025-08-04 08:00 | 216 | 8 | Winter | 8 | 3.7 | -23.7 | 4.14 | 74.7 | 0 | 0 | 0.04 | 0.04 | 23.7 | 59.74 | 22.87 | -59.7 | 0 | 0 | 0 | Battery-supported
2025-08-04 09:00 | 216 | 8 | Winter | 9 | 3.7 | -20.9 | 23.14 | 41.7 | 0 | 0 | 120 | 120 | 20.9 | 61.93 | 44.24 | 58.07 | 0 | 0 | 0 | Normal
2025-08-04 10:00 | 216 | 8 | Winter | 10 | 3.7 | -24.1 | 6.62 | 57.6 | 0 | 0 | 4.25 | 4.25 | 24.1 | 66.81 | 19.22 | -62.56 | 0 | 0 | 0 | Battery-supported
2025-08-04 11:00 | 216 | 8 | Winter | 11 | 3.7 | -25.7 | 19.71 | 1.9 | 427.5 | 21.8 | 120 | 141.8 | 25.7 | 77.92 | 42.72 | 63.88 | 0 | 0 | 0 | Normal
2025-08-04 12:00 | 216 | 8 | Winter | 12 | 3.7 | -26.1 | 9.24 | 14.5 | 584.4 | 29.8 | 26.47 | 56.27 | 26.1 | 72.12 | 36.38 | -15.85 | 0 | 0 | 0 | Battery-supported
2025-08-04 13:00 | 216 | 8 | Winter | 13 | 3.7 | -26.9 | 6.06 | 32.5 | 327.9 | 16.72 | 2.35 | 19.07 | 26.9 | 65.78 | 17.7 | -46.71 | 0 | 0 | 0 | Battery-supported
2025-08-04 14:00 | 216 | 8 | Winter | 14 | 3.7 | -19.9 | 6.38 | 18.1 | 0 | 0 | 3.34 | 3.34 | 19.9 | 63.7 | 15 | -6.75 | 53.61 | 17.155 | 0 | Diesel-backup
2025-08-04 15:00 | 216 | 8 | Winter | 15 | 3.7 | -24.4 | 9.52 | 42.6 | 0 | 0 | 30.54 | 30.54 | 24.4 | 69.09 | 15 | 0 | 38.55 | 12.654 | 0 | Diesel-backup
2025-08-04 16:00 | 216 | 8 | Winter | 16 | 3.7 | -19 | 1.98 | 50.3 | 0 | 0 | 0 | 0 | 19 | 62.4 | 15 | 0 | 62.4 | 19.968 | 0 | Diesel-backup
2025-08-04 17:00 | 216 | 8 | Winter | 17 | 3.7 | -20.3 | 6.2 | 98.3 | 0 | 0 | 2.75 | 2.75 | 20.3 | 63.37 | 15 | 0 | 60.62 | 19.398 | 0 | Diesel-backup
2025-08-04 18:00 | 216 | 8 | Winter | 18 | 3.7 | -26.9 | 27.95 | 19.9 | 205.3 | 10.47 | 120 | 130.47 | 26.9 | 67.68 | 38.11 | 62.79 | 0 | 0 | 0 | Normal
2025-08-04 19:00 | 216 | 8 | Winter | 19 | 3.7 | -24.4 | 32.68 | 43.5 | 415.9 | 21.21 | 0 | 21.21 | 24.4 | 68.84 | 19.05 | -47.63 | 0 | 0 | 0 | Battery-supported
2025-08-04 20:00 | 216 | 8 | Winter | 20 | 3.7 | -24.4 | 6.63 | 0 | 574.8 | 29.31 | 4.29 | 33.6 | 24.4 | 68.45 | 15 | -10.14 | 24.71 | 8.55 | 0 | Diesel-backup
2025-08-04 21:00 | 216 | 8 | Winter | 21 | 3.7 | -23.1 | 15.03 | 35.5 | 105 | 5.36 | 120 | 125.36 | 23.1 | 60.82 | 38.75 | 64.54 | 0 | 0 | 0 | Normal
2025-08-04 22:00 | 216 | 8 | Winter | 22 | 3.7 | -23.2 | 13.05 | 74.4 | 0 | 0 | 120 | 120 | 23.2 | 61.56 | 60.26 | 58.44 | 0 | 0 | 0 | Normal
2025-08-04 23:00 | 216 | 8 | Winter | 23 | 3.7 | -16.7 | 4.56 | 31.7 | 0 | 0 | 0.17 | 0.17 | 16.7 | 54.93 | 38.35 | -54.76 | 0 | 0 | 0 | Battery-supported
2025-08-05 | 217 | 8 | Winter | 0 | 3.94 | -26 | 15.17 | 61.8 | 0 | 0 | 120 | 120 | 26 | 61.43 | 59.91 | 58.57 | 0 | 0 | 0 | Normal
2025-08-05 01:00 | 217 | 8 | Winter | 1 | 3.94 | -23.4 | 8.05 | 52.1 | 0 | 0 | 13.18 | 13.18 | 23.4 | 57.75 | 42.08 | -44.57 | 0 | 0 | 0 | Battery-supported
2025-08-05 02:00 | 217 | 8 | Winter | 2 | 3.94 | -23 | 10.7 | 19.4 | 0 | 0 | 52.24 | 52.24 | 23 | 60.97 | 38.59 | -8.73 | 0 | 0 | 0 | Battery-supported
2025-08-05 03:00 | 217 | 8 | Winter | 3 | 3.94 | -24.7 | 16.95 | 37.5 | 298.8 | 15.24 | 120 | 135.24 | 24.7 | 56.41 | 67.6 | 78.83 | 0 | 0 | 0 | Normal
2025-08-05 04:00 | 217 | 8 | Winter | 4 | 3.94 | -24.8 | 8.4 | 31.8 | 497.4 | 25.37 | 16.47 | 41.84 | 24.8 | 49.91 | 64.37 | -8.07 | 0 | 0 | 0 | Battery-supported
2025-08-05 05:00 | 217 | 8 | Winter | 5 | 3.94 | -27.7 | 8.34 | 34.4 | 369.5 | 18.84 | 15.87 | 34.71 | 27.7 | 55.75 | 55.95 | -21.04 | 0 | 0 | 0 | Battery-supported
2025-08-05 06:00 | 217 | 8 | Winter | 6 | 3.94 | -25.4 | 14.2 | 15.8 | 38 | 1.94 | 120 | 121.94 | 25.4 | 52.9 | 81.36 | 69.04 | 0 | 0 | 0 | Normal
2025-08-05 07:00 | 217 | 8 | Winter | 7 | 3.94 | -24.7 | 20.03 | 63.9 | 0 | 0 | 120 | 120 | 24.7 | 61.95 | 95 | 37.07 | 0 | 0 | 0 | Normal
2025-08-05 08:00 | 217 | 8 | Winter | 8 | 3.94 | -25.1 | 13.73 | 86.3 | 0 | 0 | 120 | 120 | 25.1 | 68.63 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-05 09:00 | 217 | 8 | Winter | 9 | 3.94 | -24.5 | 8.6 | 86.7 | 0 | 0 | 18.57 | 18.57 | 24.5 | 70.65 | 74.17 | -52.08 | 0 | 0 | 0 | Battery-supported
2025-08-05 10:00 | 217 | 8 | Winter | 10 | 3.94 | -22.5 | 18.81 | 22.1 | 0 | 0 | 120 | 120 | 22.5 | 67.57 | 93.46 | 52.43 | 0 | 0 | 0 | Normal
2025-08-05 11:00 | 217 | 8 | Winter | 11 | 3.94 | -23.3 | 12.72 | 63.2 | 241.4 | 12.31 | 109.7 | 122.01 | 23.3 | 70.45 | 95 | 4.18 | 0 | 0 | 0 | Normal
2025-08-05 12:00 | 217 | 8 | Winter | 12 | 3.94 | -24.9 | 22.5 | 55.3 | 384.1 | 19.59 | 120 | 139.59 | 24.9 | 72.42 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-05 13:00 | 217 | 8 | Winter | 13 | 3.94 | -27.3 | 25.95 | 64.9 | 235.4 | 12.01 | 120 | 132.01 | 27.3 | 74.08 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-05 14:00 | 217 | 8 | Winter | 14 | 3.94 | -25.7 | 13.6 | 59.4 | 0 | 0 | 120 | 120 | 25.7 | 72.57 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-05 15:00 | 217 | 8 | Winter | 15 | 3.94 | -24.4 | 21.59 | 51.9 | 0 | 0 | 120 | 120 | 24.4 | 73.95 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-05 16:00 | 217 | 8 | Winter | 16 | 3.94 | -23 | 21.96 | 59.1 | 0 | 0 | 120 | 120 | 23 | 74.33 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-05 17:00 | 217 | 8 | Winter | 17 | 3.94 | -24.3 | 9.83 | 47.1 | 0 | 0 | 35.5 | 35.5 | 24.3 | 67.6 | 82.16 | -32.1 | 0 | 0 | 0 | Battery-supported
2025-08-05 18:00 | 217 | 8 | Winter | 18 | 3.94 | -25.1 | 21.96 | 37.3 | 31 | 1.58 | 120 | 121.58 | 25.1 | 74.25 | 95 | 34.89 | 0 | 0 | 0 | Normal
2025-08-05 19:00 | 217 | 8 | Winter | 19 | 3.94 | -25.5 | 11 | 26.3 | 399.7 | 20.38 | 59.05 | 79.43 | 25.5 | 66.17 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-05 20:00 | 217 | 8 | Winter | 20 | 3.94 | -26.5 | 16.02 | 85.4 | 234.8 | 11.97 | 120 | 131.97 | 26.5 | 67.39 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-05 21:00 | 217 | 8 | Winter | 21 | 3.94 | -23.4 | 10.34 | 49.8 | 260.6 | 13.29 | 44.79 | 58.08 | 23.4 | 65.03 | 92.22 | -6.95 | 0 | 0 | 0 | Battery-supported
2025-08-05 22:00 | 217 | 8 | Winter | 22 | 3.94 | -26.3 | 3.63 | 81.2 | 0 | 0 | 0 | 0 | 26.3 | 61.71 | 67.54 | -61.71 | 0 | 0 | 0 | Battery-supported
2025-08-05 23:00 | 217 | 8 | Winter | 23 | 3.94 | -25.5 | 30.21 | 29.8 | 0 | 0 | 0 | 0 | 25.5 | 53.84 | 46 | -53.84 | 0 | 0 | 0 | Battery-supported
2025-08-06 | 218 | 8 | Winter | 0 | 4.18 | -24.4 | 15.64 | 28.8 | 0 | 0 | 120 | 120 | 24.4 | 54.61 | 70.06 | 65.39 | 0 | 0 | 0 | Normal
2025-08-06 01:00 | 218 | 8 | Winter | 1 | 4.18 | -26.8 | 16.45 | 15.4 | 0 | 0 | 120 | 120 | 26.8 | 58.71 | 92.62 | 61.29 | 0 | 0 | 0 | Normal
2025-08-06 02:00 | 218 | 8 | Winter | 2 | 4.18 | -23.4 | 11.65 | 64.5 | 110.5 | 5.64 | 75.77 | 81.41 | 23.4 | 53.7 | 95 | 6.47 | 0 | 0 | 0 | Normal
2025-08-06 03:00 | 218 | 8 | Winter | 3 | 4.18 | -23 | 21.84 | 36.3 | 422.3 | 21.54 | 120 | 141.54 | 23 | 60.14 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-06 04:00 | 218 | 8 | Winter | 4 | 4.18 | -26.2 | 9.69 | 11.2 | 579.8 | 29.57 | 33.2 | 62.77 | 26.2 | 57.75 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-06 05:00 | 218 | 8 | Winter | 5 | 4.18 | -26.3 | 10.09 | 77.6 | 143.8 | 7.33 | 40.06 | 47.39 | 26.3 | 60.18 | 89.88 | -12.79 | 0 | 0 | 0 | Battery-supported
2025-08-06 06:00 | 218 | 8 | Winter | 6 | 4.18 | -24.4 | 5.11 | 63.5 | 0 | 0 | 0.58 | 0.58 | 24.4 | 56.97 | 67.33 | -56.39 | 0 | 0 | 0 | Battery-supported
2025-08-06 07:00 | 218 | 8 | Winter | 7 | 4.18 | -27.3 | 12.39 | 58.8 | 0 | 0 | 98.34 | 98.34 | 27.3 | 56.84 | 82.6 | 41.5 | 0 | 0 | 0 | Normal
2025-08-06 08:00 | 218 | 8 | Winter | 8 | 4.18 | -27.5 | 21.21 | 68 | 0 | 0 | 120 | 120 | 27.5 | 65.23 | 95 | 33.7 | 0 | 0 | 0 | Normal
2025-08-06 09:00 | 218 | 8 | Winter | 9 | 4.18 | -23.1 | 9.76 | 23.8 | 0 | 0 | 34.33 | 34.33 | 23.1 | 69.75 | 80.83 | -35.42 | 0 | 0 | 0 | Battery-supported
2025-08-06 10:00 | 218 | 8 | Winter | 10 | 4.18 | -23.6 | 4.62 | 71.3 | 20.3 | 1.04 | 0.2 | 1.24 | 23.6 | 67.91 | 54.16 | -66.67 | 0 | 0 | 0 | Battery-supported
2025-08-06 11:00 | 218 | 8 | Winter | 11 | 4.18 | -24 | 18.69 | 52.3 | 291.2 | 14.85 | 120 | 134.85 | 24 | 54.21 | 83.84 | 80.64 | 0 | 0 | 0 | Normal
2025-08-06 12:00 | 218 | 8 | Winter | 12 | 4.18 | -23 | 14.27 | 87.9 | 223.7 | 11.41 | 120 | 131.41 | 23 | 63.46 | 95 | 30.33 | 0 | 0 | 0 | Normal
2025-08-06 13:00 | 218 | 8 | Winter | 13 | 4.18 | -29 | 28.16 | 57.6 | 272 | 13.87 | 0 | 13.87 | 29 | 75.57 | 70.32 | -61.7 | 0 | 0 | 0 | Battery-supported
2025-08-06 14:00 | 218 | 8 | Winter | 14 | 4.18 | -21.3 | 6.38 | 70.7 | 20.5 | 1.05 | 3.34 | 4.39 | 21.3 | 66.56 | 45.45 | -62.17 | 0 | 0 | 0 | Battery-supported
2025-08-06 15:00 | 218 | 8 | Winter | 15 | 4.18 | -23 | 15.67 | 38.6 | 0 | 0 | 120 | 120 | 23 | 74.5 | 62.2 | 45.5 | 0 | 0 | 0 | Normal
2025-08-06 16:00 | 218 | 8 | Winter | 16 | 4.18 | -21.3 | 4.48 | 19.1 | 0 | 0 | 0.13 | 0.13 | 21.3 | 63.27 | 36.94 | -63.14 | 0 | 0 | 0 | Battery-supported
2025-08-06 17:00 | 218 | 8 | Winter | 17 | 4.18 | -22.3 | 10.51 | 46.4 | 0 | 0 | 48.21 | 48.21 | 22.3 | 66.8 | 29.5 | -18.59 | 0 | 0 | 0 | Battery-supported
2025-08-06 18:00 | 218 | 8 | Winter | 18 | 4.18 | -22.9 | 11.77 | 31 | 0 | 0 | 79.16 | 79.16 | 22.9 | 62.37 | 35.68 | 16.79 | 0 | 0 | 0 | Normal
2025-08-06 19:00 | 218 | 8 | Winter | 19 | 4.18 | -23.4 | 3.33 | 17.7 | 298.5 | 15.22 | 0 | 15.22 | 23.4 | 60.21 | 17.69 | -44.99 | 0 | 0 | 0 | Battery-supported
2025-08-06 20:00 | 218 | 8 | Winter | 20 | 4.18 | -22 | 20.32 | 67.4 | 312.9 | 15.96 | 120 | 135.96 | 22 | 66.46 | 43.26 | 69.5 | 0 | 0 | 0 | Normal
2025-08-06 21:00 | 218 | 8 | Winter | 21 | 4.18 | -23.5 | 17.18 | 46.4 | 378.1 | 19.28 | 120 | 139.28 | 23.5 | 56.93 | 73.57 | 82.35 | 0 | 0 | 0 | Normal
2025-08-06 22:00 | 218 | 8 | Winter | 22 | 4.18 | -21.1 | 14.27 | 80.3 | 85.1 | 4.34 | 120 | 124.34 | 21.1 | 66.76 | 94.76 | 57.58 | 0 | 0 | 0 | Normal
2025-08-06 23:00 | 218 | 8 | Winter | 23 | 4.18 | -26.7 | 4.7 | 92 | 0 | 0 | 0.24 | 0.24 | 26.7 | 59.35 | 71.11 | -59.11 | 0 | 0 | 0 | Battery-supported
2025-08-07 | 219 | 8 | Winter | 0 | 4.4 | -24.6 | 6.79 | 13.4 | 0 | 0 | 4.98 | 4.98 | 24.6 | 57.92 | 49.94 | -52.94 | 0 | 0 | 0 | Battery-supported
2025-08-07 01:00 | 219 | 8 | Winter | 1 | 4.4 | -19.3 | 18.33 | 72.2 | 0.4 | 0.02 | 120 | 120.02 | 19.3 | 54.62 | 74 | 65.4 | 0 | 0 | 0 | Normal
2025-08-07 02:00 | 219 | 8 | Winter | 2 | 4.4 | -25.6 | 10.44 | 77.8 | 179.1 | 9.13 | 46.78 | 55.91 | 25.6 | 64.36 | 70.62 | -8.45 | 0 | 0 | 0 | Battery-supported
2025-08-07 03:00 | 219 | 8 | Winter | 3 | 4.4 | -25.1 | 9.17 | 44.7 | 431.7 | 22.02 | 25.51 | 47.53 | 25.1 | 63.52 | 64.23 | -15.99 | 0 | 0 | 0 | Battery-supported
2025-08-07 04:00 | 219 | 8 | Winter | 4 | 4.4 | -26.9 | 21.53 | 62.8 | 291.9 | 14.89 | 120 | 134.89 | 26.9 | 55.26 | 93.53 | 79.63 | 0 | 0 | 0 | Normal
2025-08-07 05:00 | 219 | 8 | Winter | 5 | 4.4 | -24.5 | 11.5 | 65 | 94.4 | 4.81 | 71.66 | 76.47 | 24.5 | 64.73 | 95 | 3.99 | 0 | 0 | 0 | Normal
2025-08-07 06:00 | 219 | 8 | Winter | 6 | 4.4 | -27.1 | 4.98 | 60.3 | 0 | 0 | 0.45 | 0.45 | 27.1 | 61.45 | 70.6 | -61 | 0 | 0 | 0 | Battery-supported
2025-08-07 07:00 | 219 | 8 | Winter | 7 | 4.4 | -26 | 18.2 | 20.6 | 0 | 0 | 120 | 120 | 26 | 50.29 | 95 | 66.3 | 0 | 0 | 0 | Normal
2025-08-07 08:00 | 219 | 8 | Winter | 8 | 4.4 | -23.8 | 4.54 | 50.4 | 0 | 0 | 0.16 | 0.16 | 23.8 | 66.81 | 68.34 | -66.65 | 0 | 0 | 0 | Battery-supported
2025-08-07 09:00 | 219 | 8 | Winter | 9 | 4.4 | -27.2 | 10.49 | 10 | 0 | 0 | 47.8 | 47.8 | 27.2 | 66.13 | 61.01 | -18.33 | 0 | 0 | 0 | Battery-supported
2025-08-07 10:00 | 219 | 8 | Winter | 10 | 4.4 | -23.8 | 12.49 | 78.5 | 38.5 | 1.96 | 101.69 | 103.65 | 23.8 | 71.53 | 72.83 | 32.12 | 0 | 0 | 0 | Normal
2025-08-07 11:00 | 219 | 8 | Winter | 11 | 4.4 | -23.4 | 16.01 | 67.6 | 244.4 | 12.46 | 120 | 132.46 | 23.4 | 67.78 | 95 | 60.25 | 0 | 0 | 0 | Normal
2025-08-07 12:00 | 219 | 8 | Winter | 12 | 4.4 | -22.6 | 3.81 | 76.8 | 278.3 | 14.19 | 0 | 14.19 | 22.6 | 69.9 | 72.72 | -55.71 | 0 | 0 | 0 | Battery-supported
2025-08-07 13:00 | 219 | 8 | Winter | 13 | 4.4 | -24.3 | 1.7 | 48.9 | 314 | 16.01 | 0 | 16.01 | 24.3 | 72.08 | 50.29 | -56.07 | 0 | 0 | 0 | Battery-supported
2025-08-07 14:00 | 219 | 8 | Winter | 14 | 4.4 | -17.1 | 1.76 | 76.8 | 39.6 | 2.38 | 0 | 2.38 | 17.1 | 58.27 | 27.93 | -55.89 | 0 | 0 | 0 | Battery-supported
2025-08-07 15:00 | 219 | 8 | Winter | 15 | 4.4 | -21.5 | 23.1 | 48.1 | 0 | 0 | 120 | 120 | 21.5 | 65.5 | 47.99 | 54.5 | 0 | 0 | 0 | Normal
2025-08-07 16:00 | 219 | 8 | Winter | 16 | 4.4 | -22.7 | 3.34 | 29 | 0 | 0 | 0 | 0 | 22.7 | 70.25 | 19.89 | -70.25 | 0 | 0 | 0 | Battery-supported
2025-08-07 17:00 | 219 | 8 | Winter | 17 | 4.4 | -25.1 | 26.52 | 28.8 | 0 | 0 | 120 | 120 | 25.1 | 68.99 | 38.66 | 51.01 | 0 | 0 | 0 | Normal
2025-08-07 18:00 | 219 | 8 | Winter | 18 | 4.4 | -23.1 | 19.35 | 36.5 | 0 | 0 | 120 | 120 | 23.1 | 62.81 | 59.71 | 57.19 | 0 | 0 | 0 | Normal
2025-08-07 19:00 | 219 | 8 | Winter | 19 | 4.4 | -19.6 | 5.61 | 27.5 | 146.2 | 7.46 | 1.31 | 8.77 | 19.6 | 68.38 | 35.86 | -59.61 | 0 | 0 | 0 | Battery-supported
2025-08-07 20:00 | 219 | 8 | Winter | 20 | 4.4 | -18.9 | 2.26 | 83 | 208.3 | 10.62 | 0 | 10.62 | 18.9 | 62 | 15.31 | -51.38 | 0 | 0 | 0 | Battery-supported
2025-08-07 21:00 | 219 | 8 | Winter | 21 | 4.4 | -19.5 | 10.99 | 41.8 | 446 | 22.75 | 58.81 | 81.56 | 19.5 | 51.35 | 26.43 | 30.21 | 0 | 0 | 0 | Normal
2025-08-07 22:00 | 219 | 8 | Winter | 22 | 4.4 | -21.2 | 7.51 | 37.4 | 309.5 | 15.78 | 9.02 | 24.8 | 21.2 | 63.86 | 15 | -28.57 | 10.49 | 3.821 | 0 | Diesel-backup
2025-08-07 23:00 | 219 | 8 | Winter | 23 | 4.4 | -25.9 | 21.74 | 51.4 | 0.6 | 0.03 | 120 | 120.03 | 25.9 | 53.28 | 39.56 | 66.75 | 0 | 0 | 0 | Normal
2025-08-08 | 220 | 8 | Winter | 0 | 4.62 | -22.3 | 12.4 | 20.7 | 0 | 0 | 98.67 | 98.67 | 22.3 | 54.63 | 55.77 | 44.04 | 0 | 0 | 0 | Normal
2025-08-08 01:00 | 220 | 8 | Winter | 1 | 4.62 | -26.5 | 10.55 | 94.4 | 69.4 | 3.54 | 49.04 | 52.58 | 26.5 | 59.21 | 53.12 | -6.63 | 0 | 0 | 0 | Battery-supported
2025-08-08 02:00 | 220 | 8 | Winter | 2 | 4.62 | -27.4 | 9.19 | 57.9 | 322 | 16.42 | 25.78 | 42.2 | 27.4 | 65.91 | 43.63 | -23.71 | 0 | 0 | 0 | Battery-supported
2025-08-08 03:00 | 220 | 8 | Winter | 3 | 4.62 | -24 | 15.96 | 65.8 | 327.9 | 16.72 | 120 | 136.72 | 24 | 57.6 | 72.75 | 79.12 | 0 | 0 | 0 | Normal
2025-08-08 04:00 | 220 | 8 | Winter | 4 | 4.62 | -23.7 | 9.96 | 71.7 | 202.1 | 10.31 | 37.73 | 48.04 | 23.7 | 55.96 | 69.58 | -7.92 | 0 | 0 | 0 | Battery-supported
2025-08-08 05:00 | 220 | 8 | Winter | 5 | 4.62 | -23.2 | 29.52 | 36.7 | 23.6 | 1.2 | 0 | 1.2 | 23.2 | 62.37 | 45.11 | -61.17 | 0 | 0 | 0 | Battery-supported
2025-08-08 06:00 | 220 | 8 | Winter | 6 | 4.62 | -24.3 | 3.24 | 27.9 | 0 | 0 | 0 | 0 | 24.3 | 62.43 | 20.14 | -62.43 | 0 | 0 | 0 | Battery-supported
2025-08-08 07:00 | 220 | 8 | Winter | 7 | 4.62 | -24.4 | 8.58 | 48.9 | 0 | 0 | 18.35 | 18.35 | 24.4 | 58.25 | 15 | -12.86 | 27.04 | 9.275 | 0 | Diesel-backup
2025-08-08 08:00 | 220 | 8 | Winter | 8 | 4.62 | -27.8 | 14.63 | 67.7 | 0 | 0 | 120 | 120 | 27.8 | 71.73 | 32.76 | 48.27 | 0 | 0 | 0 | Normal
2025-08-08 09:00 | 220 | 8 | Winter | 9 | 4.62 | -25.8 | 13.51 | 11.7 | 0 | 0 | 120 | 120 | 25.8 | 64.29 | 53.26 | 55.71 | 0 | 0 | 0 | Normal
2025-08-08 10:00 | 220 | 8 | Winter | 10 | 4.62 | -28.7 | 29.47 | 33 | 103 | 5.25 | 0 | 5.25 | 28.7 | 70.78 | 27.05 | -65.53 | 0 | 0 | 0 | Battery-supported
2025-08-08 11:00 | 220 | 8 | Winter | 11 | 4.62 | -29.6 | 6.44 | 61.8 | 273.4 | 13.94 | 3.56 | 17.5 | 29.6 | 72.32 | 15 | -30.13 | 24.69 | 8.542 | 0 | Diesel-backup
2025-08-08 12:00 | 220 | 8 | Winter | 12 | 4.62 | -23.2 | 1.02 | 83.3 | 245.9 | 12.54 | 0 | 12.54 | 23.2 | 61.02 | 15 | 0 | 48.48 | 15.514 | 0 | Diesel-backup
2025-08-08 13:00 | 220 | 8 | Winter | 13 | 4.62 | -26.2 | 18.46 | 33.7 | 381.1 | 19.44 | 120 | 139.44 | 26.2 | 62.59 | 43.28 | 76.85 | 0 | 0 | 0 | Normal
2025-08-08 14:00 | 220 | 8 | Winter | 14 | 4.62 | -22.2 | 12.05 | 77.6 | 57.2 | 2.92 | 87.48 | 90.4 | 22.2 | 63.61 | 53.14 | 26.79 | 0 | 0 | 0 | Normal
2025-08-08 15:00 | 220 | 8 | Winter | 15 | 4.62 | -21.3 | 18.56 | 42.6 | 0 | 0 | 120 | 120 | 21.3 | 68.52 | 72.08 | 51.48 | 0 | 0 | 0 | Normal
2025-08-08 16:00 | 220 | 8 | Winter | 16 | 4.62 | -24.7 | 13.12 | 80.3 | 0 | 0 | 120 | 120 | 24.7 | 70.02 | 90.48 | 49.98 | 0 | 0 | 0 | Normal
2025-08-08 17:00 | 220 | 8 | Winter | 17 | 4.62 | -21.8 | 1.48 | 0.8 | 0 | 0 | 0 | 0 | 21.8 | 62.4 | 65.52 | -62.4 | 0 | 0 | 0 | Battery-supported
2025-08-08 18:00 | 220 | 8 | Winter | 18 | 4.62 | -24.3 | 13.62 | 69.3 | 0 | 0 | 120 | 120 | 24.3 | 77.68 | 81.09 | 42.32 | 0 | 0 | 0 | Normal
2025-08-08 19:00 | 220 | 8 | Winter | 19 | 4.62 | -26.7 | 6.41 | 35.8 | 23.9 | 1.22 | 3.45 | 4.67 | 26.7 | 65.41 | 56.79 | -60.74 | 0 | 0 | 0 | Battery-supported
2025-08-08 20:00 | 220 | 8 | Winter | 20 | 4.62 | -22.3 | 8.58 | 67.6 | 215.6 | 11 | 18.35 | 29.35 | 22.3 | 67.5 | 41.53 | -38.15 | 0 | 0 | 0 | Battery-supported
2025-08-08 21:00 | 220 | 8 | Winter | 21 | 4.62 | -23.7 | 9.75 | 79.5 | 261.6 | 13.34 | 34.17 | 47.51 | 23.7 | 56.58 | 37.91 | -9.07 | 0 | 0 | 0 | Battery-supported
2025-08-08 22:00 | 220 | 8 | Winter | 22 | 4.62 | -23.8 | 4.53 | 41.7 | 391.3 | 19.96 | 0.15 | 20.11 | 23.8 | 63.66 | 20.49 | -43.55 | 0 | 0 | 0 | Battery-supported
2025-08-08 23:00 | 220 | 8 | Winter | 23 | 4.62 | -18.7 | 6.26 | 37.3 | 171.1 | 8.73 | 2.94 | 11.67 | 18.7 | 53.25 | 15 | -13.72 | 27.86 | 9.528 | 0 | Diesel-backup
2025-08-09 | 221 | 8 | Winter | 0 | 4.83 | -26.6 | 16.59 | 42.9 | 21.1 | 1.08 | 120 | 121.08 | 26.6 | 60.64 | 37.24 | 60.44 | 0 | 0 | 0 | Normal
2025-08-09 01:00 | 221 | 8 | Winter | 1 | 4.83 | -22.8 | 16.57 | 46.1 | 275.9 | 14.07 | 120 | 134.07 | 22.8 | 61.66 | 63.89 | 72.41 | 0 | 0 | 0 | Normal
2025-08-09 02:00 | 221 | 8 | Winter | 2 | 4.83 | -26.2 | 2.94 | 89.3 | 211.2 | 10.77 | 0 | 10.77 | 26.2 | 60.54 | 43.98 | -49.77 | 0 | 0 | 0 | Battery-supported
2025-08-09 03:00 | 221 | 8 | Winter | 3 | 4.83 | -22.4 | 12.12 | 60.3 | 326.8 | 16.67 | 89.65 | 106.32 | 22.4 | 60.35 | 60.9 | 45.97 | 0 | 0 | 0 | Normal
2025-08-09 04:00 | 221 | 8 | Winter | 4 | 4.83 | -24.1 | 17.66 | 76.7 | 131.6 | 6.71 | 120 | 126.71 | 24.1 | 58.66 | 85.94 | 68.05 | 0 | 0 | 0 | Normal
2025-08-09 05:00 | 221 | 8 | Winter | 5 | 4.83 | -24.3 | 11.37 | 61.7 | 0 | 0 | 68.22 | 68.22 | 24.3 | 48.79 | 93.09 | 19.43 | 0 | 0 | 0 | Normal
2025-08-09 06:00 | 221 | 8 | Winter | 6 | 4.83 | -27.4 | 12.55 | 29.6 | 0 | 0 | 103.74 | 103.74 | 27.4 | 71.02 | 95 | 5.19 | 0 | 0 | 0 | Normal
2025-08-09 07:00 | 221 | 8 | Winter | 7 | 4.83 | -27.2 | 3.12 | 11.2 | 0 | 0 | 0 | 0 | 27.2 | 64.27 | 69.29 | -64.27 | 0 | 0 | 0 | Battery-supported
2025-08-09 08:00 | 221 | 8 | Winter | 8 | 4.83 | -23.5 | 21.21 | 87.8 | 0 | 0 | 120 | 120 | 23.5 | 65.26 | 89.44 | 54.74 | 0 | 0 | 0 | Normal
2025-08-09 09:00 | 221 | 8 | Winter | 9 | 4.83 | -21.6 | 4.82 | 95.4 | 0 | 0 | 0.32 | 0.32 | 21.6 | 70.06 | 61.54 | -69.74 | 0 | 0 | 0 | Battery-supported
2025-08-09 10:00 | 221 | 8 | Winter | 10 | 4.83 | -24.3 | 8.29 | 30.5 | 134.8 | 6.87 | 15.38 | 22.25 | 24.3 | 63.43 | 45.07 | -41.18 | 0 | 0 | 0 | Battery-supported
2025-08-09 11:00 | 221 | 8 | Winter | 11 | 4.83 | -27.1 | 17.76 | 38.5 | 371.3 | 18.94 | 120 | 138.94 | 27.1 | 66.45 | 71.74 | 72.49 | 0 | 0 | 0 | Normal
2025-08-09 12:00 | 221 | 8 | Winter | 12 | 4.83 | -24 | 25.55 | 53.1 | 394.9 | 20.14 | 120 | 140.14 | 24 | 61.34 | 95 | 63.19 | 0 | 0 | 0 | Normal
2025-08-09 13:00 | 221 | 8 | Winter | 13 | 4.83 | -19.1 | 8.74 | 37.1 | 376.7 | 19.21 | 20.14 | 39.35 | 19.1 | 61.3 | 86.22 | -21.95 | 0 | 0 | 0 | Battery-supported
2025-08-09 14:00 | 221 | 8 | Winter | 14 | 4.83 | -23.8 | 33.66 | 76.1 | 75 | 3.82 | 0 | 3.82 | 23.8 | 64.15 | 62.09 | -60.33 | 0 | 0 | 0 | Battery-supported
2025-08-09 15:00 | 221 | 8 | Winter | 15 | 4.83 | -20.4 | 11.62 | 42.2 | 0 | 0 | 74.93 | 74.93 | 20.4 | 62.24 | 66.76 | 12.69 | 0 | 0 | 0 | Normal
2025-08-09 16:00 | 221 | 8 | Winter | 16 | 4.83 | -24.9 | 10.82 | 42.8 | 0 | 0 | 54.9 | 54.9 | 24.9 | 62.02 | 63.91 | -7.12 | 0 | 0 | 0 | Battery-supported
2025-08-09 17:00 | 221 | 8 | Winter | 17 | 4.83 | -23.1 | 5.33 | 22.5 | 0 | 0 | 0.86 | 0.86 | 23.1 | 63.36 | 38.91 | -62.5 | 0 | 0 | 0 | Battery-supported
2025-08-09 18:00 | 221 | 8 | Winter | 18 | 4.83 | -21.4 | 8.4 | 2.2 | 0 | 0 | 16.47 | 16.47 | 21.4 | 66.22 | 19.01 | -49.75 | 0 | 0 | 0 | Battery-supported
2025-08-09 19:00 | 221 | 8 | Winter | 19 | 4.83 | -21.7 | 12.25 | 92.7 | 0 | 0 | 93.76 | 93.76 | 21.7 | 70.16 | 27.69 | 23.6 | 0 | 0 | 0 | Normal
2025-08-09 20:00 | 221 | 8 | Winter | 20 | 4.83 | -24.2 | 14.73 | 47.2 | 200.1 | 10.21 | 120 | 130.21 | 24.2 | 67.38 | 50.82 | 62.83 | 0 | 0 | 0 | Normal
2025-08-09 21:00 | 221 | 8 | Winter | 21 | 4.83 | -24.4 | 14.32 | 83.4 | 223.3 | 11.39 | 120 | 131.39 | 24.4 | 57.41 | 78.04 | 73.98 | 0 | 0 | 0 | Normal
2025-08-09 22:00 | 221 | 8 | Winter | 22 | 4.83 | -20.6 | 7.83 | 36.2 | 466.3 | 23.78 | 11.36 | 35.14 | 20.6 | 58.12 | 68.85 | -22.98 | 0 | 0 | 0 | Battery-supported
2025-08-09 23:00 | 221 | 8 | Winter | 23 | 4.83 | -20.3 | 22.92 | 25.3 | 341.6 | 17.42 | 120 | 137.42 | 20.3 | 60.01 | 95 | 71.06 | 0 | 0 | 0 | Normal
2025-08-10 | 222 | 8 | Winter | 0 | 5.04 | -19.9 | 11.03 | 75.8 | 101.5 | 5.18 | 59.76 | 64.94 | 19.9 | 59.39 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-10 01:00 | 222 | 8 | Winter | 1 | 5.04 | -19.6 | 10.59 | 50.4 | 341.3 | 17.41 | 49.88 | 67.29 | 19.6 | 56.65 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-10 02:00 | 222 | 8 | Winter | 2 | 5.04 | -23.7 | 5.07 | 69.8 | 312.1 | 15.92 | 0.54 | 16.46 | 23.7 | 55.68 | 79.31 | -39.22 | 0 | 0 | 0 | Battery-supported
2025-08-10 03:00 | 222 | 8 | Winter | 3 | 5.04 | -25 | 15.61 | 9.9 | 476.7 | 24.31 | 120 | 144.31 | 25 | 59.78 | 95 | 42.63 | 0 | 0 | 0 | Normal
2025-08-10 04:00 | 222 | 8 | Winter | 4 | 5.04 | -21.7 | 10.21 | 64.9 | 92.7 | 4.73 | 42.28 | 47.01 | 21.7 | 57.67 | 90.74 | -10.66 | 0 | 0 | 0 | Battery-supported
2025-08-10 05:00 | 222 | 8 | Winter | 5 | 5.04 | -23.4 | 8.8 | 58.7 | 0 | 0 | 20.84 | 20.84 | 23.4 | 48.58 | 79.64 | -27.74 | 0 | 0 | 0 | Battery-supported
2025-08-10 06:00 | 222 | 8 | Winter | 6 | 5.04 | -27.4 | 3.97 | 80.2 | 0 | 0 | 0.01 | 0.01 | 27.4 | 62.51 | 54.64 | -62.5 | 0 | 0 | 0 | Battery-supported
2025-08-10 07:00 | 222 | 8 | Winter | 7 | 5.04 | -27.7 | 4.1 | 100 | 0 | 0 | 0.03 | 0.03 | 27.7 | 69.6 | 26.81 | -69.57 | 0 | 0 | 0 | Battery-supported
2025-08-10 08:00 | 222 | 8 | Winter | 8 | 5.04 | -24.4 | 13.02 | 89.4 | 0 | 0 | 120 | 120 | 24.4 | 64.84 | 47.11 | 55.16 | 0 | 0 | 0 | Normal
2025-08-10 09:00 | 222 | 8 | Winter | 9 | 5.04 | -25.8 | 24.85 | 75.9 | 0 | 0 | 120 | 120 | 25.8 | 61.54 | 68.62 | 58.46 | 0 | 0 | 0 | Normal
2025-08-10 10:00 | 222 | 8 | Winter | 10 | 5.04 | -25.3 | 9.24 | 30.2 | 161.1 | 8.22 | 26.47 | 34.69 | 25.3 | 65.64 | 56.24 | -30.95 | 0 | 0 | 0 | Battery-supported
2025-08-10 11:00 | 222 | 8 | Winter | 11 | 5.04 | -22.6 | 9.2 | 13.8 | 477.4 | 24.35 | 25.92 | 50.27 | 22.6 | 62.79 | 51.24 | -12.52 | 0 | 0 | 0 | Battery-supported
2025-08-10 12:00 | 222 | 8 | Winter | 12 | 5.04 | -23 | 15.73 | 49.9 | 410.4 | 20.93 | 120 | 140.93 | 23 | 70.41 | 77.19 | 70.52 | 0 | 0 | 0 | Normal
2025-08-10 13:00 | 222 | 8 | Winter | 13 | 5.04 | -21.4 | 20.74 | 33.9 | 397.2 | 20.26 | 120 | 140.26 | 21.4 | 74.93 | 95 | 48.4 | 0 | 0 | 0 | Normal
2025-08-10 14:00 | 222 | 8 | Winter | 14 | 5.04 | -28.2 | 7.35 | 67.3 | 103 | 5.25 | 7.99 | 13.24 | 28.2 | 71.82 | 71.57 | -58.58 | 0 | 0 | 0 | Battery-supported
2025-08-10 15:00 | 222 | 8 | Winter | 15 | 5.04 | -23 | 5.13 | 68.2 | 0 | 0 | 0.61 | 0.61 | 23 | 62.59 | 46.78 | -61.98 | 0 | 0 | 0 | Battery-supported
2025-08-10 16:00 | 222 | 8 | Winter | 16 | 5.04 | -21.7 | 10.04 | 74 | 0 | 0 | 39.15 | 39.15 | 21.7 | 59.86 | 38.49 | -20.71 | 0 | 0 | 0 | Battery-supported
2025-08-10 17:00 | 222 | 8 | Winter | 17 | 5.04 | -26.2 | 14.18 | 88.2 | 0 | 0 | 120 | 120 | 26.2 | 73.32 | 55.67 | 46.68 | 0 | 0 | 0 | Normal
2025-08-10 18:00 | 222 | 8 | Winter | 18 | 5.04 | -24.1 | 1.76 | 56.5 | 0 | 0 | 0 | 0 | 24.1 | 69.99 | 27.67 | -69.99 | 0 | 0 | 0 | Battery-supported
2025-08-10 19:00 | 222 | 8 | Winter | 19 | 5.04 | -24.3 | 8.03 | 59.9 | 0 | 0 | 13.01 | 13.01 | 24.3 | 71.99 | 15 | -31.69 | 27.29 | 9.353 | 0 | Diesel-backup
2025-08-10 20:00 | 222 | 8 | Winter | 20 | 5.04 | -22.4 | 9.41 | 15 | 160.3 | 8.18 | 28.89 | 37.07 | 22.4 | 63.29 | 15 | 0 | 26.22 | 9.021 | 0 | Diesel-backup
2025-08-10 21:00 | 222 | 8 | Winter | 21 | 5.04 | -18.9 | 8.63 | 26.2 | 413.9 | 21.11 | 18.9 | 40.01 | 18.9 | 60.43 | 15 | 0 | 20.42 | 7.177 | 0 | Diesel-backup
2025-08-10 22:00 | 222 | 8 | Winter | 22 | 5.04 | -18.2 | 3.69 | 38.5 | 466.2 | 23.78 | 0 | 23.78 | 18.2 | 53.9 | 15 | 0 | 30.12 | 10.212 | 0 | Diesel-backup
2025-08-10 23:00 | 222 | 8 | Winter | 23 | 5.04 | -24.7 | 8.05 | 86.3 | 193.7 | 9.88 | 13.18 | 23.06 | 24.7 | 56.85 | 15 | 0 | 33.79 | 11.298 | 0 | Diesel-backup
2025-08-11 | 223 | 8 | Winter | 0 | 5.24 | -22 | 9.49 | 35.2 | 294.2 | 15 | 30.08 | 45.08 | 22 | 48.79 | 15 | 0 | 3.71 | 1.383 | 0 | Diesel-backup
2025-08-11 01:00 | 223 | 8 | Winter | 1 | 5.24 | -22.2 | 5.72 | 88.6 | 209.3 | 10.67 | 1.53 | 12.2 | 22.2 | 55.14 | 15 | 0 | 42.94 | 13.854 | 0 | Diesel-backup
2025-08-11 02:00 | 223 | 8 | Winter | 2 | 5.24 | -23 | 12.28 | 58.5 | 353.3 | 18.02 | 94.73 | 112.75 | 23 | 55.9 | 35.92 | 56.85 | 0 | 0 | 0 | Normal
2025-08-11 03:00 | 223 | 8 | Winter | 3 | 5.24 | -23.4 | 17.09 | 47.4 | 268 | 13.67 | 120 | 133.67 | 23.4 | 54.12 | 65.2 | 79.55 | 0 | 0 | 0 | Normal
2025-08-11 04:00 | 223 | 8 | Winter | 4 | 5.24 | -23.9 | 17.45 | 43.9 | 38.1 | 1.94 | 120 | 121.94 | 23.9 | 60.69 | 87.74 | 61.25 | 0 | 0 | 0 | Normal
2025-08-11 05:00 | 223 | 8 | Winter | 5 | 5.24 | -21.2 | 6.68 | 24.2 | 0 | 0 | 4.5 | 4.5 | 21.2 | 53.43 | 68.16 | -48.93 | 0 | 0 | 0 | Battery-supported
2025-08-11 06:00 | 223 | 8 | Winter | 6 | 5.24 | -22.7 | 14 | 44.7 | 0 | 0 | 120 | 120 | 22.7 | 53.89 | 92.49 | 66.11 | 0 | 0 | 0 | Normal
2025-08-11 07:00 | 223 | 8 | Winter | 7 | 5.24 | -27.6 | 13.31 | 23.3 | 0 | 0 | 120 | 120 | 27.6 | 58.93 | 95 | 6.82 | 0 | 0 | 0 | Normal
2025-08-11 08:00 | 223 | 8 | Winter | 8 | 5.24 | -23.6 | 27.99 | 79.5 | 0 | 0 | 120 | 120 | 23.6 | 60.92 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-11 09:00 | 223 | 8 | Winter | 9 | 5.24 | -23.3 | 14.05 | 21.3 | 0 | 0 | 120 | 120 | 23.3 | 64.02 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-11 10:00 | 223 | 8 | Winter | 10 | 5.24 | -24.5 | 14.55 | 83.2 | 89.5 | 4.56 | 120 | 124.56 | 24.5 | 65.32 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-11 11:00 | 223 | 8 | Winter | 11 | 5.24 | -22.4 | 19.11 | 72 | 249.2 | 12.71 | 120 | 132.71 | 22.4 | 64.42 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-11 12:00 | 223 | 8 | Winter | 12 | 5.24 | -24.2 | 4.38 | 45.4 | 432.4 | 22.05 | 0.1 | 22.15 | 24.2 | 68.73 | 76.37 | -46.58 | 0 | 0 | 0 | Battery-supported
2025-08-11 13:00 | 223 | 8 | Winter | 13 | 5.24 | -23.8 | 10.84 | 74.8 | 237.7 | 12.12 | 55.35 | 67.47 | 23.8 | 72.92 | 74.19 | -5.45 | 0 | 0 | 0 | Battery-supported
2025-08-11 14:00 | 223 | 8 | Winter | 14 | 5.24 | -23.6 | 25.71 | 31.3 | 182 | 9.28 | 120 | 129.28 | 23.6 | 70.64 | 95 | 56.55 | 0 | 0 | 0 | Normal
2025-08-11 15:00 | 223 | 8 | Winter | 15 | 5.24 | -27.9 | 26.02 | 29.6 | 0 | 0 | 120 | 120 | 27.9 | 64.65 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-11 16:00 | 223 | 8 | Winter | 16 | 5.24 | -23.3 | 8.04 | 74.1 | 0 | 0 | 13.1 | 13.1 | 23.3 | 69.87 | 72.29 | -56.77 | 0 | 0 | 0 | Battery-supported
2025-08-11 17:00 | 223 | 8 | Winter | 17 | 5.24 | -24.3 | 25.31 | 34.5 | 0 | 0 | 120 | 120 | 24.3 | 71.63 | 90.09 | 48.37 | 0 | 0 | 0 | Normal
2025-08-11 18:00 | 223 | 8 | Winter | 18 | 5.24 | -25.2 | 8.82 | 22.4 | 0 | 0 | 21.07 | 21.07 | 25.2 | 71.23 | 70.03 | -50.16 | 0 | 0 | 0 | Battery-supported
2025-08-11 19:00 | 223 | 8 | Winter | 19 | 5.24 | -19.3 | 12.54 | 63.6 | 0 | 0 | 103.4 | 103.4 | 19.3 | 60.49 | 85.82 | 42.91 | 0 | 0 | 0 | Normal
2025-08-11 20:00 | 223 | 8 | Winter | 20 | 5.24 | -21.3 | 3.24 | 88.3 | 19.2 | 0.98 | 0 | 0.98 | 21.3 | 70.16 | 58.15 | -69.18 | 0 | 0 | 0 | Battery-supported
2025-08-11 21:00 | 223 | 8 | Winter | 21 | 5.24 | -22.5 | 22.26 | 51.4 | 255.7 | 13.04 | 120 | 133.04 | 22.5 | 53.91 | 87.27 | 79.13 | 0 | 0 | 0 | Normal
2025-08-11 22:00 | 223 | 8 | Winter | 22 | 5.24 | -23.8 | 8.54 | 38.5 | 447.6 | 22.83 | 17.92 | 40.75 | 23.8 | 63.07 | 78.34 | -22.32 | 0 | 0 | 0 | Battery-supported
2025-08-11 23:00 | 223 | 8 | Winter | 23 | 5.24 | -22.2 | 3.77 | 38.5 | 443.4 | 22.61 | 0 | 22.61 | 22.2 | 61.35 | 62.84 | -38.74 | 0 | 0 | 0 | Battery-supported
2025-08-12 | 224 | 8 | Winter | 0 | 5.43 | -20.8 | 9.63 | 44.5 | 346.7 | 17.68 | 32.24 | 49.92 | 20.8 | 57.8 | 59.69 | -7.88 | 0 | 0 | 0 | Battery-supported
2025-08-12 01:00 | 224 | 8 | Winter | 1 | 5.43 | -25.2 | 1.35 | 27.1 | 521.1 | 26.58 | 0 | 26.58 | 25.2 | 53.01 | 49.12 | -26.43 | 0 | 0 | 0 | Battery-supported
2025-08-12 02:00 | 224 | 8 | Winter | 2 | 5.43 | -23.8 | 15.29 | 25.2 | 466.2 | 23.78 | 120 | 143.78 | 23.8 | 59.61 | 80.09 | 84.17 | 0 | 0 | 0 | Normal
2025-08-12 03:00 | 224 | 8 | Winter | 3 | 5.43 | -22.3 | 19.91 | 46.7 | 200.7 | 10.24 | 120 | 130.24 | 22.3 | 60.63 | 95 | 40.51 | 0 | 0 | 0 | Normal
2025-08-12 04:00 | 224 | 8 | Winter | 4 | 5.43 | -28.8 | 5.22 | 0 | 0 | 0 | 0.71 | 0.71 | 28.8 | 63.99 | 69.69 | -63.28 | 0 | 0 | 0 | Battery-supported
2025-08-12 05:00 | 224 | 8 | Winter | 5 | 5.43 | -25 | 5.09 | 55.7 | 0 | 0 | 0.56 | 0.56 | 25 | 59.67 | 46.04 | -59.11 | 0 | 0 | 0 | Battery-supported
2025-08-12 06:00 | 224 | 8 | Winter | 6 | 5.43 | -26 | 14.64 | 76.9 | 0 | 0 | 120 | 120 | 26 | 59.5 | 68.31 | 60.5 | 0 | 0 | 0 | Normal
2025-08-12 07:00 | 224 | 8 | Winter | 7 | 5.43 | -25.5 | 15.7 | 39.7 | 0 | 0 | 120 | 120 | 25.5 | 58.39 | 90.98 | 61.61 | 0 | 0 | 0 | Normal
2025-08-12 08:00 | 224 | 8 | Winter | 8 | 5.43 | -26.4 | 6.88 | 47 | 0 | 0 | 5.4 | 5.4 | 26.4 | 69.02 | 65.53 | -63.62 | 0 | 0 | 0 | Battery-supported
2025-08-12 09:00 | 224 | 8 | Winter | 9 | 5.43 | -24.9 | 5.73 | 73.7 | 0 | 0 | 1.55 | 1.55 | 24.9 | 72.69 | 37.08 | -71.14 | 0 | 0 | 0 | Battery-supported
2025-08-12 10:00 | 224 | 8 | Winter | 10 | 5.43 | -20.8 | 17.9 | 16.5 | 231.5 | 11.81 | 120 | 131.81 | 20.8 | 60.99 | 63.14 | 70.82 | 0 | 0 | 0 | Normal
2025-08-12 11:00 | 224 | 8 | Winter | 11 | 5.43 | -25.5 | 3.49 | 86.4 | 193.5 | 9.87 | 0 | 9.87 | 25.5 | 70.07 | 39.06 | -60.2 | 0 | 0 | 0 | Battery-supported
2025-08-12 12:00 | 224 | 8 | Winter | 12 | 5.43 | -23.9 | 7.74 | 46.8 | 425.7 | 21.71 | 10.67 | 32.38 | 23.9 | 56.14 | 29.55 | -23.76 | 0 | 0 | 0 | Battery-supported
2025-08-12 13:00 | 224 | 8 | Winter | 13 | 5.43 | -19.8 | 5.63 | 46 | 359.7 | 18.34 | 1.35 | 19.69 | 19.8 | 60.7 | 15 | -36.39 | 4.62 | 1.719 | 0 | Diesel-backup
2025-08-12 14:00 | 224 | 8 | Winter | 14 | 5.43 | -25 | 14.51 | 54.3 | 156.5 | 7.98 | 120 | 127.98 | 25 | 70.85 | 36.02 | 57.13 | 0 | 0 | 0 | Normal
2025-08-12 15:00 | 224 | 8 | Winter | 15 | 5.43 | -19.4 | 5.94 | 61.2 | 0 | 0 | 2.03 | 2.03 | 19.4 | 66.42 | 15 | -52.56 | 11.83 | 4.288 | 0 | Diesel-backup
2025-08-12 16:00 | 224 | 8 | Winter | 16 | 5.43 | -23 | 19.29 | 75.7 | 0 | 0 | 120 | 120 | 23 | 61.55 | 36.51 | 58.45 | 0 | 0 | 0 | Normal
2025-08-12 17:00 | 224 | 8 | Winter | 17 | 5.43 | -18.8 | 7.55 | 39.4 | 0 | 0 | 9.3 | 9.3 | 18.8 | 62.93 | 15.06 | -53.63 | 0 | 0 | 0 | Battery-supported
2025-08-12 18:00 | 224 | 8 | Winter | 18 | 5.43 | -20.8 | 13 | 23.5 | 0 | 0 | 120 | 120 | 20.8 | 66.92 | 34.59 | 53.08 | 0 | 0 | 0 | Normal
2025-08-12 19:00 | 224 | 8 | Winter | 19 | 5.43 | -21.6 | 6.01 | 63.9 | 0 | 0 | 2.21 | 2.21 | 21.6 | 61.36 | 15 | -48.98 | 10.17 | 3.709 | 0 | Diesel-backup
2025-08-12 20:00 | 224 | 8 | Winter | 20 | 5.43 | -22.4 | 11.56 | 81.8 | 0 | 0 | 73.29 | 73.29 | 22.4 | 58.69 | 20.37 | 14.6 | 0 | 0 | 0 | Normal
2025-08-12 21:00 | 224 | 8 | Winter | 21 | 5.43 | -23.7 | 6.54 | 63.8 | 161.1 | 8.22 | 3.93 | 12.15 | 23.7 | 53.28 | 15 | -13.43 | 27.7 | 9.477 | 0 | Diesel-backup
2025-08-12 22:00 | 224 | 8 | Winter | 22 | 5.43 | -22.3 | 4.89 | 19 | 493 | 25.14 | 0.38 | 25.52 | 22.3 | 50.89 | 15 | 0 | 25.37 | 8.756 | 0 | Diesel-backup
2025-08-12 23:00 | 224 | 8 | Winter | 23 | 5.43 | -20.7 | 15.64 | 15.9 | 576 | 29.38 | 120 | 149.38 | 20.7 | 58.51 | 48.44 | 90.87 | 0 | 0 | 0 | Normal
2025-08-13 | 225 | 8 | Winter | 0 | 5.63 | -23 | 5.89 | 85.6 | 215 | 10.96 | 1.91 | 12.87 | 23 | 58.37 | 30.24 | -45.5 | 0 | 0 | 0 | Battery-supported
2025-08-13 01:00 | 225 | 8 | Winter | 1 | 5.63 | -24 | 5.96 | 65.3 | 331.4 | 16.9 | 2.08 | 18.98 | 24 | 57.24 | 15 | -38.1 | 0.16 | 0.06 | 0 | Diesel-backup
2025-08-13 02:00 | 225 | 8 | Winter | 2 | 5.63 | -24.2 | 10.94 | 75.6 | 217 | 11.07 | 57.64 | 68.71 | 24.2 | 55.59 | 19.83 | 13.12 | 0 | 0 | 0 | Normal
2025-08-13 03:00 | 225 | 8 | Winter | 3 | 5.63 | -21.9 | 12.11 | 73.8 | 89.7 | 4.57 | 89.33 | 93.9 | 21.9 | 61.26 | 31.84 | 32.64 | 0 | 0 | 0 | Normal
2025-08-13 04:00 | 225 | 8 | Winter | 4 | 5.63 | -21.7 | 4.76 | 39.2 | 0 | 0 | 0.28 | 0.28 | 21.7 | 55.8 | 15 | -42.1 | 13.42 | 4.837 | 0 | Diesel-backup
2025-08-13 05:00 | 225 | 8 | Winter | 5 | 5.63 | -26.2 | 13.81 | 34.9 | 0 | 0 | 120 | 120 | 26.2 | 62.43 | 36.19 | 57.57 | 0 | 0 | 0 | Normal
2025-08-13 06:00 | 225 | 8 | Winter | 6 | 5.63 | -26.5 | 6.23 | 32.9 | 0 | 0 | 2.85 | 2.85 | 26.5 | 57.81 | 15 | -52.96 | 2 | 0.748 | 0 | Diesel-backup
2025-08-13 07:00 | 225 | 8 | Winter | 7 | 5.63 | -24.3 | 3.92 | 69.3 | 0 | 0 | 0.01 | 0.01 | 24.3 | 54.53 | 15 | 0 | 54.52 | 17.446 | 0 | Diesel-backup
2025-08-13 08:00 | 225 | 8 | Winter | 8 | 5.63 | -21.8 | 8.43 | 32.3 | 0 | 0 | 16.77 | 16.77 | 21.8 | 68.8 | 15 | 0 | 52.03 | 16.65 | 0 | Diesel-backup
2025-08-13 09:00 | 225 | 8 | Winter | 9 | 5.63 | -22.6 | 8.35 | 68.4 | 0 | 0 | 15.97 | 15.97 | 22.6 | 65.88 | 15 | 0 | 49.91 | 15.971 | 0 | Diesel-backup
2025-08-13 10:00 | 225 | 8 | Winter | 10 | 5.63 | -27.7 | 13.14 | 95.9 | 80.9 | 4.13 | 120 | 124.13 | 27.7 | 71.33 | 34.43 | 52.8 | 0 | 0 | 0 | Normal
2025-08-13 11:00 | 225 | 8 | Winter | 11 | 5.63 | -25.3 | 28.51 | 44.1 | 372.3 | 18.99 | 0 | 18.99 | 25.3 | 69.55 | 15 | -48.58 | 1.98 | 0.744 | 0 | Diesel-backup
2025-08-13 12:00 | 225 | 8 | Winter | 12 | 5.63 | -26.5 | 10.82 | 51.3 | 403.7 | 20.59 | 54.9 | 75.49 | 26.5 | 73.4 | 15.77 | 2.09 | 0 | 0 | 0 | Normal
2025-08-13 13:00 | 225 | 8 | Winter | 13 | 5.63 | -24.7 | 14.22 | 35.2 | 409.5 | 20.88 | 120 | 140.88 | 24.7 | 72.31 | 41 | 68.57 | 0 | 0 | 0 | Normal
2025-08-13 14:00 | 225 | 8 | Winter | 14 | 5.63 | -20.2 | 3.16 | 60.2 | 158 | 8.06 | 0 | 8.06 | 20.2 | 58.68 | 20.75 | -50.62 | 0 | 0 | 0 | Battery-supported
2025-08-13 15:00 | 225 | 8 | Winter | 15 | 5.63 | -26.4 | 19.79 | 60.8 | 0 | 0 | 120 | 120 | 26.4 | 68.31 | 39.78 | 51.69 | 0 | 0 | 0 | Normal
2025-08-13 16:00 | 225 | 8 | Winter | 16 | 5.63 | -26.5 | 9.32 | 31.5 | 0 | 0 | 27.59 | 27.59 | 26.5 | 65.32 | 24.68 | -37.73 | 0 | 0 | 0 | Battery-supported
2025-08-13 17:00 | 225 | 8 | Winter | 17 | 5.63 | -24.4 | 4.16 | 59.9 | 0 | 0 | 0.04 | 0.04 | 24.4 | 68.06 | 15 | -24.21 | 43.81 | 14.085 | 0 | Diesel-backup
2025-08-13 18:00 | 225 | 8 | Winter | 18 | 5.63 | -21.7 | 19.35 | 53.1 | 0 | 0 | 120 | 120 | 21.7 | 63.09 | 35.94 | 56.91 | 0 | 0 | 0 | Normal
2025-08-13 19:00 | 225 | 8 | Winter | 19 | 5.63 | -20.9 | 9.57 | 29.9 | 0 | 0 | 31.3 | 31.3 | 20.9 | 62.6 | 23.42 | -31.3 | 0 | 0 | 0 | Battery-supported
2025-08-13 20:00 | 225 | 8 | Winter | 20 | 5.63 | -21.2 | 17.55 | 36.5 | 0 | 0 | 120 | 120 | 21.2 | 63.25 | 44.31 | 56.75 | 0 | 0 | 0 | Normal
2025-08-13 21:00 | 225 | 8 | Winter | 21 | 5.63 | -19.6 | 30.28 | 20.1 | 170.6 | 8.7 | 0 | 8.7 | 19.6 | 53.44 | 26.41 | -44.74 | 0 | 0 | 0 | Battery-supported
2025-08-13 22:00 | 225 | 8 | Winter | 22 | 5.63 | -26.3 | 3.43 | 30 | 388.3 | 19.8 | 0 | 19.8 | 26.3 | 71.34 | 15 | -28.53 | 23.01 | 8.012 | 0 | Diesel-backup
2025-08-13 23:00 | 225 | 8 | Winter | 23 | 5.63 | -20 | 6.05 | 56.7 | 373.4 | 19.04 | 2.32 | 21.36 | 20 | 47.22 | 15 | 0 | 25.86 | 8.909 | 0 | Diesel-backup
2025-08-14 | 226 | 8 | Winter | 0 | 5.82 | -23.5 | 15.75 | 58 | 363.4 | 18.53 | 120 | 138.53 | 23.5 | 57.84 | 44.69 | 80.69 | 0 | 0 | 0 | Normal
2025-08-14 01:00 | 226 | 8 | Winter | 1 | 5.82 | -21.6 | 9.96 | 1.2 | 611.8 | 31.2 | 37.73 | 68.93 | 21.6 | 50.56 | 51.45 | 18.37 | 0 | 0 | 0 | Normal
2025-08-14 02:00 | 226 | 8 | Winter | 2 | 5.82 | -26.5 | 1.47 | 55.4 | 243.1 | 12.4 | 0 | 12.4 | 26.5 | 62.11 | 31.57 | -49.71 | 0 | 0 | 0 | Battery-supported
2025-08-14 03:00 | 226 | 8 | Winter | 3 | 5.82 | -24 | 7.83 | 76.2 | 41.1 | 2.1 | 11.36 | 13.46 | 24 | 53.29 | 15.64 | -39.83 | 0 | 0 | 0 | Battery-supported
2025-08-14 04:00 | 226 | 8 | Winter | 4 | 5.82 | -23.8 | 8.66 | 17.6 | 0 | 0 | 19.23 | 19.23 | 23.8 | 58.5 | 15 | -1.6 | 37.67 | 12.409 | 0 | Diesel-backup
2025-08-14 05:00 | 226 | 8 | Winter | 5 | 5.82 | -22.1 | 9.56 | 55.3 | 0 | 0 | 31.15 | 31.15 | 22.1 | 54.13 | 15 | 0 | 22.98 | 8.001 | 0 | Diesel-backup
2025-08-14 06:00 | 226 | 8 | Winter | 6 | 5.82 | -28.4 | 5.89 | 94.6 | 0 | 0 | 1.91 | 1.91 | 28.4 | 67.66 | 15 | 0 | 65.75 | 21.04 | 0 | Diesel-backup
2025-08-14 07:00 | 226 | 8 | Winter | 7 | 5.82 | -25 | 22.65 | 91 | 0 | 0 | 120 | 120 | 25 | 54.01 | 39.28 | 65.99 | 0 | 0 | 0 | Normal
2025-08-14 08:00 | 226 | 8 | Winter | 8 | 5.82 | -27.5 | 3.16 | 47.7 | 0 | 0 | 0 | 0 | 27.5 | 65.03 | 15 | -60.71 | 4.32 | 1.607 | 0 | Diesel-backup
2025-08-14 09:00 | 226 | 8 | Winter | 9 | 5.82 | -23.9 | 12.55 | 35.9 | 0 | 0 | 103.74 | 103.74 | 23.9 | 62.28 | 30.26 | 41.46 | 0 | 0 | 0 | Normal
2025-08-14 10:00 | 226 | 8 | Winter | 10 | 5.82 | -23.2 | 6.91 | 48.3 | 197.3 | 10.06 | 5.55 | 15.61 | 23.2 | 67.65 | 15 | -38.14 | 13.9 | 5 | 0 | Diesel-backup
2025-08-14 11:00 | 226 | 8 | Winter | 11 | 5.82 | -21.8 | 6.58 | 16 | 495.2 | 25.26 | 4.09 | 29.35 | 21.8 | 65.58 | 15 | 0 | 36.23 | 12 | 0 | Diesel-backup
2025-08-14 12:00 | 226 | 8 | Winter | 12 | 5.82 | -25.5 | 20.94 | 78 | 272.3 | 13.89 | 120 | 133.89 | 25.5 | 67.25 | 39.52 | 66.64 | 0 | 0 | 0 | Normal
2025-08-14 13:00 | 226 | 8 | Winter | 13 | 5.82 | -21.9 | 8.37 | 40.5 | 391.8 | 19.98 | 16.17 | 36.15 | 21.9 | 67.4 | 27.02 | -31.25 | 0 | 0 | 0 | Battery-supported
2025-08-14 14:00 | 226 | 8 | Winter | 14 | 5.82 | -20.6 | 12.6 | 61.3 | 167.1 | 8.52 | 105.47 | 113.99 | 20.6 | 54.47 | 48.93 | 59.52 | 0 | 0 | 0 | Normal
2025-08-14 15:00 | 226 | 8 | Winter | 15 | 5.82 | -26.8 | 16.37 | 37.1 | 0 | 0 | 120 | 120 | 26.8 | 68.76 | 67.78 | 51.24 | 0 | 0 | 0 | Normal
2025-08-14 16:00 | 226 | 8 | Winter | 16 | 5.82 | -21.5 | 10.25 | 62.7 | 0 | 0 | 43.04 | 43.04 | 21.5 | 64.36 | 59.26 | -21.32 | 0 | 0 | 0 | Battery-supported
2025-08-14 17:00 | 226 | 8 | Winter | 17 | 5.82 | -20.4 | 21.11 | 73.6 | 0 | 0 | 120 | 120 | 20.4 | 64.04 | 79.85 | 55.96 | 0 | 0 | 0 | Normal
2025-08-14 18:00 | 226 | 8 | Winter | 18 | 5.82 | -22.9 | 3.85 | 57.5 | 0 | 0 | 0.01 | 0.01 | 22.9 | 66.09 | 53.42 | -66.08 | 0 | 0 | 0 | Battery-supported
2025-08-14 19:00 | 226 | 8 | Winter | 19 | 5.82 | -24.8 | 13.06 | 55.2 | 0 | 0 | 120 | 120 | 24.8 | 68.74 | 72.28 | 51.26 | 0 | 0 | 0 | Normal
2025-08-14 20:00 | 226 | 8 | Winter | 20 | 5.82 | -20 | 28.65 | 60.9 | 0 | 0 | 0 | 0 | 20 | 64.73 | 46.39 | -64.73 | 0 | 0 | 0 | Battery-supported
2025-08-14 21:00 | 226 | 8 | Winter | 21 | 5.82 | -24.8 | 12.41 | 76.1 | 41.1 | 2.1 | 99 | 101.1 | 24.8 | 67.52 | 58.75 | 33.58 | 0 | 0 | 0 | Normal
2025-08-14 22:00 | 226 | 8 | Winter | 22 | 5.82 | -22.7 | 2.62 | 54.8 | 244.8 | 12.48 | 0 | 12.48 | 22.7 | 60.5 | 39.54 | -48.02 | 0 | 0 | 0 | Battery-supported
2025-08-14 23:00 | 226 | 8 | Winter | 23 | 5.82 | -22.6 | 13.34 | 33.6 | 462 | 23.56 | 120 | 143.56 | 22.6 | 51.52 | 73.41 | 92.04 | 0 | 0 | 0 | Normal
2025-08-15 | 227 | 8 | Winter | 0 | 6.01 | -21.2 | 23.15 | 34.5 | 486.3 | 24.8 | 120 | 144.8 | 21.2 | 59.5 | 95 | 58.67 | 0 | 0 | 0 | Normal
2025-08-15 01:00 | 227 | 8 | Winter | 1 | 6.01 | -24.5 | 7.89 | 93.4 | 169.7 | 8.65 | 11.84 | 20.49 | 24.5 | 58.85 | 79.66 | -38.36 | 0 | 0 | 0 | Battery-supported
2025-08-15 02:00 | 227 | 8 | Winter | 2 | 6.01 | -25 | 7.82 | 78.2 | 134.4 | 6.85 | 11.28 | 18.13 | 25 | 57.66 | 63.84 | -39.53 | 0 | 0 | 0 | Battery-supported
2025-08-15 03:00 | 227 | 8 | Winter | 3 | 6.01 | -23.7 | 15.35 | 56.5 | 0 | 0 | 120 | 120 | 23.7 | 52.85 | 88.56 | 67.15 | 0 | 0 | 0 | Normal
2025-08-15 04:00 | 227 | 8 | Winter | 4 | 6.01 | -22 | 13.74 | 24.3 | 0 | 0 | 120 | 120 | 22 | 55.77 | 95 | 17.51 | 0 | 0 | 0 | Normal
2025-08-15 05:00 | 227 | 8 | Winter | 5 | 6.01 | -19.5 | 10.47 | 55.6 | 0 | 0 | 47.39 | 47.39 | 19.5 | 55.23 | 91.86 | -7.84 | 0 | 0 | 0 | Battery-supported
2025-08-15 06:00 | 227 | 8 | Winter | 6 | 6.01 | -28.1 | 6.18 | 38.2 | 0 | 0 | 2.69 | 2.69 | 28.1 | 66.04 | 66.52 | -63.35 | 0 | 0 | 0 | Battery-supported
2025-08-15 07:00 | 227 | 8 | Winter | 7 | 6.01 | -24.2 | 7.33 | 53.4 | 0 | 0 | 7.86 | 7.86 | 24.2 | 54.74 | 47.77 | -46.88 | 0 | 0 | 0 | Battery-supported
2025-08-15 08:00 | 227 | 8 | Winter | 8 | 6.01 | -27.4 | 4.98 | 42.5 | 0 | 0 | 0.45 | 0.45 | 27.4 | 68.68 | 20.48 | -68.23 | 0 | 0 | 0 | Battery-supported
2025-08-15 09:00 | 227 | 8 | Winter | 9 | 6.01 | -22.7 | 2.39 | 41.2 | 0.8 | 0.04 | 0 | 0.04 | 22.7 | 63.66 | 15 | -13.7 | 49.92 | 15.974 | 0 | Diesel-backup
2025-08-15 10:00 | 227 | 8 | Winter | 10 | 6.01 | -26.8 | 19.74 | 59.5 | 181.9 | 9.28 | 120 | 129.28 | 26.8 | 67.47 | 37.75 | 61.81 | 0 | 0 | 0 | Normal
2025-08-15 11:00 | 227 | 8 | Winter | 11 | 6.01 | -26 | 15.84 | 52.3 | 345.2 | 17.61 | 120 | 137.61 | 26 | 62.86 | 65.25 | 74.75 | 0 | 0 | 0 | Normal
2025-08-15 12:00 | 227 | 8 | Winter | 12 | 6.01 | -25.5 | 14.92 | 26 | 528 | 26.93 | 120 | 146.93 | 25.5 | 64.19 | 95 | 80.83 | 0 | 0 | 0 | Normal
2025-08-15 13:00 | 227 | 8 | Winter | 13 | 6.01 | -24 | 14.76 | 82.2 | 218 | 11.12 | 120 | 131.12 | 24 | 65.74 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-15 14:00 | 227 | 8 | Winter | 14 | 6.01 | -22.8 | 8.82 | 35.3 | 241.6 | 12.32 | 21.07 | 33.39 | 22.8 | 68.26 | 81.05 | -34.87 | 0 | 0 | 0 | Battery-supported
2025-08-15 15:00 | 227 | 8 | Winter | 15 | 6.01 | -22 | 8.08 | 34.6 | 0.8 | 0.04 | 13.45 | 13.49 | 22 | 64.02 | 60.84 | -50.53 | 0 | 0 | 0 | Battery-supported
2025-08-15 16:00 | 227 | 8 | Winter | 16 | 6.01 | -22.7 | 4.18 | 36.9 | 0 | 0 | 0.04 | 0.04 | 22.7 | 60.86 | 36.51 | -60.82 | 0 | 0 | 0 | Battery-supported
2025-08-15 17:00 | 227 | 8 | Winter | 17 | 6.01 | -25.4 | 16.63 | 36.2 | 0 | 0 | 120 | 120 | 25.4 | 67.3 | 55.91 | 52.7 | 0 | 0 | 0 | Normal
2025-08-15 18:00 | 227 | 8 | Winter | 18 | 6.01 | -20.6 | 38.28 | 54.3 | 0 | 0 | 0 | 0 | 20.6 | 58.58 | 32.47 | -58.58 | 0 | 0 | 0 | Battery-supported
2025-08-15 19:00 | 227 | 8 | Winter | 19 | 6.01 | -22.2 | 12.98 | 26.2 | 0 | 0 | 119.24 | 119.24 | 22.2 | 68.12 | 51.29 | 51.12 | 0 | 0 | 0 | Normal
2025-08-15 20:00 | 227 | 8 | Winter | 20 | 6.01 | -19.4 | 18.04 | 19.2 | 0 | 0 | 120 | 120 | 19.4 | 68.34 | 70.3 | 51.66 | 0 | 0 | 0 | Normal
2025-08-15 21:00 | 227 | 8 | Winter | 21 | 6.01 | -23.6 | 18.09 | 9.8 | 0 | 0 | 120 | 120 | 23.6 | 58.93 | 92.77 | 61.07 | 0 | 0 | 0 | Normal
2025-08-15 22:00 | 227 | 8 | Winter | 22 | 6.01 | -25.7 | 24.03 | 16.8 | 283.7 | 14.47 | 120 | 134.47 | 25.7 | 63.34 | 95 | 6.06 | 0 | 0 | 0 | Normal
2025-08-15 23:00 | 227 | 8 | Winter | 23 | 6.01 | -22.5 | 5.64 | 26.7 | 452.7 | 23.09 | 1.37 | 24.46 | 22.5 | 54.59 | 82.95 | -30.13 | 0 | 0 | 0 | Battery-supported
2025-08-16 | 228 | 8 | Winter | 0 | 6.19 | -19.8 | 3.2 | 42.6 | 438.2 | 22.35 | 0 | 22.35 | 19.8 | 55.67 | 69.62 | -33.32 | 0 | 0 | 0 | Battery-supported
2025-08-16 01:00 | 228 | 8 | Winter | 1 | 6.19 | -22.6 | 11.42 | 19.9 | 426.1 | 21.73 | 69.53 | 91.26 | 22.6 | 57.3 | 82.12 | 33.96 | 0 | 0 | 0 | Normal
2025-08-16 02:00 | 228 | 8 | Winter | 2 | 6.19 | -23.8 | 9.33 | 81.7 | 89.8 | 4.58 | 27.73 | 32.31 | 23.8 | 62.6 | 70 | -30.29 | 0 | 0 | 0 | Battery-supported
2025-08-16 03:00 | 228 | 8 | Winter | 3 | 6.19 | -25.7 | 36.34 | 77 | 0 | 0 | 0 | 0 | 25.7 | 58.13 | 46.75 | -58.13 | 0 | 0 | 0 | Battery-supported
2025-08-16 04:00 | 228 | 8 | Winter | 4 | 6.19 | -20.3 | 5.03 | 12.1 | 0 | 0 | 0.5 | 0.5 | 20.3 | 54.78 | 25.04 | -54.28 | 0 | 0 | 0 | Battery-supported
2025-08-16 05:00 | 228 | 8 | Winter | 5 | 6.19 | -26.7 | 28.32 | 44.5 | 0 | 0 | 0 | 0 | 26.7 | 57.09 | 15 | -25.09 | 32 | 10.772 | 0 | Diesel-backup
2025-08-16 06:00 | 228 | 8 | Winter | 6 | 6.19 | -26.3 | 9.39 | 55.6 | 0 | 0 | 28.6 | 28.6 | 26.3 | 63.65 | 15 | 0 | 35.05 | 11.662 | 0 | Diesel-backup
2025-08-16 07:00 | 228 | 8 | Winter | 7 | 6.19 | -23.6 | 4.61 | 36.8 | 0 | 0 | 0.19 | 0.19 | 23.6 | 55.84 | 15 | 0 | 55.65 | 17.808 | 0 | Diesel-backup
2025-08-16 08:00 | 228 | 8 | Winter | 8 | 6.19 | -29 | 25.32 | 32.1 | 0 | 0 | 120 | 120 | 29 | 70.5 | 33.22 | 49.5 | 0 | 0 | 0 | Normal
2025-08-16 09:00 | 228 | 8 | Winter | 9 | 6.19 | -22 | 5.69 | 80.2 | 12.7 | 0.65 | 1.47 | 2.12 | 22 | 61.19 | 15 | -45.54 | 13.53 | 4.875 | 0 | Diesel-backup
2025-08-16 10:00 | 228 | 8 | Winter | 10 | 6.19 | -23.3 | 18.08 | 55.5 | 202 | 10.3 | 120 | 130.3 | 23.3 | 65.3 | 38.92 | 65 | 0 | 0 | 0 | Normal
2025-08-16 11:00 | 228 | 8 | Winter | 11 | 6.19 | -22.5 | 11.62 | 15.4 | 507 | 25.86 | 74.93 | 100.79 | 22.5 | 68.12 | 50.94 | 32.67 | 0 | 0 | 0 | Normal
2025-08-16 12:00 | 228 | 8 | Winter | 12 | 6.19 | -22.9 | 28.26 | 31.8 | 499.3 | 25.46 | 0 | 25.46 | 22.9 | 67.08 | 34.29 | -41.62 | 0 | 0 | 0 | Battery-supported
2025-08-16 13:00 | 228 | 8 | Winter | 13 | 6.19 | -24.1 | 20.39 | 100 | 143.3 | 7.31 | 120 | 127.31 | 24.1 | 71.96 | 54.66 | 55.35 | 0 | 0 | 0 | Normal
2025-08-16 14:00 | 228 | 8 | Winter | 14 | 6.19 | -25.7 | 9.23 | 74.5 | 152.7 | 7.79 | 26.33 | 34.12 | 25.7 | 65.83 | 41.98 | -31.71 | 0 | 0 | 0 | Battery-supported
2025-08-16 15:00 | 228 | 8 | Winter | 15 | 6.19 | -23.3 | 25.39 | 65.1 | 16.3 | 0.83 | 120 | 120.83 | 23.3 | 66.08 | 62.13 | 54.75 | 0 | 0 | 0 | Normal
2025-08-16 16:00 | 228 | 8 | Winter | 16 | 6.19 | -24.8 | 13.94 | 0 | 0 | 0 | 120 | 120 | 24.8 | 72.15 | 79.74 | 47.85 | 0 | 0 | 0 | Normal
2025-08-16 17:00 | 228 | 8 | Winter | 17 | 6.19 | -21.3 | 10.63 | 70.9 | 0 | 0 | 50.73 | 50.73 | 21.3 | 60.3 | 75.91 | -9.57 | 0 | 0 | 0 | Battery-supported
2025-08-16 18:00 | 228 | 8 | Winter | 18 | 6.19 | -20.3 | 11.47 | 20 | 0 | 0 | 70.86 | 70.86 | 20.3 | 67.87 | 77.01 | 2.99 | 0 | 0 | 0 | Normal
2025-08-16 19:00 | 228 | 8 | Winter | 19 | 6.19 | -18.7 | 18.5 | 29.7 | 0 | 0 | 120 | 120 | 18.7 | 67.57 | 95 | 48.89 | 0 | 0 | 0 | Normal
2025-08-16 20:00 | 228 | 8 | Winter | 20 | 6.19 | -21.1 | 8.93 | 82.8 | 0 | 0 | 22.41 | 22.41 | 21.1 | 59.47 | 80.18 | -37.06 | 0 | 0 | 0 | Battery-supported
2025-08-16 21:00 | 228 | 8 | Winter | 21 | 6.19 | -19.9 | 7.36 | 76.1 | 0 | 0 | 8.05 | 8.05 | 19.9 | 64.43 | 57.62 | -56.38 | 0 | 0 | 0 | Battery-supported
2025-08-16 22:00 | 228 | 8 | Winter | 22 | 6.19 | -22.7 | 6.26 | 31 | 178 | 9.08 | 2.94 | 12.02 | 22.7 | 56.39 | 39.88 | -44.37 | 0 | 0 | 0 | Battery-supported
2025-08-16 23:00 | 228 | 8 | Winter | 23 | 6.19 | -23.4 | 12.85 | 35.8 | 366.5 | 18.69 | 114.41 | 133.1 | 23.4 | 51.44 | 69.93 | 81.66 | 0 | 0 | 0 | Normal
2025-08-17 | 229 | 8 | Winter | 0 | 6.37 | -21.5 | 6.55 | 37.7 | 438.7 | 22.37 | 3.97 | 26.34 | 21.5 | 51.9 | 59.7 | -25.56 | 0 | 0 | 0 | Battery-supported
2025-08-17 01:00 | 229 | 8 | Winter | 1 | 6.37 | -23.7 | 18.63 | 55.7 | 248.6 | 12.68 | 120 | 132.68 | 23.7 | 57.86 | 87.24 | 74.82 | 0 | 0 | 0 | Normal
2025-08-17 02:00 | 229 | 8 | Winter | 2 | 6.37 | -22.7 | 8.78 | 59.6 | 77.9 | 3.97 | 20.6 | 24.57 | 22.7 | 55.85 | 74.72 | -31.28 | 0 | 0 | 0 | Battery-supported
2025-08-17 03:00 | 229 | 8 | Winter | 3 | 6.37 | -26 | 14.57 | 15.2 | 0 | 0 | 120 | 120 | 26 | 57.64 | 95 | 55.1 | 0 | 0 | 0 | Normal
2025-08-17 04:00 | 229 | 8 | Winter | 4 | 6.37 | -26 | 21.03 | 71 | 0 | 0 | 120 | 120 | 26 | 55.83 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-17 05:00 | 229 | 8 | Winter | 5 | 6.37 | -22.9 | 24.36 | 60.2 | 0 | 0 | 120 | 120 | 22.9 | 52.07 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-17 06:00 | 229 | 8 | Winter | 6 | 6.37 | -22.6 | 12.03 | 92.3 | 0 | 0 | 86.87 | 86.87 | 22.6 | 64 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-17 07:00 | 229 | 8 | Winter | 7 | 6.37 | -26.9 | 2.12 | 34 | 0 | 0 | 0 | 0 | 26.9 | 63.11 | 69.76 | -63.11 | 0 | 0 | 0 | Battery-supported
2025-08-17 08:00 | 229 | 8 | Winter | 8 | 6.37 | -23.3 | 2.23 | 64.7 | 0 | 0 | 0 | 0 | 23.3 | 70.1 | 41.72 | -70.1 | 0 | 0 | 0 | Battery-supported
2025-08-17 09:00 | 229 | 8 | Winter | 9 | 6.37 | -25.9 | 18.34 | 82.3 | 23.1 | 1.18 | 120 | 121.18 | 25.9 | 64.95 | 62.41 | 56.23 | 0 | 0 | 0 | Normal
2025-08-17 10:00 | 229 | 8 | Winter | 10 | 6.37 | -24.5 | 5.41 | 40.2 | 253.1 | 12.91 | 0.98 | 13.89 | 24.5 | 65.72 | 41.68 | -51.83 | 0 | 0 | 0 | Battery-supported
2025-08-17 11:00 | 229 | 8 | Winter | 11 | 6.37 | -21.2 | 8.52 | 73.5 | 259.2 | 13.22 | 17.71 | 30.93 | 21.2 | 59.94 | 30.07 | -29.01 | 0 | 0 | 0 | Battery-supported
2025-08-17 12:00 | 229 | 8 | Winter | 12 | 6.37 | -22.3 | 19.95 | 77.4 | 275.2 | 14.04 | 120 | 134.04 | 22.3 | 63.11 | 56.17 | 70.93 | 0 | 0 | 0 | Normal
2025-08-17 13:00 | 229 | 8 | Winter | 13 | 6.37 | -21.9 | 7.42 | 51.8 | 353.4 | 18.02 | 8.43 | 26.45 | 21.9 | 68.97 | 39.17 | -42.52 | 0 | 0 | 0 | Battery-supported
2025-08-17 14:00 | 229 | 8 | Winter | 14 | 6.37 | -19.1 | 4.18 | 53.9 | 215.9 | 11.01 | 0.04 | 11.05 | 19.1 | 60.18 | 19.51 | -49.13 | 0 | 0 | 0 | Battery-supported
2025-08-17 15:00 | 229 | 8 | Winter | 15 | 6.37 | -24.4 | 8.7 | 64.3 | 31.2 | 1.59 | 19.68 | 21.27 | 24.4 | 66.81 | 15 | -11.29 | 34.25 | 11.432 | 0 | Diesel-backup
2025-08-17 16:00 | 229 | 8 | Winter | 16 | 6.37 | -24.7 | 16.3 | 31.5 | 0 | 0 | 120 | 120 | 24.7 | 64.84 | 35.3 | 55.16 | 0 | 0 | 0 | Normal
2025-08-17 17:00 | 229 | 8 | Winter | 17 | 6.37 | -23.8 | 7.32 | 36.7 | 0 | 0 | 7.8 | 7.8 | 23.8 | 69.71 | 15 | -50.75 | 11.16 | 4.056 | 0 | Diesel-backup
2025-08-17 18:00 | 229 | 8 | Winter | 18 | 6.37 | -22.5 | 14.98 | 63.1 | 0 | 0 | 120 | 120 | 22.5 | 63.06 | 35.95 | 56.94 | 0 | 0 | 0 | Normal
2025-08-17 19:00 | 229 | 8 | Winter | 19 | 6.37 | -27 | 4.28 | 44.4 | 0 | 0 | 0.07 | 0.07 | 27 | 74.91 | 15 | -52.38 | 22.46 | 7.834 | 0 | Diesel-backup
2025-08-17 20:00 | 229 | 8 | Winter | 20 | 6.37 | -22.2 | 6.12 | 16.2 | 0 | 0 | 2.52 | 2.52 | 22.2 | 63.64 | 15 | 0 | 61.12 | 19.558 | 0 | Diesel-backup
2025-08-17 21:00 | 229 | 8 | Winter | 21 | 6.37 | -23 | 8.78 | 33.3 | 0 | 0 | 20.6 | 20.6 | 23 | 67.69 | 15 | 0 | 47.09 | 15.069 | 0 | Diesel-backup
2025-08-17 22:00 | 229 | 8 | Winter | 22 | 6.37 | -20.3 | 21.5 | 28 | 111.2 | 5.67 | 120 | 125.67 | 20.3 | 60.09 | 39.13 | 65.58 | 0 | 0 | 0 | Normal
2025-08-17 23:00 | 229 | 8 | Winter | 23 | 6.37 | -21.4 | 7.94 | 64 | 222.1 | 11.33 | 12.25 | 23.58 | 21.4 | 56.19 | 26.09 | -32.61 | 0 | 0 | 0 | Battery-supported
2025-08-18 | 230 | 8 | Winter | 0 | 6.55 | -23.7 | 7.19 | 6.8 | 536.5 | 27.36 | 7.03 | 34.39 | 23.7 | 58.97 | 16.26 | -24.58 | 0 | 0 | 0 | Battery-supported
2025-08-18 01:00 | 230 | 8 | Winter | 1 | 6.55 | -21.5 | 7.21 | 28.7 | 273.4 | 13.94 | 7.15 | 21.09 | 21.5 | 61.98 | 15 | -3.14 | 37.75 | 12.429 | 0 | Diesel-backup
2025-08-18 02:00 | 230 | 8 | Winter | 2 | 6.55 | -21.6 | 14.95 | 72.1 | 24.3 | 1.24 | 120 | 121.24 | 21.6 | 57.9 | 38.31 | 63.34 | 0 | 0 | 0 | Normal
2025-08-18 03:00 | 230 | 8 | Winter | 3 | 6.55 | -25.2 | 17.21 | 56.3 | 0 | 0 | 120 | 120 | 25.2 | 62.6 | 59.43 | 57.4 | 0 | 0 | 0 | Normal
2025-08-18 04:00 | 230 | 8 | Winter | 4 | 6.55 | -25 | 20.91 | 76.1 | 0 | 0 | 120 | 120 | 25 | 68.46 | 78.4 | 51.54 | 0 | 0 | 0 | Normal
2025-08-18 05:00 | 230 | 8 | Winter | 5 | 6.55 | -29.1 | 30.75 | 47.2 | 0 | 0 | 0 | 0 | 29.1 | 64.93 | 52.43 | -64.93 | 0 | 0 | 0 | Battery-supported
2025-08-18 06:00 | 230 | 8 | Winter | 6 | 6.55 | -26.9 | 12.86 | 57.3 | 0 | 0 | 114.77 | 114.77 | 26.9 | 53.5 | 74.97 | 61.27 | 0 | 0 | 0 | Normal
2025-08-18 07:00 | 230 | 8 | Winter | 7 | 6.55 | -26.3 | 6.6 | 21.8 | 0 | 0 | 4.17 | 4.17 | 26.3 | 61.99 | 51.85 | -57.82 | 0 | 0 | 0 | Battery-supported
2025-08-18 08:00 | 230 | 8 | Winter | 8 | 6.55 | -24.5 | 9.56 | 2.9 | 0 | 0 | 31.15 | 31.15 | 24.5 | 72.19 | 35.43 | -41.04 | 0 | 0 | 0 | Battery-supported
2025-08-18 09:00 | 230 | 8 | Winter | 9 | 6.55 | -26.7 | 5.59 | 10.2 | 80.2 | 4.09 | 1.28 | 5.37 | 26.7 | 70.96 | 15 | -51.08 | 14.51 | 5.211 | 0 | Diesel-backup
2025-08-18 10:00 | 230 | 8 | Winter | 10 | 6.55 | -25.6 | 11.46 | 25 | 306.1 | 15.61 | 70.59 | 86.2 | 25.6 | 63.97 | 23.18 | 22.23 | 0 | 0 | 0 | Normal
2025-08-18 11:00 | 230 | 8 | Winter | 11 | 6.55 | -26.9 | 6.25 | 29.6 | 453 | 23.1 | 2.91 | 26.01 | 26.9 | 69.56 | 15 | -20.45 | 23.1 | 8.039 | 0 | Diesel-backup
2025-08-18 12:00 | 230 | 8 | Winter | 12 | 6.55 | -23.5 | 20.84 | 38.2 | 468.1 | 23.87 | 120 | 143.87 | 23.5 | 72.44 | 41.29 | 71.43 | 0 | 0 | 0 | Normal
2025-08-18 13:00 | 230 | 8 | Winter | 13 | 6.55 | -22.6 | 12.26 | 92.2 | 179.5 | 9.15 | 94.09 | 103.24 | 22.6 | 59.93 | 57.22 | 43.31 | 0 | 0 | 0 | Normal
2025-08-18 14:00 | 230 | 8 | Winter | 14 | 6.55 | -22.3 | 24.72 | 20.6 | 318.8 | 16.26 | 120 | 136.26 | 22.3 | 58.42 | 85.87 | 77.84 | 0 | 0 | 0 | Normal
2025-08-18 15:00 | 230 | 8 | Winter | 15 | 6.55 | -22.8 | 16.85 | 53.2 | 52.2 | 2.66 | 120 | 122.66 | 22.8 | 62.45 | 95 | 24.81 | 0 | 0 | 0 | Normal
2025-08-18 16:00 | 230 | 8 | Winter | 16 | 6.55 | -25.8 | 15.96 | 57.1 | 0 | 0 | 120 | 120 | 25.8 | 73.39 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-18 17:00 | 230 | 8 | Winter | 17 | 6.55 | -23.5 | 4.15 | 87.4 | 0 | 0 | 0.04 | 0.04 | 23.5 | 58.31 | 71.69 | -58.27 | 0 | 0 | 0 | Battery-supported
2025-08-18 18:00 | 230 | 8 | Winter | 18 | 6.55 | -22.8 | 14.93 | 32.6 | 0 | 0 | 120 | 120 | 22.8 | 66.28 | 91.46 | 53.72 | 0 | 0 | 0 | Normal
2025-08-18 19:00 | 230 | 8 | Winter | 19 | 6.55 | -22.6 | 30.37 | 72.5 | 0 | 0 | 0 | 0 | 22.6 | 67.59 | 64.42 | -67.59 | 0 | 0 | 0 | Battery-supported
2025-08-18 20:00 | 230 | 8 | Winter | 20 | 6.55 | -21.5 | 8.09 | 19.3 | 0 | 0 | 13.53 | 13.53 | 21.5 | 64.51 | 44.03 | -50.98 | 0 | 0 | 0 | Battery-supported
2025-08-18 21:00 | 230 | 8 | Winter | 21 | 6.55 | -18.6 | 19.02 | 24.8 | 0 | 0 | 120 | 120 | 18.6 | 47.68 | 70.65 | 72.32 | 0 | 0 | 0 | Normal
2025-08-18 22:00 | 230 | 8 | Winter | 22 | 6.55 | -20.1 | 3.31 | 46.7 | 34.4 | 1.75 | 0 | 1.75 | 20.1 | 55.62 | 49.1 | -53.87 | 0 | 0 | 0 | Battery-supported
2025-08-18 23:00 | 230 | 8 | Winter | 23 | 6.55 | -24.3 | 5.03 | 68.9 | 168.5 | 8.59 | 0.5 | 9.09 | 24.3 | 54.94 | 30.76 | -45.85 | 0 | 0 | 0 | Battery-supported
2025-08-19 | 231 | 8 | Winter | 0 | 6.73 | -20.8 | 9.97 | 23.6 | 418.7 | 21.35 | 37.91 | 59.26 | 20.8 | 56.38 | 31.82 | 2.88 | 0 | 0 | 0 | Normal
2025-08-19 01:00 | 231 | 8 | Winter | 1 | 6.73 | -21.3 | 7.25 | 69.9 | 127.4 | 6.5 | 7.38 | 13.88 | 21.3 | 52.74 | 16.27 | -38.86 | 0 | 0 | 0 | Battery-supported
2025-08-19 02:00 | 231 | 8 | Winter | 2 | 6.73 | -24.8 | 6.18 | 73.4 | 0 | 0 | 2.69 | 2.69 | 24.8 | 61.13 | 15 | -3.19 | 55.25 | 17.681 | 0 | Diesel-backup
2025-08-19 03:00 | 231 | 8 | Winter | 3 | 6.73 | -21.6 | 7.28 | 51.8 | 0 | 0 | 7.56 | 7.56 | 21.6 | 56.4 | 15 | 0 | 48.84 | 15.629 | 0 | Diesel-backup
2025-08-19 04:00 | 231 | 8 | Winter | 4 | 6.73 | -24.2 | 13.95 | 61.7 | 0 | 0 | 120 | 120 | 24.2 | 54.15 | 39.23 | 65.85 | 0 | 0 | 0 | Normal
2025-08-19 05:00 | 231 | 8 | Winter | 5 | 6.73 | -27.2 | 19.12 | 70.6 | 0 | 0 | 120 | 120 | 27.2 | 64.41 | 59.69 | 55.59 | 0 | 0 | 0 | Normal
2025-08-19 06:00 | 231 | 8 | Winter | 6 | 6.73 | -23.4 | 14.65 | 63.6 | 0 | 0 | 120 | 120 | 23.4 | 57.81 | 82.58 | 62.19 | 0 | 0 | 0 | Normal
2025-08-19 07:00 | 231 | 8 | Winter | 7 | 6.73 | -24 | 15.15 | 15.6 | 0 | 0 | 120 | 120 | 24 | 60.27 | 95 | 33.76 | 0 | 0 | 0 | Normal
2025-08-19 08:00 | 231 | 8 | Winter | 8 | 6.73 | -25.1 | 10.24 | 54.3 | 0 | 0 | 42.85 | 42.85 | 25.1 | 68.88 | 84.59 | -26.03 | 0 | 0 | 0 | Battery-supported
2025-08-19 09:00 | 231 | 8 | Winter | 9 | 6.73 | -24.6 | 4.93 | 38.3 | 79.5 | 4.05 | 0.41 | 4.46 | 24.6 | 71.61 | 57.73 | -67.15 | 0 | 0 | 0 | Battery-supported
2025-08-19 10:00 | 231 | 8 | Winter | 10 | 6.73 | -25.9 | 9.75 | 12.5 | 353.8 | 18.04 | 34.17 | 52.21 | 25.9 | 71.2 | 50.13 | -18.99 | 0 | 0 | 0 | Battery-supported
2025-08-19 11:00 | 231 | 8 | Winter | 11 | 6.73 | -22.8 | 11.62 | 63.2 | 308.2 | 15.72 | 74.93 | 90.65 | 22.8 | 67.42 | 58.68 | 23.23 | 0 | 0 | 0 | Normal
2025-08-19 12:00 | 231 | 8 | Winter | 12 | 6.73 | -23.9 | 19.61 | 38.8 | 464.8 | 23.7 | 120 | 143.7 | 23.9 | 59.29 | 89.74 | 84.41 | 0 | 0 | 0 | Normal
2025-08-19 13:00 | 231 | 8 | Winter | 13 | 6.73 | -23.1 | 26.91 | 21.1 | 493.2 | 25.15 | 120 | 145.15 | 23.1 | 64.35 | 95 | 14.28 | 0 | 0 | 0 | Normal
2025-08-19 14:00 | 231 | 8 | Winter | 14 | 6.73 | -22.3 | 13.26 | 38.3 | 278.1 | 14.18 | 120 | 134.18 | 22.3 | 54.74 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-19 15:00 | 231 | 8 | Winter | 15 | 6.73 | -25.2 | 18.46 | 74.4 | 49.3 | 2.51 | 120 | 122.51 | 25.2 | 62.19 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-19 16:00 | 231 | 8 | Winter | 16 | 6.73 | -24.3 | 1.76 | 50.4 | 0 | 0 | 0 | 0 | 24.3 | 71.48 | 66.41 | -71.48 | 0 | 0 | 0 | Battery-supported
2025-08-19 17:00 | 231 | 8 | Winter | 17 | 6.73 | -26.9 | 8.66 | 40.5 | 0 | 0 | 19.23 | 19.23 | 26.9 | 67.56 | 47.08 | -48.33 | 0 | 0 | 0 | Battery-supported
2025-08-19 18:00 | 231 | 8 | Winter | 18 | 6.73 | -20.5 | 10.21 | 68 | 0 | 0 | 42.28 | 42.28 | 20.5 | 67.58 | 36.96 | -25.3 | 0 | 0 | 0 | Battery-supported
2025-08-19 19:00 | 231 | 8 | Winter | 19 | 6.73 | -24.3 | 14.43 | 62 | 0 | 0 | 120 | 120 | 24.3 | 63.66 | 57.69 | 56.34 | 0 | 0 | 0 | Normal
2025-08-19 20:00 | 231 | 8 | Winter | 20 | 6.73 | -21.3 | 27.28 | 41.7 | 0 | 0 | 120 | 120 | 21.3 | 63.25 | 78.57 | 56.75 | 0 | 0 | 0 | Normal
2025-08-19 21:00 | 231 | 8 | Winter | 21 | 6.73 | -20.8 | 12.79 | 24.4 | 0 | 0 | 112.22 | 112.22 | 20.8 | 55.89 | 95 | 44.64 | 0 | 0 | 0 | Normal
2025-08-19 22:00 | 231 | 8 | Winter | 22 | 6.73 | -20.4 | 2.97 | 62.6 | 0 | 0 | 0 | 0 | 20.4 | 61.09 | 70.56 | -61.09 | 0 | 0 | 0 | Battery-supported
2025-08-19 23:00 | 231 | 8 | Winter | 23 | 6.73 | -24.6 | 15.26 | 35.3 | 197.1 | 10.05 | 120 | 130.05 | 24.6 | 63.11 | 95 | 66.4 | 0 | 0 | 0 | Normal
2025-08-20 | 232 | 8 | Winter | 0 | 6.91 | -22.3 | 8.24 | 66.4 | 223 | 11.37 | 14.91 | 26.28 | 22.3 | 54.82 | 83.58 | -28.54 | 0 | 0 | 0 | Battery-supported
2025-08-20 01:00 | 232 | 8 | Winter | 1 | 6.91 | -18.9 | 14.37 | 68.6 | 91.1 | 4.65 | 120 | 124.65 | 18.9 | 51.45 | 95 | 31.02 | 0 | 0 | 0 | Normal
2025-08-20 02:00 | 232 | 8 | Winter | 2 | 6.91 | -19.2 | 15.97 | 91.7 | 0 | 0 | 120 | 120 | 19.2 | 54.48 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-20 03:00 | 232 | 8 | Winter | 3 | 6.91 | -21.2 | 2.8 | 40.4 | 0 | 0 | 0 | 0 | 21.2 | 65.28 | 68.89 | -65.28 | 0 | 0 | 0 | Battery-supported
2025-08-20 04:00 | 232 | 8 | Winter | 4 | 6.91 | -23 | 9.86 | 20.7 | 0 | 0 | 36.01 | 36.01 | 23 | 57.87 | 60.14 | -21.86 | 0 | 0 | 0 | Battery-supported
2025-08-20 05:00 | 232 | 8 | Winter | 5 | 6.91 | -26.2 | 10.09 | 58.1 | 0 | 0 | 40.06 | 40.06 | 26.2 | 57.49 | 53.17 | -17.43 | 0 | 0 | 0 | Battery-supported
2025-08-20 06:00 | 232 | 8 | Winter | 6 | 6.91 | -22.7 | 12.67 | 22.8 | 0 | 0 | 107.92 | 107.92 | 22.7 | 54.18 | 72.95 | 53.74 | 0 | 0 | 0 | Normal
2025-08-20 07:00 | 232 | 8 | Winter | 7 | 6.91 | -24.7 | 6.49 | 25.7 | 0 | 0 | 3.74 | 3.74 | 24.7 | 58.55 | 51.02 | -54.81 | 0 | 0 | 0 | Battery-supported
2025-08-20 08:00 | 232 | 8 | Winter | 8 | 6.91 | -23.2 | 5.31 | 77.8 | 0 | 0 | 0.83 | 0.83 | 23.2 | 67.07 | 24.53 | -66.24 | 0 | 0 | 0 | Battery-supported
2025-08-20 09:00 | 232 | 8 | Winter | 9 | 6.91 | -25.8 | 26.98 | 65.9 | 68.1 | 3.47 | 120 | 123.47 | 25.8 | 64.78 | 46.13 | 58.69 | 0 | 0 | 0 | Normal
2025-08-20 10:00 | 232 | 8 | Winter | 10 | 6.91 | -24.6 | 11.91 | 5.2 | 387.1 | 19.74 | 83.25 | 102.99 | 24.6 | 71 | 57.9 | 31.99 | 0 | 0 | 0 | Normal
2025-08-20 11:00 | 232 | 8 | Winter | 11 | 6.91 | -23.6 | 5.7 | 45.3 | 389 | 19.84 | 1.49 | 21.33 | 23.6 | 63.58 | 41 | -42.25 | 0 | 0 | 0 | Battery-supported
2025-08-20 12:00 | 232 | 8 | Winter | 12 | 6.91 | -23.2 | 7.38 | 73 | 296.9 | 15.14 | 8.18 | 23.32 | 23.2 | 71 | 21.93 | -47.68 | 0 | 0 | 0 | Battery-supported
2025-08-20 13:00 | 232 | 8 | Winter | 13 | 6.91 | -22.2 | 27.69 | 24.1 | 482.7 | 24.62 | 120 | 144.62 | 22.2 | 65.84 | 50.92 | 78.78 | 0 | 0 | 0 | Normal
2025-08-20 14:00 | 232 | 8 | Winter | 14 | 6.91 | -24.2 | 21.76 | 30.9 | 309.4 | 15.78 | 120 | 135.78 | 24.2 | 65.48 | 76.79 | 70.3 | 0 | 0 | 0 | Normal
2025-08-20 15:00 | 232 | 8 | Winter | 15 | 6.91 | -25.5 | 6.85 | 31.8 | 102.5 | 5.23 | 5.26 | 10.49 | 25.5 | 56.86 | 58.24 | -46.37 | 0 | 0 | 0 | Battery-supported
2025-08-20 16:00 | 232 | 8 | Winter | 16 | 6.91 | -18.6 | 4.97 | 65.1 | 0 | 0 | 0.44 | 0.44 | 18.6 | 59.8 | 34.5 | -59.36 | 0 | 0 | 0 | Battery-supported
2025-08-20 17:00 | 232 | 8 | Winter | 17 | 6.91 | -16.4 | 5.23 | 100 | 0 | 0 | 0.72 | 0.72 | 16.4 | 59.09 | 15 | -48.74 | 9.63 | 3.518 | 0 | Diesel-backup
2025-08-20 18:00 | 232 | 8 | Winter | 18 | 6.91 | -20.7 | 20.44 | 23.6 | 0 | 0 | 120 | 120 | 20.7 | 63.57 | 35.77 | 56.43 | 0 | 0 | 0 | Normal
2025-08-20 19:00 | 232 | 8 | Winter | 19 | 6.91 | -24.4 | 7.89 | 56.8 | 0 | 0 | 11.84 | 11.84 | 24.4 | 69.44 | 15 | -51.92 | 5.68 | 2.105 | 0 | Diesel-backup
2025-08-20 20:00 | 232 | 8 | Winter | 20 | 6.91 | -23.1 | 3.59 | 21.8 | 0 | 0 | 0 | 0 | 23.1 | 64.23 | 15 | 0 | 64.23 | 20.554 | 0 | Diesel-backup
2025-08-20 21:00 | 232 | 8 | Winter | 21 | 6.91 | -20.4 | 7.53 | 67.4 | 0 | 0 | 9.16 | 9.16 | 20.4 | 57.49 | 15 | 0 | 48.33 | 15.466 | 0 | Diesel-backup
2025-08-20 22:00 | 232 | 8 | Winter | 22 | 6.91 | -18.7 | 12.59 | 61.5 | 0 | 0 | 105.12 | 105.12 | 18.7 | 49.76 | 35.37 | 55.36 | 0 | 0 | 0 | Normal
2025-08-20 23:00 | 232 | 8 | Winter | 23 | 6.91 | -24.6 | 9.75 | 67.7 | 92.3 | 4.71 | 34.17 | 38.88 | 24.6 | 63.32 | 25.6 | -24.44 | 0 | 0 | 0 | Battery-supported
2025-08-21 | 233 | 8 | Winter | 0 | 7.08 | -22.4 | 21.94 | 56.2 | 217.5 | 11.09 | 120 | 131.09 | 22.4 | 61.18 | 51.32 | 69.91 | 0 | 0 | 0 | Normal
2025-08-21 01:00 | 233 | 8 | Winter | 1 | 7.08 | -22 | 12.66 | 17.3 | 94.7 | 4.83 | 107.57 | 112.4 | 22 | 58.05 | 71.32 | 54.35 | 0 | 0 | 0 | Normal
2025-08-21 02:00 | 233 | 8 | Winter | 2 | 7.08 | -20.9 | 13.72 | 32.2 | 0 | 0 | 120 | 120 | 20.9 | 58.72 | 93.88 | 61.28 | 0 | 0 | 0 | Normal
2025-08-21 03:00 | 233 | 8 | Winter | 3 | 7.08 | -24 | 17.75 | 31.7 | 0 | 0 | 120 | 120 | 24 | 57.56 | 95 | 3.06 | 0 | 0 | 0 | Normal
2025-08-21 04:00 | 233 | 8 | Winter | 4 | 7.08 | -27 | 17.21 | 68.4 | 0 | 0 | 120 | 120 | 27 | 61.06 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-21 05:00 | 233 | 8 | Winter | 5 | 7.08 | -22.5 | 7.49 | 15.6 | 0 | 0 | 8.89 | 8.89 | 22.5 | 56.32 | 76.03 | -47.43 | 0 | 0 | 0 | Battery-supported
2025-08-21 06:00 | 233 | 8 | Winter | 6 | 7.08 | -21.7 | 5.02 | 79.2 | 0 | 0 | 0.49 | 0.49 | 21.7 | 61.68 | 51.55 | -61.19 | 0 | 0 | 0 | Battery-supported
2025-08-21 07:00 | 233 | 8 | Winter | 7 | 7.08 | -24.5 | 12.06 | 46 | 0 | 0 | 87.79 | 87.79 | 24.5 | 60.08 | 61.75 | 27.71 | 0 | 0 | 0 | Normal
2025-08-21 08:00 | 233 | 8 | Winter | 8 | 7.08 | -23.4 | 11.07 | 43.6 | 0 | 0 | 60.72 | 60.72 | 23.4 | 63.12 | 60.79 | -2.4 | 0 | 0 | 0 | Battery-supported
2025-08-21 09:00 | 233 | 8 | Winter | 9 | 7.08 | -25.3 | 12.72 | 43 | 105.7 | 5.39 | 109.7 | 115.09 | 25.3 | 67.85 | 78.17 | 47.24 | 0 | 0 | 0 | Normal
2025-08-21 10:00 | 233 | 8 | Winter | 10 | 7.08 | -26 | 13.37 | 34.3 | 307.8 | 15.7 | 120 | 135.7 | 26 | 66.88 | 95 | 45.72 | 0 | 0 | 0 | Normal
2025-08-21 11:00 | 233 | 8 | Winter | 11 | 7.08 | -21.6 | 25.77 | 77.5 | 248 | 12.65 | 120 | 132.65 | 21.6 | 65.1 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-21 12:00 | 233 | 8 | Winter | 12 | 7.08 | -22.7 | 8.83 | 80 | 262.4 | 13.38 | 21.19 | 34.57 | 22.7 | 64.83 | 82.9 | -30.26 | 0 | 0 | 0 | Battery-supported
2025-08-21 13:00 | 233 | 8 | Winter | 13 | 7.08 | -22.1 | 13.69 | 50 | 370.3 | 18.89 | 120 | 138.89 | 22.1 | 59.47 | 95 | 32.89 | 0 | 0 | 0 | Normal
2025-08-21 14:00 | 233 | 8 | Winter | 14 | 7.08 | -19.5 | 5.01 | 58.6 | 232.3 | 11.85 | 0.48 | 12.33 | 19.5 | 58 | 76.73 | -45.67 | 0 | 0 | 0 | Battery-supported
2025-08-21 15:00 | 233 | 8 | Winter | 15 | 7.08 | -24.8 | 6.15 | 24 | 128 | 6.53 | 2.6 | 9.13 | 24.8 | 66.1 | 53.94 | -56.97 | 0 | 0 | 0 | Battery-supported
2025-08-21 16:00 | 233 | 8 | Winter | 16 | 7.08 | -23.3 | 10.64 | 7.3 | 0 | 0 | 50.95 | 50.95 | 23.3 | 71.61 | 45.68 | -20.66 | 0 | 0 | 0 | Battery-supported
2025-08-21 17:00 | 233 | 8 | Winter | 17 | 7.08 | -21.4 | 5.56 | 13.6 | 0 | 0 | 1.22 | 1.22 | 21.4 | 56.87 | 23.42 | -55.65 | 0 | 0 | 0 | Battery-supported
2025-08-21 18:00 | 233 | 8 | Winter | 18 | 7.08 | -22.8 | 15.38 | 35.8 | 0 | 0 | 120 | 120 | 22.8 | 67.19 | 42.85 | 52.81 | 0 | 0 | 0 | Normal
2025-08-21 19:00 | 233 | 8 | Winter | 19 | 7.08 | -19.7 | 14.04 | 27.4 | 0 | 0 | 120 | 120 | 19.7 | 68.93 | 61.65 | 51.07 | 0 | 0 | 0 | Normal
2025-08-21 20:00 | 233 | 8 | Winter | 20 | 7.08 | -21.7 | 6.9 | 48.1 | 0 | 0 | 5.5 | 5.5 | 21.7 | 68.56 | 36.42 | -63.06 | 0 | 0 | 0 | Battery-supported
2025-08-21 21:00 | 233 | 8 | Winter | 21 | 7.08 | -23.6 | 9.24 | 27.4 | 0 | 0 | 26.47 | 26.47 | 23.6 | 58.5 | 23.61 | -32.03 | 0 | 0 | 0 | Battery-supported
2025-08-21 22:00 | 233 | 8 | Winter | 22 | 7.08 | -21.4 | 20.52 | 83.5 | 0 | 0 | 120 | 120 | 21.4 | 55.49 | 47.35 | 64.51 | 0 | 0 | 0 | Normal
2025-08-21 23:00 | 233 | 8 | Winter | 23 | 7.08 | -21.4 | 11.97 | 26.5 | 87.2 | 4.45 | 85.05 | 89.5 | 21.4 | 58.96 | 58.59 | 30.54 | 0 | 0 | 0 | Normal
2025-08-22 | 234 | 8 | Winter | 0 | 7.26 | -19.9 | 34.31 | 72 | 140.4 | 7.16 | 0 | 7.16 | 19.9 | 60.93 | 37.08 | -53.77 | 0 | 0 | 0 | Battery-supported
2025-08-22 01:00 | 234 | 8 | Winter | 1 | 7.26 | -21.5 | 9.23 | 44.5 | 22.1 | 1.13 | 26.33 | 27.46 | 21.5 | 59.37 | 24.32 | -31.91 | 0 | 0 | 0 | Battery-supported
2025-08-22 02:00 | 234 | 8 | Winter | 2 | 7.26 | -21.7 | 9.91 | 59.6 | 0 | 0 | 36.86 | 36.86 | 21.7 | 57.44 | 16.09 | -20.58 | 0 | 0 | 0 | Battery-supported
2025-08-22 03:00 | 234 | 8 | Winter | 3 | 7.26 | -22.4 | 10.62 | 6.1 | 0 | 0 | 50.52 | 50.52 | 22.4 | 62.24 | 15 | -2.72 | 9 | 3.296 | 0 | Diesel-backup
2025-08-22 04:00 | 234 | 8 | Winter | 4 | 7.26 | -23.9 | 3.24 | 55.1 | 0 | 0 | 0 | 0 | 23.9 | 59.61 | 15 | 0 | 59.61 | 19.075 | 0 | Diesel-backup
2025-08-22 05:00 | 234 | 8 | Winter | 5 | 7.26 | -25.3 | 9.63 | 56.5 | 0 | 0 | 32.24 | 32.24 | 25.3 | 60.67 | 15 | 0 | 28.43 | 9.701 | 0 | Diesel-backup
2025-08-22 06:00 | 234 | 8 | Winter | 6 | 7.26 | -23.4 | 9.42 | 67.7 | 0 | 0 | 29.04 | 29.04 | 23.4 | 60.94 | 15 | 0 | 31.9 | 10.743 | 0 | Diesel-backup
2025-08-22 07:00 | 234 | 8 | Winter | 7 | 7.26 | -24.9 | 16.18 | 56.9 | 0 | 0 | 120 | 120 | 24.9 | 57.35 | 38.06 | 62.65 | 0 | 0 | 0 | Normal
2025-08-22 08:00 | 234 | 8 | Winter | 8 | 7.26 | -20.5 | 20.97 | 56.7 | 0 | 0 | 120 | 120 | 20.5 | 75.46 | 54.45 | 44.54 | 0 | 0 | 0 | Normal
2025-08-22 09:00 | 234 | 8 | Winter | 9 | 7.26 | -21.2 | 8.73 | 87.7 | 60.3 | 3.08 | 20.02 | 23.1 | 21.2 | 64.83 | 37.75 | -41.73 | 0 | 0 | 0 | Battery-supported
2025-08-22 10:00 | 234 | 8 | Winter | 10 | 7.26 | -22.6 | 2.09 | 35.9 | 310.7 | 15.85 | 0 | 15.85 | 22.6 | 64.86 | 18.15 | -49.01 | 0 | 0 | 0 | Battery-supported
2025-08-22 11:00 | 234 | 8 | Winter | 11 | 7.26 | -22.9 | 11.64 | 16.5 | 521.9 | 26.62 | 75.49 | 102.11 | 22.9 | 69.28 | 30.23 | 32.83 | 0 | 0 | 0 | Normal
2025-08-22 12:00 | 234 | 8 | Winter | 12 | 7.26 | -23.7 | 5.5 | 80.2 | 261.5 | 13.34 | 1.12 | 14.46 | 23.7 | 71.09 | 15 | -38.08 | 18.55 | 6.565 | 0 | Diesel-backup
2025-08-22 13:00 | 234 | 8 | Winter | 13 | 7.26 | -25.9 | 12.27 | 13.8 | 533.7 | 27.22 | 94.41 | 121.63 | 25.9 | 66.16 | 35.41 | 55.47 | 0 | 0 | 0 | Normal
2025-08-22 14:00 | 234 | 8 | Winter | 14 | 7.26 | -23.2 | 12.07 | 68.4 | 207 | 10.56 | 88.1 | 98.66 | 23.2 | 59.36 | 49.88 | 39.3 | 0 | 0 | 0 | Normal
2025-08-22 15:00 | 234 | 8 | Winter | 15 | 7.26 | -22.1 | 6.55 | 92.3 | 54.1 | 2.76 | 3.97 | 6.73 | 22.1 | 63.78 | 27.06 | -57.05 | 0 | 0 | 0 | Battery-supported
2025-08-22 16:00 | 234 | 8 | Winter | 16 | 7.26 | -21.5 | 11.7 | 39.6 | 0 | 0 | 77.17 | 77.17 | 21.5 | 65.64 | 31.3 | 11.53 | 0 | 0 | 0 | Normal
2025-08-22 17:00 | 234 | 8 | Winter | 17 | 7.26 | -20.6 | 3.67 | 51.1 | 0 | 0 | 0 | 0 | 20.6 | 60.63 | 15 | -40.75 | 19.88 | 7.002 | 0 | Diesel-backup
2025-08-22 18:00 | 234 | 8 | Winter | 18 | 7.26 | -19.4 | 12.72 | 75.1 | 0 | 0 | 109.7 | 109.7 | 19.4 | 62.3 | 32.44 | 47.4 | 0 | 0 | 0 | Normal
2025-08-22 19:00 | 234 | 8 | Winter | 19 | 7.26 | -22.8 | 17.07 | 77.1 | 0 | 0 | 120 | 120 | 22.8 | 65.29 | 52.58 | 54.71 | 0 | 0 | 0 | Normal
2025-08-22 20:00 | 234 | 8 | Winter | 20 | 7.26 | -22.7 | 14.39 | 22.2 | 0 | 0 | 120 | 120 | 22.7 | 59.16 | 74.97 | 60.84 | 0 | 0 | 0 | Normal
2025-08-22 21:00 | 234 | 8 | Winter | 21 | 7.26 | -18.1 | 7.59 | 39.1 | 0 | 0 | 9.58 | 9.58 | 18.1 | 55.74 | 56.5 | -46.16 | 0 | 0 | 0 | Battery-supported
2025-08-22 22:00 | 234 | 8 | Winter | 22 | 7.26 | -19.7 | 16.34 | 44 | 0 | 0 | 120 | 120 | 19.7 | 58.29 | 79.21 | 61.71 | 0 | 0 | 0 | Normal
2025-08-22 23:00 | 234 | 8 | Winter | 23 | 7.26 | -22.5 | 15.26 | 87 | 11.5 | 0.59 | 120 | 120.59 | 22.5 | 58.29 | 95 | 42.91 | 0 | 0 | 0 | Normal
2025-08-23 | 235 | 8 | Winter | 0 | 7.43 | -22.1 | 15.64 | 34.2 | 173.6 | 8.85 | 120 | 128.85 | 22.1 | 58.65 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-23 01:00 | 235 | 8 | Winter | 1 | 7.43 | -22.4 | 22.38 | 77.6 | 0 | 0 | 120 | 120 | 22.4 | 54.79 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-23 02:00 | 235 | 8 | Winter | 2 | 7.43 | -22.5 | 13.43 | 63.8 | 0 | 0 | 120 | 120 | 22.5 | 57.02 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-23 03:00 | 235 | 8 | Winter | 3 | 7.43 | -21.9 | 5.11 | 51.5 | 0 | 0 | 0.58 | 0.58 | 21.9 | 59.59 | 71.4 | -59.01 | 0 | 0 | 0 | Battery-supported
2025-08-23 04:00 | 235 | 8 | Winter | 4 | 7.43 | -17.8 | 5.73 | 28.1 | 0 | 0 | 1.55 | 1.55 | 17.8 | 47.33 | 53.08 | -45.78 | 0 | 0 | 0 | Battery-supported
2025-08-23 05:00 | 235 | 8 | Winter | 5 | 7.43 | -23.2 | 13.43 | 65.9 | 0 | 0 | 120 | 120 | 23.2 | 54.11 | 77.33 | 65.89 | 0 | 0 | 0 | Normal
2025-08-23 06:00 | 235 | 8 | Winter | 6 | 7.43 | -22.4 | 2.86 | 50.5 | 0 | 0 | 0 | 0 | 22.4 | 51.7 | 56.65 | -51.7 | 0 | 0 | 0 | Battery-supported
2025-08-23 07:00 | 235 | 8 | Winter | 7 | 7.43 | -27.7 | 9.52 | 74.2 | 0 | 0 | 30.54 | 30.54 | 27.7 | 69.44 | 41.09 | -38.9 | 0 | 0 | 0 | Battery-supported
2025-08-23 08:00 | 235 | 8 | Winter | 8 | 7.43 | -25.2 | 8.43 | 10.7 | 0 | 0 | 16.77 | 16.77 | 25.2 | 67.09 | 20.96 | -50.32 | 0 | 0 | 0 | Battery-supported
2025-08-23 09:00 | 235 | 8 | Winter | 9 | 7.43 | -21.3 | 14.97 | 31.2 | 149.3 | 7.61 | 120 | 127.61 | 21.3 | 70.05 | 42.15 | 57.56 | 0 | 0 | 0 | Normal
2025-08-23 10:00 | 235 | 8 | Winter | 10 | 7.43 | -23 | 4.46 | 40.4 | 303.2 | 15.46 | 0.12 | 15.58 | 23 | 65.7 | 22.1 | -50.12 | 0 | 0 | 0 | Battery-supported
2025-08-23 11:00 | 235 | 8 | Winter | 11 | 7.43 | -33.3 | 15.15 | 73.7 | 267.5 | 13.64 | 120 | 133.64 | 33.3 | 83.48 | 40.56 | 50.16 | 0 | 0 | 0 | Normal
2025-08-23 12:00 | 235 | 8 | Winter | 12 | 7.43 | -21.9 | 9.17 | 75 | 287.1 | 14.64 | 25.51 | 40.15 | 21.9 | 69.83 | 28.68 | -29.68 | 0 | 0 | 0 | Battery-supported
2025-08-23 13:00 | 235 | 8 | Winter | 13 | 7.43 | -18.8 | 12.91 | 49.9 | 374.3 | 19.09 | 116.62 | 135.71 | 18.8 | 59.06 | 56.89 | 76.65 | 0 | 0 | 0 | Normal
2025-08-23 14:00 | 235 | 8 | Winter | 14 | 7.43 | -27 | 4.74 | 6.3 | 414.4 | 21.13 | 0.27 | 21.4 | 27 | 70.45 | 37.27 | -49.05 | 0 | 0 | 0 | Battery-supported
2025-08-23 15:00 | 235 | 8 | Winter | 15 | 7.43 | -18.9 | 15.5 | 33.1 | 146.5 | 7.47 | 120 | 127.47 | 18.9 | 57.88 | 62.88 | 69.59 | 0 | 0 | 0 | Normal
2025-08-23 16:00 | 235 | 8 | Winter | 16 | 7.43 | -27.9 | 18.79 | 99.5 | 0 | 0 | 120 | 120 | 27.9 | 73.55 | 79.97 | 46.45 | 0 | 0 | 0 | Normal
2025-08-23 17:00 | 235 | 8 | Winter | 17 | 7.43 | -19.5 | 45 | 48.8 | 0 | 0 | 0 | 0 | 19.5 | 66.81 | 53.25 | -66.81 | 0 | 0 | 0 | Battery-supported
2025-08-23 18:00 | 235 | 8 | Winter | 18 | 7.43 | -21.3 | 12.41 | 47.4 | 0 | 0 | 99 | 99 | 21.3 | 71.82 | 63.25 | 27.18 | 0 | 0 | 0 | Normal
2025-08-23 19:00 | 235 | 8 | Winter | 19 | 7.43 | -26.3 | 18.41 | 26.4 | 0 | 0 | 120 | 120 | 26.3 | 74.81 | 79.88 | 45.19 | 0 | 0 | 0 | Normal
2025-08-23 20:00 | 235 | 8 | Winter | 20 | 7.43 | -20.1 | 5.52 | 23.4 | 0 | 0 | 1.15 | 1.15 | 20.1 | 64.83 | 54.41 | -63.68 | 0 | 0 | 0 | Battery-supported
2025-08-23 21:00 | 235 | 8 | Winter | 21 | 7.43 | -18.6 | 21.69 | 12.2 | 0 | 0 | 120 | 120 | 18.6 | 55.01 | 78.33 | 64.99 | 0 | 0 | 0 | Normal
2025-08-23 22:00 | 235 | 8 | Winter | 22 | 7.43 | -20.5 | 3.86 | 13.9 | 0 | 0 | 0.01 | 0.01 | 20.5 | 54.51 | 56.53 | -54.5 | 0 | 0 | 0 | Battery-supported
2025-08-23 23:00 | 235 | 8 | Winter | 23 | 7.43 | -20.2 | 26.62 | 84 | 0 | 0 | 120 | 120 | 20.2 | 62.49 | 77.69 | 57.51 | 0 | 0 | 0 | Normal
2025-08-24 | 236 | 8 | Winter | 0 | 7.6 | -22.6 | 11.66 | 84.6 | 59.4 | 3.03 | 76.05 | 79.08 | 22.6 | 54.14 | 86.87 | 24.94 | 0 | 0 | 0 | Normal
2025-08-24 01:00 | 236 | 8 | Winter | 1 | 7.6 | -26.2 | 4.13 | 40.8 | 0 | 0 | 0.03 | 0.03 | 26.2 | 57.05 | 64.06 | -57.02 | 0 | 0 | 0 | Battery-supported
2025-08-24 02:00 | 236 | 8 | Winter | 2 | 7.6 | -20.9 | 8.56 | 25.5 | 0 | 0 | 18.13 | 18.13 | 20.9 | 51.51 | 50.71 | -33.38 | 0 | 0 | 0 | Battery-supported
2025-08-24 03:00 | 236 | 8 | Winter | 3 | 7.6 | -19 | 18.26 | 57.8 | 0 | 0 | 120 | 120 | 19 | 58.3 | 73.41 | 61.7 | 0 | 0 | 0 | Normal
2025-08-24 04:00 | 236 | 8 | Winter | 4 | 7.6 | -20.7 | 9.61 | 32.2 | 0 | 0 | 31.93 | 31.93 | 20.7 | 59.55 | 62.37 | -27.62 | 0 | 0 | 0 | Battery-supported
2025-08-24 05:00 | 236 | 8 | Winter | 5 | 7.6 | -27.9 | 9.53 | 83.4 | 0 | 0 | 30.69 | 30.69 | 27.9 | 64.68 | 48.77 | -33.99 | 0 | 0 | 0 | Battery-supported
2025-08-24 06:00 | 236 | 8 | Winter | 6 | 7.6 | -27.1 | 17.3 | 64.6 | 0 | 0 | 120 | 120 | 27.1 | 63.35 | 69.62 | 56.65 | 0 | 0 | 0 | Normal
2025-08-24 07:00 | 236 | 8 | Winter | 7 | 7.6 | -25.8 | 10.11 | 0 | 0 | 0 | 40.42 | 40.42 | 25.8 | 56.07 | 63.36 | -15.65 | 0 | 0 | 0 | Battery-supported
2025-08-24 08:00 | 236 | 8 | Winter | 8 | 7.6 | -27.5 | 20.88 | 75.8 | 0 | 0 | 120 | 120 | 27.5 | 71.59 | 81.17 | 48.41 | 0 | 0 | 0 | Normal
2025-08-24 09:00 | 236 | 8 | Winter | 9 | 7.6 | -23.8 | 7.41 | 42.2 | 145.4 | 7.42 | 8.37 | 15.79 | 23.8 | 71.73 | 58.8 | -55.94 | 0 | 0 | 0 | Battery-supported
2025-08-24 10:00 | 236 | 8 | Winter | 10 | 7.6 | -22.9 | 3.03 | 49 | 280.7 | 14.32 | 0 | 14.32 | 22.9 | 61.57 | 39.9 | -47.25 | 0 | 0 | 0 | Battery-supported
2025-08-24 11:00 | 236 | 8 | Winter | 11 | 7.6 | -26.7 | 10.48 | 20.7 | 507.4 | 25.88 | 47.6 | 73.48 | 26.7 | 64.82 | 43.08 | 8.66 | 0 | 0 | 0 | Normal
2025-08-24 12:00 | 236 | 8 | Winter | 12 | 7.6 | -21.5 | 11.25 | 30.2 | 507.3 | 25.87 | 65.15 | 91.02 | 21.5 | 65.75 | 52.38 | 25.27 | 0 | 0 | 0 | Normal
2025-08-24 13:00 | 236 | 8 | Winter | 13 | 7.6 | -21.5 | 7.22 | 65.5 | 305.6 | 15.59 | 7.21 | 22.8 | 21.5 | 67.56 | 34.48 | -44.76 | 0 | 0 | 0 | Battery-supported
2025-08-24 14:00 | 236 | 8 | Winter | 14 | 7.6 | -23.7 | 12.67 | 49.7 | 278.5 | 14.2 | 107.92 | 122.12 | 23.7 | 69.96 | 53.67 | 52.16 | 0 | 0 | 0 | Normal
2025-08-24 15:00 | 236 | 8 | Winter | 15 | 7.6 | -22.5 | 3.42 | 90.8 | 67.9 | 3.46 | 0 | 3.46 | 22.5 | 70.34 | 26.92 | -66.88 | 0 | 0 | 0 | Battery-supported
2025-08-24 16:00 | 236 | 8 | Winter | 16 | 7.6 | -26 | 12.89 | 59.6 | 0 | 0 | 115.88 | 115.88 | 26 | 69.64 | 43.94 | 46.24 | 0 | 0 | 0 | Normal
2025-08-24 17:00 | 236 | 8 | Winter | 17 | 7.6 | -22.1 | 4.93 | 22 | 0 | 0 | 0.41 | 0.41 | 22.1 | 58.47 | 20.71 | -58.06 | 0 | 0 | 0 | Battery-supported
2025-08-24 18:00 | 236 | 8 | Winter | 18 | 7.6 | -21.1 | 4.12 | 69.9 | 0 | 0 | 0.03 | 0.03 | 21.1 | 66.16 | 15 | -14.28 | 51.85 | 16.591 | 0 | Diesel-backup
2025-08-24 19:00 | 236 | 8 | Winter | 19 | 7.6 | -20.6 | 11.06 | 72.1 | 0 | 0 | 60.47 | 60.47 | 20.6 | 68.35 | 15 | 0 | 7.88 | 2.896 | 0 | Diesel-backup
2025-08-24 20:00 | 236 | 8 | Winter | 20 | 7.6 | -20.1 | 3.89 | 53.7 | 0 | 0 | 0.01 | 0.01 | 20.1 | 60.61 | 15 | 0 | 60.6 | 19.392 | 0 | Diesel-backup
2025-08-24 21:00 | 236 | 8 | Winter | 21 | 7.6 | -20.5 | 2.29 | 46.1 | 0 | 0 | 0 | 0 | 20.5 | 54.95 | 15 | 0 | 54.95 | 17.584 | 0 | Diesel-backup
2025-08-24 22:00 | 236 | 8 | Winter | 22 | 7.6 | -21.7 | 13.91 | 46 | 0 | 0 | 120 | 120 | 21.7 | 47.99 | 41.5 | 72.01 | 0 | 0 | 0 | Normal
2025-08-24 23:00 | 236 | 8 | Winter | 23 | 7.6 | -20.8 | 5.32 | 30.9 | 0 | 0 | 0.84 | 0.84 | 20.8 | 54.68 | 19.96 | -53.84 | 0 | 0 | 0 | Battery-supported
2025-08-25 | 237 | 8 | Winter | 0 | 7.76 | -19.4 | 14.72 | 58 | 52.7 | 2.69 | 120 | 122.69 | 19.4 | 60.79 | 42.74 | 61.9 | 0 | 0 | 0 | Normal
2025-08-25 01:00 | 237 | 8 | Winter | 1 | 7.76 | -22.2 | 8.91 | 31.8 | 0 | 0 | 22.16 | 22.16 | 22.2 | 55.42 | 29.44 | -33.26 | 0 | 0 | 0 | Battery-supported
2025-08-25 02:00 | 237 | 8 | Winter | 2 | 7.76 | -21.6 | 11.03 | 63.9 | 0 | 0 | 59.76 | 59.76 | 21.6 | 52.38 | 32.15 | 7.38 | 0 | 0 | 0 | Normal
2025-08-25 03:00 | 237 | 8 | Winter | 3 | 7.76 | -23.1 | 18.39 | 53.5 | 0 | 0 | 120 | 120 | 23.1 | 65.94 | 52.05 | 54.06 | 0 | 0 | 0 | Normal
2025-08-25 04:00 | 237 | 8 | Winter | 4 | 7.76 | -24.5 | 13.44 | 43.4 | 0 | 0 | 120 | 120 | 24.5 | 61.96 | 73.41 | 58.04 | 0 | 0 | 0 | Normal
2025-08-25 05:00 | 237 | 8 | Winter | 5 | 7.76 | -22.2 | 14.91 | 37.4 | 0 | 0 | 120 | 120 | 22.2 | 59.1 | 95 | 58.68 | 0 | 0 | 0 | Normal
2025-08-25 06:00 | 237 | 8 | Winter | 6 | 7.76 | -24.9 | 14.59 | 74.9 | 0 | 0 | 120 | 120 | 24.9 | 60.52 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-25 07:00 | 237 | 8 | Winter | 7 | 7.76 | -22.9 | 6.78 | 65.8 | 0 | 0 | 4.94 | 4.94 | 22.9 | 55.2 | 74.9 | -50.26 | 0 | 0 | 0 | Battery-supported
2025-08-25 08:00 | 237 | 8 | Winter | 8 | 7.76 | -23.8 | 13.08 | 55.4 | 0 | 0 | 120 | 120 | 23.8 | 65.75 | 94.86 | 54.25 | 0 | 0 | 0 | Normal
2025-08-25 09:00 | 237 | 8 | Winter | 9 | 7.76 | -24.4 | 5.78 | 40.4 | 159.7 | 8.14 | 1.66 | 9.8 | 24.4 | 74.05 | 69.16 | -64.25 | 0 | 0 | 0 | Battery-supported
2025-08-25 10:00 | 237 | 8 | Winter | 10 | 7.76 | -24.4 | 13.1 | 83 | 170.9 | 8.72 | 120 | 128.72 | 24.4 | 64.65 | 92.74 | 64.07 | 0 | 0 | 0 | Normal
2025-08-25 11:00 | 237 | 8 | Winter | 11 | 7.76 | -24.5 | 8.65 | 64.8 | 310 | 15.81 | 19.12 | 34.93 | 24.5 | 72.96 | 77.53 | -38.03 | 0 | 0 | 0 | Battery-supported
2025-08-25 12:00 | 237 | 8 | Winter | 12 | 7.76 | -26.7 | 9.77 | 49.2 | 414.1 | 21.12 | 34.5 | 55.62 | 26.7 | 71.1 | 71.33 | -15.48 | 0 | 0 | 0 | Battery-supported
2025-08-25 13:00 | 237 | 8 | Winter | 13 | 7.76 | -21.9 | 24.83 | 35.7 | 441.4 | 22.51 | 120 | 142.51 | 21.9 | 66.32 | 95 | 64.31 | 0 | 0 | 0 | Normal
2025-08-25 14:00 | 237 | 8 | Winter | 14 | 7.76 | -21.8 | 14.24 | 72.5 | 206.5 | 10.53 | 120 | 130.53 | 21.8 | 58.12 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-25 15:00 | 237 | 8 | Winter | 15 | 7.76 | -20.1 | 7.12 | 75 | 100.3 | 5.12 | 6.64 | 11.76 | 20.1 | 64.8 | 73.78 | -53.04 | 0 | 0 | 0 | Battery-supported
2025-08-25 16:00 | 237 | 8 | Winter | 16 | 7.76 | -22.8 | 3.4 | 72.5 | 0 | 0 | 0 | 0 | 22.8 | 65.54 | 47.57 | -65.54 | 0 | 0 | 0 | Battery-supported
2025-08-25 17:00 | 237 | 8 | Winter | 17 | 7.76 | -17.1 | 11.24 | 57.2 | 0 | 0 | 64.9 | 64.9 | 17.1 | 53.65 | 51.71 | 11.25 | 0 | 0 | 0 | Normal
2025-08-25 18:00 | 237 | 8 | Winter | 18 | 7.76 | -21.9 | 3.73 | 83.7 | 0 | 0 | 0 | 0 | 21.9 | 65.07 | 25.68 | -65.07 | 0 | 0 | 0 | Battery-supported
2025-08-25 19:00 | 237 | 8 | Winter | 19 | 7.76 | -22.8 | 26.62 | 58.5 | 0 | 0 | 120 | 120 | 22.8 | 64.1 | 46.25 | 55.9 | 0 | 0 | 0 | Normal
2025-08-25 20:00 | 237 | 8 | Winter | 20 | 7.76 | -23 | 9.95 | 24.5 | 0 | 0 | 37.56 | 37.56 | 23 | 67.06 | 34.45 | -29.5 | 0 | 0 | 0 | Battery-supported
2025-08-25 21:00 | 237 | 8 | Winter | 21 | 7.76 | -24.7 | 17.35 | 15.3 | 0 | 0 | 120 | 120 | 24.7 | 56.28 | 57.9 | 63.72 | 0 | 0 | 0 | Normal
2025-08-25 22:00 | 237 | 8 | Winter | 22 | 7.76 | -17.7 | 4.3 | 34.7 | 0 | 0 | 0.07 | 0.07 | 17.7 | 48.64 | 38.47 | -48.57 | 0 | 0 | 0 | Battery-supported
2025-08-25 23:00 | 237 | 8 | Winter | 23 | 7.76 | -18.3 | 14.03 | 78.2 | 0 | 0 | 120 | 120 | 18.3 | 53.68 | 62.88 | 66.32 | 0 | 0 | 0 | Normal
2025-08-26 | 238 | 8 | Winter | 0 | 7.93 | -20.1 | 19.39 | 64.2 | 13.7 | 0.7 | 120 | 120.7 | 20.1 | 53.52 | 87.6 | 67.18 | 0 | 0 | 0 | Normal
2025-08-26 01:00 | 238 | 8 | Winter | 1 | 7.93 | -23.8 | 14.67 | 84.8 | 0 | 0 | 120 | 120 | 23.8 | 57.45 | 95 | 20.11 | 0 | 0 | 0 | Normal
2025-08-26 02:00 | 238 | 8 | Winter | 2 | 7.93 | -18.2 | 16.57 | 63.7 | 0 | 0 | 120 | 120 | 18.2 | 48.32 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-26 03:00 | 238 | 8 | Winter | 3 | 7.93 | -23.4 | 13.26 | 71.6 | 0 | 0 | 120 | 120 | 23.4 | 58.17 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-26 04:00 | 238 | 8 | Winter | 4 | 7.93 | -23.5 | 8.15 | 61 | 0 | 0 | 14.07 | 14.07 | 23.5 | 61.06 | 76.2 | -46.99 | 0 | 0 | 0 | Battery-supported
2025-08-26 05:00 | 238 | 8 | Winter | 5 | 7.93 | -20.1 | 5.92 | 74.1 | 0 | 0 | 1.98 | 1.98 | 20.1 | 56.2 | 54.52 | -54.22 | 0 | 0 | 0 | Battery-supported
2025-08-26 06:00 | 238 | 8 | Winter | 6 | 7.93 | -22 | 6.56 | 15.8 | 0 | 0 | 4.01 | 4.01 | 22 | 55.53 | 33.91 | -51.52 | 0 | 0 | 0 | Battery-supported
2025-08-26 07:00 | 238 | 8 | Winter | 7 | 7.93 | -18.8 | 26.93 | 99.6 | 0 | 0 | 120 | 120 | 18.8 | 47.23 | 60.69 | 72.77 | 0 | 0 | 0 | Normal
2025-08-26 08:00 | 238 | 8 | Winter | 8 | 7.93 | -23.2 | 11.93 | 19.8 | 0 | 0 | 83.85 | 83.85 | 23.2 | 62.79 | 68.44 | 21.06 | 0 | 0 | 0 | Normal
2025-08-26 09:00 | 238 | 8 | Winter | 9 | 7.93 | -24.5 | 20.43 | 66.1 | 123.4 | 6.29 | 120 | 126.29 | 24.5 | 64.52 | 91.17 | 61.77 | 0 | 0 | 0 | Normal
2025-08-26 10:00 | 238 | 8 | Winter | 10 | 7.93 | -24.8 | 7.38 | 53.4 | 276.1 | 14.08 | 8.18 | 22.26 | 24.8 | 71.16 | 71.61 | -48.9 | 0 | 0 | 0 | Battery-supported
2025-08-26 11:00 | 238 | 8 | Winter | 11 | 7.93 | -27.3 | 16.01 | 66.4 | 303.8 | 15.49 | 120 | 135.49 | 27.3 | 73.51 | 94.42 | 61.98 | 0 | 0 | 0 | Normal
2025-08-26 12:00 | 238 | 8 | Winter | 12 | 7.93 | -23.6 | 5.64 | 31.3 | 501.8 | 25.59 | 1.37 | 26.96 | 23.6 | 67.85 | 78.06 | -40.89 | 0 | 0 | 0 | Battery-supported
2025-08-26 13:00 | 238 | 8 | Winter | 13 | 7.93 | -20.1 | 9.04 | 36.8 | 438.3 | 22.35 | 23.8 | 46.15 | 20.1 | 61.71 | 71.84 | -15.56 | 0 | 0 | 0 | Battery-supported
2025-08-26 14:00 | 238 | 8 | Winter | 14 | 7.93 | -20.9 | 7.92 | 46 | 301.7 | 15.39 | 12.09 | 27.48 | 20.9 | 69.11 | 55.19 | -41.63 | 0 | 0 | 0 | Battery-supported
2025-08-26 15:00 | 238 | 8 | Winter | 15 | 7.93 | -21.8 | 25.21 | 36.2 | 178.4 | 9.1 | 120 | 129.1 | 21.8 | 67.32 | 77.92 | 61.78 | 0 | 0 | 0 | Normal
2025-08-26 16:00 | 238 | 8 | Winter | 16 | 7.93 | -23.6 | 6.29 | 79.1 | 0 | 0 | 3.04 | 3.04 | 23.6 | 58.3 | 55.82 | -55.26 | 0 | 0 | 0 | Battery-supported
2025-08-26 17:00 | 238 | 8 | Winter | 17 | 7.93 | -20.6 | 15 | 14.4 | 0 | 0 | 120 | 120 | 20.6 | 69.93 | 74.24 | 50.07 | 0 | 0 | 0 | Normal
2025-08-26 18:00 | 238 | 8 | Winter | 18 | 7.93 | -18.7 | 13.47 | 9.6 | 0 | 0 | 120 | 120 | 18.7 | 61.05 | 95 | 56.41 | 0 | 0 | 0 | Normal
2025-08-26 19:00 | 238 | 8 | Winter | 19 | 7.93 | -19.8 | 4.57 | 47.8 | 0 | 0 | 0.17 | 0.17 | 19.8 | 66.56 | 68.44 | -66.39 | 0 | 0 | 0 | Battery-supported
2025-08-26 20:00 | 238 | 8 | Winter | 20 | 7.93 | -20.3 | 20.55 | 35.8 | 0 | 0 | 120 | 120 | 20.3 | 65.18 | 88.62 | 54.82 | 0 | 0 | 0 | Normal
2025-08-26 21:00 | 238 | 8 | Winter | 21 | 7.93 | -22.5 | 21.91 | 79.5 | 0 | 0 | 120 | 120 | 22.5 | 52.34 | 95 | 17.34 | 0 | 0 | 0 | Normal
2025-08-26 22:00 | 238 | 8 | Winter | 22 | 7.93 | -19 | 11.96 | 29.1 | 0 | 0 | 84.75 | 84.75 | 19 | 52.13 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-26 23:00 | 238 | 8 | Winter | 23 | 7.93 | -28 | 10.8 | 62.2 | 0 | 0 | 54.45 | 54.45 | 28 | 55.29 | 94.66 | -0.84 | 0 | 0 | 0 | Battery-supported
2025-08-27 | 239 | 8 | Winter | 0 | 8.1 | -20.5 | 2.97 | 65.3 | 0 | 0 | 0 | 0 | 20.5 | 52.4 | 73.7 | -52.4 | 0 | 0 | 0 | Battery-supported
2025-08-27 01:00 | 239 | 8 | Winter | 1 | 8.1 | -16 | 4.1 | 59.3 | 0 | 0 | 0.03 | 0.03 | 16 | 51.57 | 53.09 | -51.54 | 0 | 0 | 0 | Battery-supported
2025-08-27 02:00 | 239 | 8 | Winter | 2 | 8.1 | -25.4 | 8.88 | 86.1 | 0 | 0 | 21.8 | 21.8 | 25.4 | 60.67 | 37.54 | -38.87 | 0 | 0 | 0 | Battery-supported
2025-08-27 03:00 | 239 | 8 | Winter | 3 | 8.1 | -23 | 5.75 | 49.1 | 0 | 0 | 1.59 | 1.59 | 23 | 55.32 | 16.05 | -53.73 | 0 | 0 | 0 | Battery-supported
2025-08-27 04:00 | 239 | 8 | Winter | 4 | 8.1 | -22.8 | 17.29 | 86.7 | 0 | 0 | 120 | 120 | 22.8 | 56.79 | 39.31 | 63.21 | 0 | 0 | 0 | Normal
2025-08-27 05:00 | 239 | 8 | Winter | 5 | 8.1 | -24.1 | 3.99 | 65.5 | 0 | 0 | 0.02 | 0.02 | 24.1 | 59.54 | 15.5 | -59.52 | 0 | 0 | 0 | Battery-supported
2025-08-27 06:00 | 239 | 8 | Winter | 6 | 8.1 | -21.1 | 3.73 | 83.1 | 0 | 0 | 0 | 0 | 21.1 | 58.79 | 15 | -1.25 | 57.54 | 18.412 | 0 | Diesel-backup
2025-08-27 07:00 | 239 | 8 | Winter | 7 | 8.1 | -22.5 | 14.2 | 27.5 | 0 | 0 | 120 | 120 | 22.5 | 54.99 | 38.92 | 65.01 | 0 | 0 | 0 | Normal
2025-08-27 08:00 | 239 | 8 | Winter | 8 | 8.1 | -23.2 | 12.9 | 100 | 3.1 | 0.16 | 116.25 | 116.41 | 23.2 | 65.6 | 57.62 | 50.81 | 0 | 0 | 0 | Normal
2025-08-27 09:00 | 239 | 8 | Winter | 9 | 8.1 | -21.8 | 11.43 | 16.7 | 227.1 | 11.58 | 69.8 | 81.38 | 21.8 | 59.78 | 65.57 | 21.6 | 0 | 0 | 0 | Normal
2025-08-27 10:00 | 239 | 8 | Winter | 10 | 8.1 | -23.3 | 16.01 | 81.2 | 183 | 9.33 | 120 | 129.33 | 23.3 | 61.43 | 90.56 | 67.9 | 0 | 0 | 0 | Normal
2025-08-27 11:00 | 239 | 8 | Winter | 11 | 8.1 | -16.1 | 6.97 | 27.8 | 480.4 | 28.82 | 5.85 | 34.67 | 16.1 | 63.62 | 78.98 | -28.95 | 0 | 0 | 0 | Battery-supported
2025-08-27 12:00 | 239 | 8 | Winter | 12 | 8.1 | -22.5 | 8.13 | 54.7 | 386.8 | 19.73 | 13.89 | 33.62 | 22.5 | 71.62 | 63.78 | -38 | 0 | 0 | 0 | Battery-supported
2025-08-27 13:00 | 239 | 8 | Winter | 13 | 8.1 | -22 | 12.67 | 59.7 | 335.4 | 17.11 | 107.92 | 125.03 | 22 | 65.82 | 85.57 | 59.21 | 0 | 0 | 0 | Normal
2025-08-27 14:00 | 239 | 8 | Winter | 14 | 8.1 | -25.8 | 11.89 | 45.5 | 308.6 | 15.74 | 82.66 | 98.4 | 25.8 | 67.5 | 95 | 25.63 | 0 | 0 | 0 | Normal
2025-08-27 15:00 | 239 | 8 | Winter | 15 | 8.1 | -22.9 | 6.08 | 85.5 | 93.1 | 4.75 | 2.4 | 7.15 | 22.9 | 64.02 | 72.25 | -56.87 | 0 | 0 | 0 | Battery-supported
2025-08-27 16:00 | 239 | 8 | Winter | 16 | 8.1 | -18.8 | 18.9 | 82.2 | 4.8 | 0.24 | 120 | 120.24 | 18.8 | 66.68 | 91.96 | 53.56 | 0 | 0 | 0 | Normal
2025-08-27 17:00 | 239 | 8 | Winter | 17 | 8.1 | -23.9 | 4.65 | 19 | 0 | 0 | 0.21 | 0.21 | 23.9 | 51.35 | 71.51 | -51.14 | 0 | 0 | 0 | Battery-supported
2025-08-27 18:00 | 239 | 8 | Winter | 18 | 8.1 | -25.5 | 8.54 | 40 | 0 | 0 | 17.92 | 17.92 | 25.5 | 77.6 | 47.63 | -59.68 | 0 | 0 | 0 | Battery-supported
2025-08-27 19:00 | 239 | 8 | Winter | 19 | 8.1 | -20.5 | 4.89 | 50.8 | 0 | 0 | 0.38 | 0.38 | 20.5 | 63.82 | 22.26 | -63.44 | 0 | 0 | 0 | Battery-supported
2025-08-27 20:00 | 239 | 8 | Winter | 20 | 8.1 | -17.6 | 33.3 | 41.9 | 0 | 0 | 0 | 0 | 17.6 | 50.42 | 15 | -18.15 | 32.27 | 10.854 | 0 | Diesel-backup
2025-08-27 21:00 | 239 | 8 | Winter | 21 | 8.1 | -20.5 | 10.95 | 33.6 | 0 | 0 | 57.87 | 57.87 | 20.5 | 65.34 | 15 | 0 | 7.47 | 2.749 | 0 | Diesel-backup
2025-08-27 22:00 | 239 | 8 | Winter | 22 | 8.1 | -21.5 | 5.51 | 85.7 | 0 | 0 | 1.14 | 1.14 | 21.5 | 46.89 | 15 | 0 | 45.75 | 14.64 | 0 | Diesel-backup
2025-08-27 23:00 | 239 | 8 | Winter | 23 | 8.1 | -25.1 | 7.94 | 50 | 0 | 0 | 12.25 | 12.25 | 25.1 | 51.07 | 15 | 0 | 38.82 | 12.729 | 0 | Diesel-backup
2025-08-28 | 240 | 8 | Winter | 0 | 8.26 | -20.2 | 12.54 | 76.9 | 0 | 0 | 103.4 | 103.4 | 20.2 | 51.61 | 34.06 | 51.79 | 0 | 0 | 0 | Normal
2025-08-28 01:00 | 240 | 8 | Winter | 1 | 8.26 | -20.1 | 17.19 | 32.2 | 0 | 0 | 120 | 120 | 20.1 | 54.47 | 58.17 | 65.53 | 0 | 0 | 0 | Normal
2025-08-28 02:00 | 240 | 8 | Winter | 2 | 8.26 | -25.8 | 5.87 | 12.7 | 0 | 0 | 1.86 | 1.86 | 25.8 | 65.61 | 32.67 | -63.75 | 0 | 0 | 0 | Battery-supported
2025-08-28 03:00 | 240 | 8 | Winter | 3 | 8.26 | -19.8 | 22.46 | 85.6 | 0 | 0 | 120 | 120 | 19.8 | 53.42 | 57.18 | 66.58 | 0 | 0 | 0 | Normal
2025-08-28 04:00 | 240 | 8 | Winter | 4 | 8.26 | -21 | 10.68 | 72.2 | 0 | 0 | 51.81 | 51.81 | 21 | 52.78 | 56.79 | -0.97 | 0 | 0 | 0 | Battery-supported
2025-08-28 05:00 | 240 | 8 | Winter | 5 | 8.26 | -20.5 | 14.25 | 68.3 | 0 | 0 | 120 | 120 | 20.5 | 54.27 | 80.98 | 65.73 | 0 | 0 | 0 | Normal
2025-08-28 06:00 | 240 | 8 | Winter | 6 | 8.26 | -21.9 | 7.54 | 50.8 | 0 | 0 | 9.23 | 9.23 | 21.9 | 55.65 | 62.41 | -46.42 | 0 | 0 | 0 | Battery-supported
2025-08-28 07:00 | 240 | 8 | Winter | 7 | 8.26 | -21.9 | 20.08 | 79.3 | 0 | 0 | 120 | 120 | 21.9 | 62.66 | 83.51 | 57.34 | 0 | 0 | 0 | Normal
2025-08-28 08:00 | 240 | 8 | Winter | 8 | 8.26 | -22.3 | 13.09 | 73.4 | 14.7 | 0.75 | 120 | 120.75 | 22.3 | 69.52 | 95 | 31.23 | 0 | 0 | 0 | Normal
2025-08-28 09:00 | 240 | 8 | Winter | 9 | 8.26 | -21.5 | 7.19 | 58.7 | 153.1 | 7.81 | 7.03 | 14.84 | 21.5 | 62.08 | 76.1 | -47.24 | 0 | 0 | 0 | Battery-supported
2025-08-28 10:00 | 240 | 8 | Winter | 10 | 8.26 | -27.2 | 8.2 | 43 | 321.8 | 16.41 | 14.53 | 30.94 | 27.2 | 68.82 | 60.95 | -37.88 | 0 | 0 | 0 | Battery-supported
2025-08-28 11:00 | 240 | 8 | Winter | 11 | 8.26 | -26.3 | 17.56 | 31.1 | 466.9 | 23.81 | 120 | 143.81 | 26.3 | 61.86 | 91.11 | 81.95 | 0 | 0 | 0 | Normal
2025-08-28 12:00 | 240 | 8 | Winter | 12 | 8.26 | -24.3 | 13.8 | 28 | 518.3 | 26.43 | 120 | 146.43 | 24.3 | 69.83 | 95 | 10.57 | 0 | 0 | 0 | Normal
2025-08-28 13:00 | 240 | 8 | Winter | 13 | 8.26 | -22.6 | 8.72 | 20.6 | 515.1 | 26.27 | 19.91 | 46.18 | 22.6 | 65.39 | 87.32 | -19.21 | 0 | 0 | 0 | Battery-supported
2025-08-28 14:00 | 240 | 8 | Winter | 14 | 8.26 | -21.1 | 17.01 | 28.3 | 374.2 | 19.08 | 120 | 139.08 | 21.1 | 65.65 | 95 | 20.88 | 0 | 0 | 0 | Normal
2025-08-28 15:00 | 240 | 8 | Winter | 15 | 8.26 | -20.8 | 12.3 | 35.1 | 201.6 | 10.28 | 95.38 | 105.66 | 20.8 | 66.33 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-28 16:00 | 240 | 8 | Winter | 16 | 8.26 | -18.7 | 2.58 | 49.1 | 20.7 | 1.06 | 0 | 1.06 | 18.7 | 67.92 | 68.26 | -66.86 | 0 | 0 | 0 | Battery-supported
2025-08-28 17:00 | 240 | 8 | Winter | 17 | 8.26 | -18.3 | 9.75 | 49.6 | 0 | 0 | 34.17 | 34.17 | 18.3 | 59.74 | 58.03 | -25.57 | 0 | 0 | 0 | Battery-supported
2025-08-28 18:00 | 240 | 8 | Winter | 18 | 8.26 | -22.5 | 17.34 | 77.9 | 0 | 0 | 120 | 120 | 22.5 | 65.72 | 78 | 54.28 | 0 | 0 | 0 | Normal
2025-08-28 19:00 | 240 | 8 | Winter | 19 | 8.26 | -20 | 26.36 | 96.2 | 0 | 0 | 120 | 120 | 20 | 69.27 | 95 | 46.19 | 0 | 0 | 0 | Normal
2025-08-28 20:00 | 240 | 8 | Winter | 20 | 8.26 | -22.3 | 5.15 | 17.3 | 0 | 0 | 0.63 | 0.63 | 22.3 | 64.61 | 69.41 | -63.98 | 0 | 0 | 0 | Battery-supported
2025-08-28 21:00 | 240 | 8 | Winter | 21 | 8.26 | -20.9 | 16.7 | 31.8 | 0 | 0 | 120 | 120 | 20.9 | 55.54 | 93.13 | 64.46 | 0 | 0 | 0 | Normal
2025-08-28 22:00 | 240 | 8 | Winter | 22 | 8.26 | -19.9 | 10.63 | 46 | 0 | 0 | 50.73 | 50.73 | 19.9 | 65.46 | 87.24 | -14.73 | 0 | 0 | 0 | Battery-supported
2025-08-28 23:00 | 240 | 8 | Winter | 23 | 8.26 | -28.4 | 4.55 | 37.8 | 0 | 0 | 0.16 | 0.16 | 28.4 | 63.22 | 62.01 | -63.06 | 0 | 0 | 0 | Battery-supported
2025-08-29 | 241 | 8 | Winter | 0 | 8.43 | -15.7 | 4.82 | 56.3 | 0 | 0 | 0.32 | 0.32 | 15.7 | 57.64 | 39.09 | -57.32 | 0 | 0 | 0 | Battery-supported
2025-08-29 01:00 | 241 | 8 | Winter | 1 | 8.43 | -20.2 | 5.27 | 47.2 | 0 | 0 | 0.78 | 0.78 | 20.2 | 52.97 | 18.21 | -52.19 | 0 | 0 | 0 | Battery-supported
2025-08-29 02:00 | 241 | 8 | Winter | 2 | 8.43 | -23.1 | 3.58 | 46.8 | 0 | 0 | 0 | 0 | 23.1 | 56.28 | 15 | -8.02 | 48.26 | 15.442 | 0 | Diesel-backup
2025-08-29 03:00 | 241 | 8 | Winter | 3 | 8.43 | -17.9 | 4.26 | 78.8 | 0 | 0 | 0.06 | 0.06 | 17.9 | 45 | 15 | 0 | 44.94 | 14.384 | 0 | Diesel-backup
2025-08-29 04:00 | 241 | 8 | Winter | 4 | 8.43 | -23.3 | 10.86 | 62.2 | 0 | 0 | 55.8 | 55.8 | 23.3 | 60.75 | 15 | 0 | 4.95 | 1.838 | 0 | Diesel-backup
2025-08-29 05:00 | 241 | 8 | Winter | 5 | 8.43 | -22.6 | 2.53 | 37.2 | 0 | 0 | 0 | 0 | 22.6 | 60.47 | 15 | 0 | 60.47 | 19.35 | 0 | Diesel-backup
2025-08-29 06:00 | 241 | 8 | Winter | 6 | 8.43 | -24.2 | 5.92 | 47.1 | 0 | 0 | 1.98 | 1.98 | 24.2 | 59.56 | 15 | 0 | 57.58 | 18.426 | 0 | Diesel-backup
2025-08-29 07:00 | 241 | 8 | Winter | 7 | 8.43 | -19.6 | 8.23 | 7.2 | 0 | 0 | 14.81 | 14.81 | 19.6 | 56.43 | 15 | 0 | 41.62 | 13.498 | 0 | Diesel-backup
2025-08-29 08:00 | 241 | 8 | Winter | 8 | 8.43 | -23.5 | 5.94 | 31.6 | 39.8 | 2.03 | 2.03 | 4.06 | 23.5 | 70 | 15 | 0 | 65.94 | 21.101 | 0 | Diesel-backup
2025-08-29 09:00 | 241 | 8 | Winter | 9 | 8.43 | -22.9 | 3.92 | 69.4 | 137.6 | 7.02 | 0.01 | 7.03 | 22.9 | 59.97 | 15 | 0 | 52.94 | 16.941 | 0 | Diesel-backup
2025-08-29 10:00 | 241 | 8 | Winter | 10 | 8.43 | -20.4 | 10.4 | 23.2 | 398.1 | 20.3 | 45.98 | 66.28 | 20.4 | 63.68 | 15.96 | 2.6 | 0 | 0 | 0 | Normal
2025-08-29 11:00 | 241 | 8 | Winter | 11 | 8.43 | -21.6 | 5.86 | 4.2 | 591.8 | 30.18 | 1.84 | 32.02 | 21.6 | 71.24 | 15 | -2.39 | 36.83 | 12.17 | 0 | Diesel-backup
2025-08-29 12:00 | 241 | 8 | Winter | 12 | 8.43 | -22.7 | 6.17 | 30.1 | 508 | 25.91 | 2.66 | 28.57 | 22.7 | 64.57 | 15 | 0 | 36 | 11.935 | 0 | Diesel-backup
2025-08-29 13:00 | 241 | 8 | Winter | 13 | 8.43 | -19.7 | 9.45 | 45.3 | 403.3 | 20.57 | 29.48 | 50.05 | 19.7 | 57.2 | 15 | 0 | 7.15 | 2.634 | 0 | Diesel-backup
2025-08-29 14:00 | 241 | 8 | Winter | 14 | 8.43 | -16.2 | 14.85 | 16 | 424.1 | 25.45 | 120 | 145.45 | 16.2 | 63.53 | 45.15 | 81.92 | 0 | 0 | 0 | Normal
2025-08-29 15:00 | 241 | 8 | Winter | 15 | 8.43 | -20.7 | 6.82 | 76.7 | 121.8 | 6.21 | 5.12 | 11.33 | 20.7 | 64.29 | 23.96 | -52.96 | 0 | 0 | 0 | Battery-supported
2025-08-29 16:00 | 241 | 8 | Winter | 16 | 8.43 | -20.8 | 7.05 | 73.3 | 23.5 | 1.2 | 6.26 | 7.46 | 20.8 | 63.69 | 15 | -22.41 | 33.82 | 11.307 | 0 | Diesel-backup
2025-08-29 17:00 | 241 | 8 | Winter | 17 | 8.43 | -20.4 | 4.42 | 45.5 | 0 | 0 | 0.11 | 0.11 | 20.4 | 61.77 | 15 | 0 | 61.66 | 19.731 | 0 | Diesel-backup
2025-08-29 18:00 | 241 | 8 | Winter | 18 | 8.43 | -17.6 | 17.19 | 78.2 | 0 | 0 | 120 | 120 | 17.6 | 64.28 | 35.5 | 55.72 | 0 | 0 | 0 | Normal
2025-08-29 19:00 | 241 | 8 | Winter | 19 | 8.43 | -21.7 | 10.51 | 56.5 | 0 | 0 | 48.21 | 48.21 | 21.7 | 62.5 | 29.79 | -14.29 | 0 | 0 | 0 | Battery-supported
2025-08-29 20:00 | 241 | 8 | Winter | 20 | 8.43 | -20.9 | 16.57 | 61.4 | 0 | 0 | 120 | 120 | 20.9 | 69.68 | 48.31 | 50.32 | 0 | 0 | 0 | Normal
2025-08-29 21:00 | 241 | 8 | Winter | 21 | 8.43 | -23.7 | 18.11 | 45.2 | 0 | 0 | 120 | 120 | 23.7 | 59.04 | 70.74 | 60.96 | 0 | 0 | 0 | Normal
2025-08-29 22:00 | 241 | 8 | Winter | 22 | 8.43 | -23.1 | 6.76 | 63.9 | 0 | 0 | 4.85 | 4.85 | 23.1 | 62.15 | 47.82 | -57.3 | 0 | 0 | 0 | Battery-supported
2025-08-29 23:00 | 241 | 8 | Winter | 23 | 8.43 | -21.9 | 29.34 | 78.7 | 0 | 0 | 0 | 0 | 21.9 | 60.48 | 23.63 | -60.48 | 0 | 0 | 0 | Battery-supported
2025-08-30 | 242 | 8 | Winter | 0 | 8.59 | -21 | 15.82 | 36.7 | 0 | 0 | 120 | 120 | 21 | 51.28 | 48.92 | 68.72 | 0 | 0 | 0 | Normal
2025-08-30 01:00 | 242 | 8 | Winter | 1 | 8.59 | -17.4 | 11.12 | 66.8 | 0 | 0 | 61.93 | 61.93 | 17.4 | 54.31 | 51.72 | 7.62 | 0 | 0 | 0 | Normal
2025-08-30 02:00 | 242 | 8 | Winter | 2 | 8.59 | -20.5 | 7.14 | 26.2 | 0 | 0 | 6.75 | 6.75 | 20.5 | 54.43 | 32.65 | -47.68 | 0 | 0 | 0 | Battery-supported
2025-08-30 03:00 | 242 | 8 | Winter | 3 | 8.59 | -24 | 6.43 | 64.2 | 0 | 0 | 3.52 | 3.52 | 24 | 61.63 | 15 | -44.12 | 13.99 | 5.031 | 0 | Diesel-backup
2025-08-30 04:00 | 242 | 8 | Winter | 4 | 8.59 | -24 | 10.31 | 49.4 | 0 | 0 | 44.2 | 44.2 | 24 | 58.76 | 15 | 0 | 14.56 | 5.227 | 0 | Diesel-backup
2025-08-30 05:00 | 242 | 8 | Winter | 5 | 8.59 | -19.7 | 11.82 | 76.8 | 0 | 0 | 80.61 | 80.61 | 19.7 | 47.17 | 27.31 | 33.44 | 0 | 0 | 0 | Normal
2025-08-30 06:00 | 242 | 8 | Winter | 6 | 8.59 | -20.5 | 2.04 | 54.1 | 0 | 0 | 0 | 0 | 20.5 | 58.66 | 15 | -30.76 | 27.9 | 9.537 | 0 | Diesel-backup
2025-08-30 07:00 | 242 | 8 | Winter | 7 | 8.59 | -23 | 7.81 | 28.6 | 0 | 0 | 11.21 | 11.21 | 23 | 49.07 | 15 | 0 | 37.86 | 12.461 | 0 | Diesel-backup
2025-08-30 08:00 | 242 | 8 | Winter | 8 | 8.59 | -24.1 | 11.52 | 24.5 | 57.7 | 2.94 | 72.2 | 75.14 | 24.1 | 67.67 | 17.75 | 7.47 | 0 | 0 | 0 | Normal
2025-08-30 09:00 | 242 | 8 | Winter | 9 | 8.59 | -20.6 | 13.16 | 47.3 | 193.1 | 9.85 | 120 | 129.85 | 20.6 | 71.18 | 39.34 | 58.67 | 0 | 0 | 0 | Normal
2025-08-30 10:00 | 242 | 8 | Winter | 10 | 8.59 | -25.1 | 9.38 | 82.3 | 187 | 9.54 | 28.45 | 37.99 | 25.1 | 73.7 | 25.06 | -35.71 | 0 | 0 | 0 | Battery-supported
2025-08-30 11:00 | 242 | 8 | Winter | 11 | 8.59 | -21.8 | 12.93 | 85.4 | 220.1 | 11.23 | 117.37 | 128.6 | 21.8 | 66.41 | 47.94 | 62.19 | 0 | 0 | 0 | Normal
2025-08-30 12:00 | 242 | 8 | Winter | 12 | 8.59 | -17.4 | 6.44 | 11.5 | 599.4 | 35.96 | 3.56 | 39.52 | 17.4 | 58.35 | 40.41 | -18.83 | 0 | 0 | 0 | Battery-supported
2025-08-30 13:00 | 242 | 8 | Winter | 13 | 8.59 | -21.6 | 12.74 | 63.2 | 322.1 | 16.43 | 110.41 | 126.84 | 21.6 | 64.35 | 63.41 | 62.49 | 0 | 0 | 0 | Normal
2025-08-30 14:00 | 242 | 8 | Winter | 14 | 8.59 | -23.4 | 11.74 | 85.4 | 175.4 | 8.95 | 78.31 | 87.26 | 23.4 | 70.61 | 69.53 | 16.65 | 0 | 0 | 0 | Normal
2025-08-30 15:00 | 242 | 8 | Winter | 15 | 8.59 | -20.4 | 17.91 | 63.5 | 156.8 | 8 | 120 | 128 | 20.4 | 60.24 | 94.47 | 67.76 | 0 | 0 | 0 | Normal
2025-08-30 16:00 | 242 | 8 | Winter | 16 | 8.59 | -21.9 | 23.01 | 55.2 | 41.4 | 2.11 | 120 | 122.11 | 21.9 | 66.57 | 95 | 1.44 | 0 | 0 | 0 | Normal
2025-08-30 17:00 | 242 | 8 | Winter | 17 | 8.59 | -23.7 | 18.16 | 65.1 | 0 | 0 | 120 | 120 | 23.7 | 63.3 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-30 18:00 | 242 | 8 | Winter | 18 | 8.59 | -18.8 | 8.68 | 49.5 | 0 | 0 | 19.45 | 19.45 | 18.8 | 60.67 | 78.51 | -41.22 | 0 | 0 | 0 | Battery-supported
2025-08-30 19:00 | 242 | 8 | Winter | 19 | 8.59 | -17.7 | 4.59 | 9.8 | 0 | 0 | 0.18 | 0.18 | 17.7 | 58.81 | 55.06 | -58.63 | 0 | 0 | 0 | Battery-supported
2025-08-30 20:00 | 242 | 8 | Winter | 20 | 8.59 | -20.8 | 5.9 | 78 | 0 | 0 | 1.93 | 1.93 | 20.8 | 65.46 | 29.65 | -63.53 | 0 | 0 | 0 | Battery-supported
2025-08-30 21:00 | 242 | 8 | Winter | 21 | 8.59 | -21 | 22.66 | 42.4 | 0 | 0 | 120 | 120 | 21 | 58.19 | 52.39 | 61.81 | 0 | 0 | 0 | Normal
2025-08-30 22:00 | 242 | 8 | Winter | 22 | 8.59 | -22.5 | 10.64 | 29.3 | 0 | 0 | 50.95 | 50.95 | 22.5 | 66.11 | 46.33 | -15.16 | 0 | 0 | 0 | Battery-supported
2025-08-30 23:00 | 242 | 8 | Winter | 23 | 8.59 | -20.9 | 12.01 | 56.3 | 0 | 0 | 86.26 | 86.26 | 20.9 | 55.29 | 57.73 | 30.97 | 0 | 0 | 0 | Normal
2025-08-31 | 243 | 8 | Winter | 0 | 8.75 | -22 | 16.48 | 56.4 | 0 | 0 | 120 | 120 | 22 | 58.29 | 80.44 | 61.71 | 0 | 0 | 0 | Normal
2025-08-31 01:00 | 243 | 8 | Winter | 1 | 8.75 | -23.3 | 10.23 | 48.6 | 0 | 0 | 42.66 | 42.66 | 23.3 | 63 | 72.3 | -20.34 | 0 | 0 | 0 | Battery-supported
2025-08-31 02:00 | 243 | 8 | Winter | 2 | 8.75 | -17.3 | 19.68 | 58 | 0 | 0 | 120 | 120 | 17.3 | 52.2 | 95 | 61.68 | 0 | 0 | 0 | Normal
2025-08-31 03:00 | 243 | 8 | Winter | 3 | 8.75 | -20.9 | 4.2 | 73.5 | 0 | 0 | 0.05 | 0.05 | 20.9 | 56.29 | 72.5 | -56.24 | 0 | 0 | 0 | Battery-supported
2025-08-31 04:00 | 243 | 8 | Winter | 4 | 8.75 | -21 | 13.49 | 79.1 | 0 | 0 | 120 | 120 | 21 | 58.44 | 95 | 61.13 | 0 | 0 | 0 | Normal
2025-08-31 05:00 | 243 | 8 | Winter | 5 | 8.75 | -20.6 | 26.6 | 65.8 | 0 | 0 | 120 | 120 | 20.6 | 52.89 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-31 06:00 | 243 | 8 | Winter | 6 | 8.75 | -21.1 | 20.59 | 44.9 | 0 | 0 | 120 | 120 | 21.1 | 56.9 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-31 07:00 | 243 | 8 | Winter | 7 | 8.75 | -23.9 | 21.27 | 47.3 | 0 | 0 | 120 | 120 | 23.9 | 55.66 | 95 | 0 | 0 | 0 | 0 | Normal
2025-08-31 08:00 | 243 | 8 | Winter | 8 | 8.75 | -22.4 | 3.9 | 43.8 | 59.3 | 3.02 | 0.01 | 3.03 | 22.4 | 64.13 | 70.56 | -61.1 | 0 | 0 | 0 | Battery-supported
2025-08-31 09:00 | 243 | 8 | Winter | 9 | 8.75 | -23.5 | 11.6 | 7.7 | 293.1 | 14.95 | 74.38 | 89.33 | 23.5 | 75.09 | 75.8 | 14.24 | 0 | 0 | 0 | Normal
2025-08-31 10:00 | 243 | 8 | Winter | 10 | 8.75 | -21.8 | 9.48 | 14.1 | 441.8 | 22.53 | 29.93 | 52.46 | 21.8 | 64.22 | 71.1 | -11.76 | 0 | 0 | 0 | Battery-supported
2025-08-31 11:00 | 243 | 8 | Winter | 11 | 8.75 | -21.8 | 5.87 | 43.8 | 412.5 | 21.04 | 1.86 | 22.9 | 21.8 | 65.69 | 53.98 | -42.79 | 0 | 0 | 0 | Battery-supported
2025-08-31 12:00 | 243 | 8 | Winter | 12 | 8.75 | -23.1 | 11.71 | 22 | 547.7 | 27.93 | 77.45 | 105.38 | 23.1 | 55.51 | 72.33 | 49.87 | 0 | 0 | 0 | Normal
2025-08-31 13:00 | 243 | 8 | Winter | 13 | 8.75 | -24.8 | 4.61 | 30.4 | 474 | 24.17 | 0.19 | 24.36 | 24.8 | 69.56 | 54.25 | -45.2 | 0 | 0 | 0 | Battery-supported
2025-08-31 14:00 | 243 | 8 | Winter | 14 | 8.75 | -21.2 | 12.89 | 84 | 182.7 | 9.32 | 115.88 | 125.2 | 21.2 | 72.1 | 73.79 | 53.1 | 0 | 0 | 0 | Normal
2025-08-31 15:00 | 243 | 8 | Winter | 15 | 8.75 | -21.6 | 5.58 | 23.7 | 255.7 | 13.04 | 1.26 | 14.3 | 21.6 | 61.21 | 55.03 | -46.91 | 0 | 0 | 0 | Battery-supported
2025-08-31 16:00 | 243 | 8 | Winter | 16 | 8.75 | -24.9 | 12.51 | 57.6 | 50.2 | 2.56 | 102.37 | 104.93 | 24.9 | 72.24 | 67.06 | 32.69 | 0 | 0 | 0 | Normal
2025-08-31 17:00 | 243 | 8 | Winter | 17 | 8.75 | -19.3 | 6.05 | 15.7 | 0 | 0 | 2.32 | 2.32 | 19.3 | 59.82 | 44.06 | -57.5 | 0 | 0 | 0 | Battery-supported
2025-08-31 18:00 | 243 | 8 | Winter | 18 | 8.75 | -18.1 | 8.35 | 79.6 | 0 | 0 | 15.97 | 15.97 | 18.1 | 54.48 | 28.66 | -38.51 | 0 | 0 | 0 | Battery-supported
2025-08-31 19:00 | 243 | 8 | Winter | 19 | 8.75 | -14.5 | 7.87 | 67 | 0 | 0 | 11.68 | 11.68 | 14.5 | 55.75 | 15 | -34.14 | 9.93 | 3.624 | 0 | Diesel-backup
2025-08-31 20:00 | 243 | 8 | Winter | 20 | 8.75 | -20.9 | 9.36 | 45.5 | 0 | 0 | 28.16 | 28.16 | 20.9 | 61.17 | 15 | 0 | 33.01 | 11.07 | 0 | Diesel-backup
2025-08-31 21:00 | 243 | 8 | Winter | 21 | 8.75 | -21.2 | 9.95 | 66.5 | 0 | 0 | 37.56 | 37.56 | 21.2 | 56.66 | 15 | 0 | 19.1 | 6.745 | 0 | Diesel-backup
2025-08-31 22:00 | 243 | 8 | Winter | 22 | 8.75 | -22.6 | 7.89 | 13.5 | 0 | 0 | 11.84 | 11.84 | 22.6 | 56.39 | 15 | 0 | 44.55 | 14.282 | 0 | Diesel-backup
2025-08-31 23:00 | 243 | 8 | Winter | 23 | 8.75 | -20 | 5.19 | 27.2 | 0 | 0 | 0.68 | 0.68 | 20 | 51.01 | 15 | 0 | 50.33 | 16.106 | 0 | Diesel-backup
2025-09-01 | 244 | 9 | Spring | 0 | 8.91 | -20.2 | 18.51 | 91.4 | 0 | 0 | 120 | 120 | 20.2 | 57.33 | 38.06 | 62.67 | 0 | 0 | 0 | Normal
2025-09-01 01:00 | 244 | 9 | Spring | 1 | 8.91 | -22.8 | 10.18 | 42 | 0 | 0 | 41.72 | 41.72 | 22.8 | 62.49 | 29.75 | -20.77 | 0 | 0 | 0 | Battery-supported
2025-09-01 02:00 | 244 | 9 | Spring | 2 | 8.91 | -21.7 | 11.84 | 0.3 | 0 | 0 | 81.19 | 81.19 | 21.7 | 59.3 | 37.81 | 21.89 | 0 | 0 | 0 | Normal
2025-09-01 03:00 | 244 | 9 | Spring | 3 | 8.91 | -26.1 | 7.88 | 20.6 | 0 | 0 | 11.76 | 11.76 | 26.1 | 61.81 | 17.79 | -50.05 | 0 | 0 | 0 | Battery-supported
2025-09-01 04:00 | 244 | 9 | Spring | 4 | 8.91 | -20.1 | 33.51 | 30.5 | 0 | 0 | 0 | 0 | 20.1 | 54.79 | 15 | -6.98 | 47.81 | 15.301 | 0 | Diesel-backup
2025-09-01 05:00 | 244 | 9 | Spring | 5 | 8.91 | -24.1 | 10.71 | 79.1 | 0 | 0 | 52.46 | 52.46 | 24.1 | 61.44 | 15 | 0 | 8.98 | 3.288 | 0 | Diesel-backup
2025-09-01 06:00 | 244 | 9 | Spring | 6 | 8.91 | -22.7 | 19.05 | 37.7 | 0 | 0 | 120 | 120 | 22.7 | 55.5 | 38.74 | 64.5 | 0 | 0 | 0 | Normal
2025-09-01 07:00 | 244 | 9 | Spring | 7 | 8.91 | -25.9 | 8.42 | 43.9 | 0 | 0 | 16.67 | 16.67 | 25.9 | 64.27 | 19.7 | -47.6 | 0 | 0 | 0 | Battery-supported
2025-09-01 08:00 | 244 | 9 | Spring | 8 | 8.91 | -24.1 | 13.78 | 14.6 | 93.6 | 4.77 | 120 | 124.77 | 24.1 | 61.97 | 42.81 | 62.8 | 0 | 0 | 0 | Normal
2025-09-01 09:00 | 244 | 9 | Spring | 9 | 8.91 | -23.4 | 9.11 | 39.9 | 225.7 | 11.51 | 24.71 | 36.22 | 23.4 | 59.42 | 33.53 | -23.2 | 0 | 0 | 0 | Battery-supported
2025-09-01 10:00 | 244 | 9 | Spring | 10 | 8.91 | -22.7 | 17.33 | 54.9 | 293.8 | 14.98 | 120 | 134.98 | 22.7 | 68.15 | 58.12 | 66.83 | 0 | 0 | 0 | Normal
2025-09-01 11:00 | 244 | 9 | Spring | 11 | 8.91 | -21.4 | 7.36 | 22.8 | 510.5 | 26.04 | 8.05 | 34.09 | 21.4 | 60.11 | 47.71 | -26.02 | 0 | 0 | 0 | Battery-supported
2025-09-01 12:00 | 244 | 9 | Spring | 12 | 8.91 | -18.9 | 4.77 | 97.3 | 177.2 | 9.04 | 0.29 | 9.33 | 18.9 | 58.88 | 27.89 | -49.55 | 0 | 0 | 0 | Battery-supported
2025-09-01 13:00 | 244 | 9 | Spring | 13 | 8.91 | -20.1 | 11.82 | 45.7 | 404.7 | 20.64 | 80.61 | 101.25 | 20.1 | 58.95 | 43.46 | 42.3 | 0 | 0 | 0 | Normal
2025-09-01 14:00 | 244 | 9 | Spring | 14 | 8.91 | -19.2 | 17.99 | 35.2 | 367.8 | 18.76 | 120 | 138.76 | 19.2 | 64.59 | 70.75 | 74.17 | 0 | 0 | 0 | Normal
2025-09-01 15:00 | 244 | 9 | Spring | 15 | 8.91 | -17.8 | 9.28 | 56 | 186.9 | 11.21 | 27.03 | 38.24 | 17.8 | 57.61 | 63 | -19.37 | 0 | 0 | 0 | Battery-supported
2025-09-01 16:00 | 244 | 9 | Spring | 16 | 8.91 | -19.4 | 7.24 | 21.2 | 88.4 | 4.51 | 7.32 | 11.83 | 19.4 | 67.96 | 40.55 | -56.13 | 0 | 0 | 0 | Battery-supported
2025-09-01 17:00 | 244 | 9 | Spring | 17 | 8.91 | -20.4 | 4.19 | 69.2 | 0 | 0 | 0.05 | 0.05 | 20.4 | 66.47 | 15 | -63.88 | 2.54 | 0.95 | 0 | Diesel-backup
2025-09-01 18:00 | 244 | 9 | Spring | 18 | 8.91 | -17.8 | 18.14 | 75.8 | 0 | 0 | 120 | 120 | 17.8 | 61.86 | 36.4 | 58.14 | 0 | 0 | 0 | Normal
2025-09-01 19:00 | 244 | 9 | Spring | 19 | 8.91 | -17.5 | 5.72 | 31.7 | 0 | 0 | 1.53 | 1.53 | 17.5 | 66.9 | 15 | -53.49 | 11.88 | 4.306 | 0 | Diesel-backup
2025-09-01 20:00 | 244 | 9 | Spring | 20 | 8.91 | -18.4 | 7.81 | 59.6 | 0 | 0 | 11.21 | 11.21 | 18.4 | 57.66 | 15 | 0 | 46.45 | 14.864 | 0 | Diesel-backup
2025-09-01 21:00 | 244 | 9 | Spring | 21 | 8.91 | -23.1 | 7.7 | 17.5 | 0 | 0 | 10.37 | 10.37 | 23.1 | 58.62 | 15 | 0 | 48.25 | 15.44 | 0 | Diesel-backup
2025-09-01 22:00 | 244 | 9 | Spring | 22 | 8.91 | -21.9 | 9.73 | 72.7 | 0 | 0 | 33.84 | 33.84 | 21.9 | 47.74 | 15 | 0 | 13.9 | 5.001 | 0 | Diesel-backup
2025-09-01 23:00 | 244 | 9 | Spring | 23 | 8.91 | -20.9 | 13.71 | 86.2 | 0 | 0 | 120 | 120 | 20.9 | 53.79 | 39.37 | 66.21 | 0 | 0 | 0 | Normal
2025-09-02 | 245 | 9 | Spring | 0 | 9.07 | -18.7 | 28.01 | 63.4 | 0 | 0 | 0 | 0 | 18.7 | 48.43 | 19.99 | -48.43 | 0 | 0 | 0 | Battery-supported
2025-09-02 01:00 | 245 | 9 | Spring | 1 | 9.07 | -20.9 | 12.09 | 37 | 0 | 0 | 88.71 | 88.71 | 20.9 | 59.54 | 30.73 | 29.17 | 0 | 0 | 0 | Normal
2025-09-02 02:00 | 245 | 9 | Spring | 2 | 9.07 | -18.7 | 4.2 | 51.8 | 0 | 0 | 0.05 | 0.05 | 18.7 | 58.74 | 15 | -39.32 | 19.37 | 6.834 | 0 | Diesel-backup
2025-09-02 03:00 | 245 | 9 | Spring | 3 | 9.07 | -18.7 | 9.42 | 53.7 | 0 | 0 | 29.04 | 29.04 | 18.7 | 52.61 | 15 | 0 | 23.57 | 8.189 | 0 | Diesel-backup
2025-09-02 04:00 | 245 | 9 | Spring | 4 | 9.07 | -19.3 | 12.2 | 17.8 | 0 | 0 | 92.17 | 92.17 | 19.3 | 63.44 | 25.57 | 28.73 | 0 | 0 | 0 | Normal
2025-09-02 05:00 | 245 | 9 | Spring | 5 | 9.07 | -19.6 | 19.77 | 83.5 | 0 | 0 | 120 | 120 | 19.6 | 51.22 | 50.88 | 68.78 | 0 | 0 | 0 | Normal
2025-09-02 06:00 | 245 | 9 | Spring | 6 | 9.07 | -24.8 | 18.49 | 82.2 | 0 | 0 | 120 | 120 | 24.8 | 55.05 | 74.79 | 64.95 | 0 | 0 | 0 | Normal
2025-09-02 07:00 | 245 | 9 | Spring | 7 | 9.07 | -21.6 | 9.19 | 80.7 | 0 | 0 | 25.78 | 25.78 | 21.6 | 54.44 | 63.32 | -28.66 | 0 | 0 | 0 | Battery-supported
2025-09-02 08:00 | 245 | 9 | Spring | 8 | 9.07 | -24 | 10.52 | 54 | 72.2 | 3.68 | 48.42 | 52.1 | 24 | 68.53 | 56.75 | -16.43 | 0 | 0 | 0 | Battery-supported
2025-09-02 09:00 | 245 | 9 | Spring | 9 | 9.07 | -26.3 | 11.42 | 67.7 | 163.8 | 8.35 | 69.53 | 77.88 | 26.3 | 73.09 | 58.51 | 4.79 | 0 | 0 | 0 | Normal
2025-09-02 10:00 | 245 | 9 | Spring | 10 | 9.07 | -23.1 | 10.54 | 23.9 | 414.4 | 21.13 | 48.83 | 69.96 | 23.1 | 69.27 | 58.77 | 0.69 | 0 | 0 | 0 | Normal
2025-09-02 11:00 | 245 | 9 | Spring | 11 | 9.07 | -19.4 | 9.41 | 42.2 | 421.7 | 21.51 | 28.89 | 50.4 | 19.4 | 61.04 | 54.51 | -10.64 | 0 | 0 | 0 | Battery-supported
2025-09-02 12:00 | 245 | 9 | Spring | 12 | 9.07 | -20.9 | 23.21 | 41.2 | 453.1 | 23.11 | 120 | 143.11 | 20.9 | 68.39 | 82.01 | 74.72 | 0 | 0 | 0 | Normal
2025-09-02 13:00 | 245 | 9 | Spring | 13 | 9.07 | -17.2 | 6.45 | 76.4 | 263.5 | 15.81 | 3.59 | 19.4 | 17.2 | 58.12 | 66.52 | -38.72 | 0 | 0 | 0 | Battery-supported
2025-09-02 14:00 | 245 | 9 | Spring | 14 | 9.07 | -20.8 | 16.68 | 49.2 | 318.4 | 16.24 | 120 | 136.24 | 20.8 | 75.44 | 88.89 | 60.8 | 0 | 0 | 0 | Normal
2025-09-02 15:00 | 245 | 9 | Spring | 15 | 9.07 | -15.4 | 14.96 | 19 | 285.5 | 17.13 | 120 | 137.13 | 15.4 | 62.7 | 95 | 16.59 | 0 | 0 | 0 | Normal
2025-09-02 16:00 | 245 | 9 | Spring | 16 | 9.07 | -20.1 | 9.19 | 50.3 | 75.5 | 3.85 | 25.78 | 29.63 | 20.1 | 55.04 | 84.84 | -25.41 | 0 | 0 | 0 | Battery-supported
2025-09-02 17:00 | 245 | 9 | Spring | 17 | 9.07 | -20.1 | 6.18 | 87 | 0 | 0 | 2.69 | 2.69 | 20.1 | 61.15 | 61.45 | -58.46 | 0 | 0 | 0 | Battery-supported
2025-09-02 18:00 | 245 | 9 | Spring | 18 | 9.07 | -22.7 | 10.13 | 23.9 | 0 | 0 | 40.79 | 40.79 | 22.7 | 62.68 | 52.7 | -21.89 | 0 | 0 | 0 | Battery-supported
2025-09-02 19:00 | 245 | 9 | Spring | 19 | 9.07 | -17.3 | 14.02 | 19.7 | 0 | 0 | 120 | 120 | 17.3 | 68.78 | 71.54 | 51.22 | 0 | 0 | 0 | Normal
2025-09-02 20:00 | 245 | 9 | Spring | 20 | 9.07 | -20.8 | 1.07 | 2.3 | 0 | 0 | 0 | 0 | 20.8 | 60.07 | 47.52 | -60.07 | 0 | 0 | 0 | Battery-supported
2025-09-02 21:00 | 245 | 9 | Spring | 21 | 9.07 | -21.2 | 4.57 | 91.4 | 0 | 0 | 0.17 | 0.17 | 21.2 | 47.19 | 28.71 | -47.02 | 0 | 0 | 0 | Battery-supported
2025-09-02 22:00 | 245 | 9 | Spring | 22 | 9.07 | -17.1 | 1.65 | 20.5 | 0 | 0 | 0 | 0 | 17.1 | 56.17 | 15 | -34.27 | 21.9 | 7.655 | 0 | Diesel-backup
2025-09-02 23:00 | 245 | 9 | Spring | 23 | 9.07 | -17.6 | 11.88 | 59.4 | 0 | 0 | 82.36 | 82.36 | 17.6 | 45 | 28.75 | 37.36 | 0 | 0 | 0 | Normal
2025-09-03 | 246 | 9 | Spring | 0 | 9.23 | -17.8 | 11.54 | 65.7 | 0 | 0 | 72.74 | 72.74 | 17.8 | 51.4 | 36.6 | 21.34 | 0 | 0 | 0 | Normal
2025-09-03 01:00 | 246 | 9 | Spring | 1 | 9.23 | -21.5 | 4.91 | 46.4 | 0 | 0 | 0.39 | 0.39 | 21.5 | 59.76 | 15 | -54 | 5.37 | 1.989 | 0 | Diesel-backup
2025-09-03 02:00 | 246 | 9 | Spring | 2 | 9.23 | -21.2 | 5.86 | 32.5 | 0 | 0 | 1.84 | 1.84 | 21.2 | 54.69 | 15 | 0 | 52.85 | 16.912 | 0 | Diesel-backup
2025-09-03 03:00 | 246 | 9 | Spring | 3 | 9.23 | -21.6 | 11.17 | 26.1 | 0 | 0 | 63.15 | 63.15 | 21.6 | 62.34 | 15.3 | 0.81 | 0 | 0 | 0 | Normal
2025-09-03 04:00 | 246 | 9 | Spring | 4 | 9.23 | -20.1 | 3.28 | 48.8 | 0 | 0 | 0 | 0 | 20.1 | 56.72 | 15 | -0.75 | 55.97 | 17.912 | 0 | Diesel-backup
2025-09-03 05:00 | 246 | 9 | Spring | 5 | 9.23 | -18.7 | 14.48 | 46 | 0 | 0 | 120 | 120 | 18.7 | 50.1 | 40.72 | 69.9 | 0 | 0 | 0 | Normal
2025-09-03 06:00 | 246 | 9 | Spring | 6 | 9.23 | -21.5 | 8.54 | 57.1 | 0 | 0 | 17.92 | 17.92 | 21.5 | 57.42 | 24.92 | -39.5 | 0 | 0 | 0 | Battery-supported
2025-09-03 07:00 | 246 | 9 | Spring | 7 | 9.23 | -18.2 | 9.7 | 47.2 | 0 | 0 | 33.36 | 33.36 | 18.2 | 60.23 | 15 | -24.81 | 2.06 | 0.773 | 0 | Diesel-backup
2025-09-03 08:00 | 246 | 9 | Spring | 8 | 9.23 | -20.6 | 10.21 | 0.4 | 136.3 | 6.95 | 42.28 | 49.23 | 20.6 | 64.64 | 15 | 0 | 15.41 | 5.515 | 0 | Diesel-backup
2025-09-03 09:00 | 246 | 9 | Spring | 9 | 9.23 | -23 | 4.24 | 49.4 | 216 | 11.02 | 0.06 | 11.08 | 23 | 68.16 | 15 | 0 | 57.08 | 18.266 | 0 | Diesel-backup
2025-09-03 10:00 | 246 | 9 | Spring | 10 | 9.23 | -20.5 | 10.24 | 82.8 | 193.2 | 9.85 | 42.85 | 52.7 | 20.5 | 65.42 | 15 | 0 | 12.72 | 4.596 | 0 | Diesel-backup
2025-09-03 11:00 | 246 | 9 | Spring | 11 | 9.23 | -18.4 | 13.5 | 17.1 | 539 | 27.49 | 120 | 147.49 | 18.4 | 58.57 | 47.72 | 88.92 | 0 | 0 | 0 | Normal
2025-09-03 12:00 | 246 | 9 | Spring | 12 | 9.23 | -17.4 | 6.24 | 53.9 | 390.7 | 23.44 | 2.88 | 26.32 | 17.4 | 53.81 | 36.73 | -27.49 | 0 | 0 | 0 | Battery-supported
2025-09-03 13:00 | 246 | 9 | Spring | 13 | 9.23 | -18.8 | 5.79 | 21.3 | 519.4 | 26.49 | 1.68 | 28.17 | 18.8 | 63.4 | 22.63 | -35.23 | 0 | 0 | 0 | Battery-supported
2025-09-03 14:00 | 246 | 9 | Spring | 14 | 9.23 | -21 | 26.97 | 62.2 | 272 | 13.87 | 120 | 133.87 | 21 | 69.87 | 46.19 | 64 | 0 | 0 | 0 | Normal
2025-09-03 15:00 | 246 | 9 | Spring | 15 | 9.23 | -21.1 | 5.41 | 1.2 | 339.9 | 17.33 | 0.98 | 18.31 | 21.1 | 66.55 | 26.89 | -48.24 | 0 | 0 | 0 | Battery-supported
2025-09-03 16:00 | 246 | 9 | Spring | 16 | 9.23 | -19 | 7.52 | 25 | 111 | 5.66 | 9.09 | 14.75 | 19 | 56.68 | 15 | -29.73 | 12.2 | 4.417 | 0 | Diesel-backup
2025-09-03 17:00 | 246 | 9 | Spring | 17 | 9.23 | -16.3 | 20.86 | 74.4 | 0 | 0 | 120 | 120 | 16.3 | 61.06 | 36.69 | 58.94 | 0 | 0 | 0 | Normal
2025-09-03 18:00 | 246 | 9 | Spring | 18 | 9.23 | -18.8 | 3.11 | 82.8 | 0 | 0 | 0 | 0 | 18.8 | 65.64 | 15 | -54.22 | 11.42 | 4.144 | 0 | Diesel-backup
2025-09-03 19:00 | 246 | 9 | Spring | 19 | 9.23 | -18.6 | 9.02 | 40.5 | 0 | 0 | 23.54 | 23.54 | 18.6 | 66.44 | 15 | 0 | 42.9 | 13.843 | 0 | Diesel-backup
2025-09-03 20:00 | 246 | 9 | Spring | 20 | 9.23 | -19.4 | 13.33 | 80.8 | 0 | 0 | 120 | 120 | 19.4 | 64.95 | 35.26 | 55.05 | 0 | 0 | 0 | Normal
2025-09-03 21:00 | 246 | 9 | Spring | 21 | 9.23 | -20.3 | 9.36 | 44.3 | 0 | 0 | 28.16 | 28.16 | 20.3 | 56.4 | 23.96 | -28.24 | 0 | 0 | 0 | Battery-supported
2025-09-03 22:00 | 246 | 9 | Spring | 22 | 9.23 | -20.1 | 2.76 | 83.2 | 0 | 0 | 0 | 0 | 20.1 | 52.63 | 15 | -22.41 | 30.22 | 10.243 | 0 | Diesel-backup
2025-09-03 23:00 | 246 | 9 | Spring | 23 | 9.23 | -19.7 | 4.55 | 69.8 | 0 | 0 | 0.16 | 0.16 | 19.7 | 54.04 | 15 | 0 | 53.88 | 17.242 | 0 | Diesel-backup
2025-09-04 | 247 | 9 | Spring | 0 | 9.39 | -16.4 | 2.44 | 51.9 | 0 | 0 | 0 | 0 | 16.4 | 55.47 | 15 | 0 | 55.47 | 17.75 | 0 | Diesel-backup
2025-09-04 01:00 | 247 | 9 | Spring | 1 | 9.39 | -21 | 8.63 | 14.2 | 0 | 0 | 18.9 | 18.9 | 21 | 52.7 | 15 | 0 | 33.8 | 11.301 | 0 | Diesel-backup
2025-09-04 02:00 | 247 | 9 | Spring | 2 | 9.39 | -20.8 | 12.16 | 41.2 | 0 | 0 | 90.9 | 90.9 | 20.8 | 52.35 | 29.19 | 38.55 | 0 | 0 | 0 | Normal
2025-09-04 03:00 | 247 | 9 | Spring | 3 | 9.39 | -23.2 | 6.2 | 25.8 | 0 | 0 | 2.75 | 2.75 | 23.2 | 61.14 | 15 | -35.47 | 22.92 | 7.983 | 0 | Diesel-backup
2025-09-04 04:00 | 247 | 9 | Spring | 4 | 9.39 | -20.1 | 7.85 | 89.9 | 0 | 0 | 11.52 | 11.52 | 20.1 | 56.69 | 15 | 0 | 45.17 | 14.454 | 0 | Diesel-backup
2025-09-04 05:00 | 247 | 9 | Spring | 5 | 9.39 | -19 | 7.82 | 68.7 | 0 | 0 | 11.28 | 11.28 | 19 | 59.93 | 15 | 0 | 48.65 | 15.568 | 0 | Diesel-backup
2025-09-04 06:00 | 247 | 9 | Spring | 6 | 9.39 | -18.6 | 18.91 | 63.1 | 0 | 0 | 120 | 120 | 18.6 | 57.31 | 38.07 | 62.69 | 0 | 0 | 0 | Normal
2025-09-04 07:00 | 247 | 9 | Spring | 7 | 9.39 | -21.9 | 11.04 | 58 | 0 | 0 | 60 | 60 | 21.9 | 54.77 | 39.99 | 5.23 | 0 | 0 | 0 | Normal
2025-09-04 08:00 | 247 | 9 | Spring | 8 | 9.39 | -21.1 | 10.19 | 78.9 | 61.8 | 3.15 | 41.91 | 45.06 | 21.1 | 70.37 | 29.87 | -25.31 | 0 | 0 | 0 | Battery-supported
2025-09-04 09:00 | 247 | 9 | Spring | 9 | 9.39 | -22.7 | 17.21 | 31.3 | 269.8 | 13.76 | 120 | 133.76 | 22.7 | 67 | 54.44 | 66.76 | 0 | 0 | 0 | Normal
2025-09-04 10:00 | 247 | 9 | Spring | 10 | 9.39 | -21 | 3.68 | 35.8 | 376.4 | 19.2 | 0 | 19.2 | 21 | 66.9 | 35.36 | -47.7 | 0 | 0 | 0 | Battery-supported
2025-09-04 11:00 | 247 | 9 | Spring | 11 | 9.39 | -21.3 | 10.95 | 46.1 | 405.2 | 20.67 | 57.87 | 78.54 | 21.3 | 62.98 | 41.08 | 15.56 | 0 | 0 | 0 | Normal
2025-09-04 12:00 | 247 | 9 | Spring | 12 | 9.39 | -21.5 | 6.87 | 16.5 | 574.7 | 29.31 | 5.36 | 34.67 | 21.5 | 66.64 | 28.3 | -31.97 | 0 | 0 | 0 | Battery-supported
2025-09-04 13:00 | 247 | 9 | Spring | 13 | 9.39 | -21 | 20.38 | 28.8 | 485.6 | 24.77 | 120 | 144.77 | 21 | 62.01 | 58.75 | 82.76 | 0 | 0 | 0 | Normal
2025-09-04 14:00 | 247 | 9 | Spring | 14 | 9.39 | -19.9 | 17.29 | 47.9 | 329.8 | 16.82 | 120 | 136.82 | 19.9 | 54.5 | 89.05 | 82.32 | 0 | 0 | 0 | Normal
2025-09-04 15:00 | 247 | 9 | Spring | 15 | 9.39 | -21.2 | 6.87 | 29.6 | 274.4 | 13.99 | 5.36 | 19.35 | 21.2 | 71.57 | 68.16 | -52.22 | 0 | 0 | 0 | Battery-supported
2025-09-04 16:00 | 247 | 9 | Spring | 16 | 9.39 | -20.7 | 8.15 | 5.2 | 145.5 | 7.42 | 14.07 | 21.49 | 20.7 | 60.34 | 52.62 | -38.85 | 0 | 0 | 0 | Battery-supported
2025-09-04 17:00 | 247 | 9 | Spring | 17 | 9.39 | -16.1 | 5.18 | 61.1 | 0 | 0 | 0.66 | 0.66 | 16.1 | 56.97 | 30.09 | -56.31 | 0 | 0 | 0 | Battery-supported
2025-09-04 18:00 | 247 | 9 | Spring | 18 | 9.39 | -13.6 | 15.74 | 47 | 0 | 0 | 120 | 120 | 13.6 | 54.22 | 54.3 | 65.78 | 0 | 0 | 0 | Normal
2025-09-04 19:00 | 247 | 9 | Spring | 19 | 9.39 | -22.1 | 13.81 | 75 | 0 | 0 | 120 | 120 | 22.1 | 72.49 | 71.78 | 47.51 | 0 | 0 | 0 | Normal
2025-09-04 20:00 | 247 | 9 | Spring | 20 | 9.39 | -22.2 | 8.43 | 51.9 | 0 | 0 | 16.77 | 16.77 | 22.2 | 67.27 | 51.58 | -50.5 | 0 | 0 | 0 | Battery-supported
2025-09-04 21:00 | 247 | 9 | Spring | 21 | 9.39 | -21.6 | 8.37 | 5.6 | 0 | 0 | 16.17 | 16.17 | 21.6 | 59.27 | 34.34 | -43.1 | 0 | 0 | 0 | Battery-supported
2025-09-04 22:00 | 247 | 9 | Spring | 22 | 9.39 | -19.8 | 7.23 | 73.5 | 0 | 0 | 7.26 | 7.26 | 19.8 | 58.8 | 15 | -48.36 | 3.18 | 1.187 | 0 | Diesel-backup
2025-09-04 23:00 | 247 | 9 | Spring | 23 | 9.39 | -17.9 | 19.67 | 47.4 | 0 | 0 | 120 | 120 | 17.9 | 56.06 | 38.53 | 63.94 | 0 | 0 | 0 | Normal
2025-09-05 | 248 | 9 | Spring | 0 | 9.55 | -18.7 | 8.87 | 31.6 | 0 | 0 | 21.67 | 21.67 | 18.7 | 54.72 | 25.31 | -33.05 | 0 | 0 | 0 | Battery-supported
2025-09-05 01:00 | 248 | 9 | Spring | 1 | 9.55 | -20 | 7.39 | 47 | 0 | 0 | 8.24 | 8.24 | 20 | 55.89 | 15 | -25.77 | 21.88 | 7.648 | 0 | Diesel-backup
2025-09-05 02:00 | 248 | 9 | Spring | 2 | 9.55 | -19.6 | 14.83 | 49.3 | 0 | 0 | 120 | 120 | 19.6 | 60.73 | 36.81 | 59.27 | 0 | 0 | 0 | Normal
2025-09-05 03:00 | 248 | 9 | Spring | 3 | 9.55 | -22.7 | 1.52 | 65.8 | 0 | 0 | 0 | 0 | 22.7 | 52.99 | 15.62 | -52.99 | 0 | 0 | 0 | Battery-supported
2025-09-05 04:00 | 248 | 9 | Spring | 4 | 9.55 | -22 | 8.04 | 28.5 | 0 | 0 | 13.1 | 13.1 | 22 | 53.6 | 15 | -1.54 | 38.96 | 12.769 | 0 | Diesel-backup
2025-09-05 05:00 | 248 | 9 | Spring | 5 | 9.55 | -21.8 | 16 | 64.6 | 0 | 0 | 120 | 120 | 21.8 | 59.53 | 37.25 | 60.47 | 0 | 0 | 0 | Normal
2025-09-05 06:00 | 248 | 9 | Spring | 6 | 9.55 | -25.5 | 22.15 | 77.2 | 0 | 0 | 120 | 120 | 25.5 | 61.96 | 58.61 | 58.04 | 0 | 0 | 0 | Normal
2025-09-05 07:00 | 248 | 9 | Spring | 7 | 9.55 | -24.7 | 6.36 | 65.1 | 0 | 0 | 3.27 | 3.27 | 24.7 | 58.45 | 36.54 | -55.18 | 0 | 0 | 0 | Battery-supported
2025-09-05 08:00 | 248 | 9 | Spring | 8 | 9.55 | -24.7 | 12.87 | 74.6 | 72.9 | 3.72 | 115.14 | 118.86 | 24.7 | 77.34 | 51.82 | 41.52 | 0 | 0 | 0 | Normal
2025-09-05 09:00 | 248 | 9 | Spring | 9 | 9.55 | -20.5 | 6.33 | 26.3 | 290.3 | 14.81 | 3.17 | 17.98 | 20.5 | 58.89 | 35.46 | -40.91 | 0 | 0 | 0 | Battery-supported
2025-09-05 10:00 | 248 | 9 | Spring | 10 | 9.55 | -21.5 | 28.13 | 81 | 203.8 | 10.39 | 0 | 10.39 | 21.5 | 64.82 | 15 | -51.14 | 3.29 | 1.229 | 0 | Diesel-backup
2025-09-05 11:00 | 248 | 9 | Spring | 11 | 9.55 | -20.5 | 10.54 | 0 | 620.8 | 31.66 | 48.83 | 80.49 | 20.5 | 64.75 | 20.79 | 15.74 | 0 | 0 | 0 | Normal
2025-09-05 12:00 | 248 | 9 | Spring | 12 | 9.55 | -25.5 | 13.72 | 39.6 | 460.9 | 23.51 | 120 | 143.51 | 25.5 | 66.99 | 48.95 | 76.52 | 0 | 0 | 0 | Normal
2025-09-05 13:00 | 248 | 9 | Spring | 13 | 9.55 | -24.4 | 1.82 | 22.7 | 515.3 | 26.28 | 0 | 26.28 | 24.4 | 64.84 | 33.53 | -38.56 | 0 | 0 | 0 | Battery-supported
2025-09-05 14:00 | 248 | 9 | Spring | 14 | 9.55 | -19.3 | 7.16 | 72.5 | 236.6 | 12.07 | 6.86 | 18.93 | 19.3 | 61.18 | 16.63 | -42.25 | 0 | 0 | 0 | Battery-supported
2025-09-05 15:00 | 248 | 9 | Spring | 15 | 9.55 | -26.5 | 14.87 | 52.7 | 218.7 | 11.15 | 120 | 131.15 | 26.5 | 75.96 | 36.94 | 55.19 | 0 | 0 | 0 | Normal
2025-09-05 16:00 | 248 | 9 | Spring | 16 | 9.55 | -17.3 | 3.65 | 53.7 | 98.9 | 5.93 | 0 | 5.93 | 17.3 | 58.87 | 15.76 | -52.94 | 0 | 0 | 0 | Battery-supported
2025-09-05 17:00 | 248 | 9 | Spring | 17 | 9.55 | -23.7 | 10.53 | 21 | 0 | 0 | 48.63 | 48.63 | 23.7 | 68.36 | 15 | -1.9 | 17.83 | 6.324 | 0 | Diesel-backup
2025-09-05 18:00 | 248 | 9 | Spring | 18 | 9.55 | -17.6 | 22.72 | 40.3 | 0 | 0 | 120 | 120 | 17.6 | 58.27 | 37.72 | 61.73 | 0 | 0 | 0 | Normal
2025-09-05 19:00 | 248 | 9 | Spring | 19 | 9.55 | -21.3 | 15.34 | 21.1 | 0 | 0 | 120 | 120 | 21.3 | 67.24 | 57.13 | 52.76 | 0 | 0 | 0 | Normal
2025-09-05 20:00 | 248 | 9 | Spring | 20 | 9.55 | -16.9 | 13.14 | 19.6 | 0 | 0 | 120 | 120 | 16.9 | 64.3 | 77.63 | 55.7 | 0 | 0 | 0 | Normal
2025-09-05 21:00 | 248 | 9 | Spring | 21 | 9.55 | -12.2 | 7.43 | 18.5 | 0 | 0 | 8.5 | 8.5 | 12.2 | 46.52 | 62.42 | -38.02 | 0 | 0 | 0 | Battery-supported
2025-09-05 22:00 | 248 | 9 | Spring | 22 | 9.55 | -24.4 | 4.36 | 40.5 | 0 | 0 | 0.09 | 0.09 | 24.4 | 62.23 | 37.57 | -62.14 | 0 | 0 | 0 | Battery-supported
2025-09-05 23:00 | 248 | 9 | Spring | 23 | 9.55 | -18.2 | 9.28 | 7.7 | 0 | 0 | 27.03 | 27.03 | 18.2 | 52.76 | 27.27 | -25.73 | 0 | 0 | 0 | Battery-supported
2025-09-06 | 249 | 9 | Spring | 0 | 9.71 | -23.8 | 14.02 | 43.6 | 0 | 0 | 120 | 120 | 23.8 | 58.99 | 49.73 | 61.01 | 0 | 0 | 0 | Normal
2025-09-06 01:00 | 249 | 9 | Spring | 1 | 9.71 | -19.3 | 5.15 | 17 | 0 | 0 | 0.63 | 0.63 | 19.3 | 56.12 | 27.53 | -55.49 | 0 | 0 | 0 | Battery-supported
2025-09-06 02:00 | 249 | 9 | Spring | 2 | 9.71 | -21 | 15.23 | 45.4 | 0 | 0 | 120 | 120 | 21 | 57.27 | 50.61 | 62.73 | 0 | 0 | 0 | Normal
2025-09-06 03:00 | 249 | 9 | Spring | 3 | 9.71 | -20.7 | 10.85 | 42.3 | 0 | 0 | 55.57 | 55.57 | 20.7 | 56.66 | 50.18 | -1.09 | 0 | 0 | 0 | Battery-supported
2025-09-06 04:00 | 249 | 9 | Spring | 4 | 9.71 | -23.3 | 5.77 | 55.9 | 0 | 0 | 1.64 | 1.64 | 23.3 | 52.41 | 29.87 | -50.77 | 0 | 0 | 0 | Battery-supported
2025-09-06 05:00 | 249 | 9 | Spring | 5 | 9.71 | -19.9 | 3 | 30.1 | 0 | 0 | 0 | 0 | 19.9 | 49.96 | 15 | -37.18 | 12.78 | 4.618 | 0 | Diesel-backup
2025-09-06 06:00 | 249 | 9 | Spring | 6 | 9.71 | -25.1 | 3.59 | 76.7 | 0 | 0 | 0 | 0 | 25.1 | 53.18 | 15 | 0 | 53.18 | 17.018 | 0 | Diesel-backup
2025-09-06 07:00 | 249 | 9 | Spring | 7 | 9.71 | -19.3 | 9.04 | 19.6 | 0 | 0 | 23.8 | 23.8 | 19.3 | 48.7 | 15 | 0 | 24.9 | 8.609 | 0 | Diesel-backup
2025-09-06 08:00 | 249 | 9 | Spring | 8 | 9.71 | -23 | 18.11 | 89.7 | 58.7 | 2.99 | 120 | 122.99 | 23 | 67.84 | 35.3 | 55.15 | 0 | 0 | 0 | Normal
2025-09-06 09:00 | 249 | 9 | Spring | 9 | 9.71 | -25.1 | 5.82 | 24.1 | 303.5 | 15.48 | 1.75 | 17.23 | 25.1 | 66.69 | 15.51 | -49.46 | 0 | 0 | 0 | Battery-supported
2025-09-06 10:00 | 249 | 9 | Spring | 10 | 9.71 | -18.4 | 19.47 | 50.1 | 326.9 | 16.67 | 120 | 136.67 | 18.4 | 58.87 | 44.14 | 77.8 | 0 | 0 | 0 | Normal
2025-09-06 11:00 | 249 | 9 | Spring | 11 | 9.71 | -21.8 | 2.73 | 57.3 | 354.5 | 18.08 | 0 | 18.08 | 21.8 | 72.01 | 22.57 | -53.93 | 0 | 0 | 0 | Battery-supported
2025-09-06 12:00 | 249 | 9 | Spring | 12 | 9.71 | -17.1 | 9.98 | 23 | 542.6 | 32.56 | 38.08 | 70.64 | 17.1 | 64.91 | 24.68 | 5.73 | 0 | 0 | 0 | Normal
2025-09-06 13:00 | 249 | 9 | Spring | 13 | 9.71 | -18.3 | 9.39 | 18 | 537.7 | 27.42 | 28.6 | 56.02 | 18.3 | 54.94 | 25.08 | 1.08 | 0 | 0 | 0 | Normal
2025-09-06 14:00 | 249 | 9 | Spring | 14 | 9.71 | -22.3 | 12.16 | 63.9 | 272.4 | 13.89 | 90.9 | 104.79 | 22.3 | 61.83 | 40.88 | 42.96 | 0 | 0 | 0 | Normal
2025-09-06 15:00 | 249 | 9 | Spring | 15 | 9.71 | -20.4 | 10.74 | 77.9 | 154 | 7.85 | 53.12 | 60.97 | 20.4 | 59.61 | 41.39 | 1.36 | 0 | 0 | 0 | Normal
2025-09-06 16:00 | 249 | 9 | Spring | 16 | 9.71 | -19.6 | 7.35 | 47.4 | 115.5 | 5.89 | 7.99 | 13.88 | 19.6 | 62.85 | 21.8 | -48.97 | 0 | 0 | 0 | Battery-supported
2025-09-06 17:00 | 249 | 9 | Spring | 17 | 9.71 | -16.2 | 7.39 | 55.9 | 0 | 0 | 8.24 | 8.24 | 16.2 | 54.03 | 15 | -16.99 | 28.8 | 9.812 | 0 | Diesel-backup
2025-09-06 18:00 | 249 | 9 | Spring | 18 | 9.71 | -18.3 | 16.23 | 52.1 | 0 | 0 | 120 | 120 | 18.3 | 58.58 | 37.6 | 61.42 | 0 | 0 | 0 | Normal
2025-09-06 19:00 | 249 | 9 | Spring | 19 | 9.71 | -18.7 | 10.3 | 37.4 | 0 | 0 | 44.01 | 44.01 | 18.7 | 63.37 | 29.86 | -19.36 | 0 | 0 | 0 | Battery-supported
2025-09-06 20:00 | 249 | 9 | Spring | 20 | 9.71 | -19.5 | 1.73 | 90.1 | 0 | 0 | 0 | 0 | 19.5 | 61.97 | 15 | -37.15 | 24.82 | 8.585 | 0 | Diesel-backup
2025-09-06 21:00 | 249 | 9 | Spring | 21 | 9.71 | -19.2 | 7.82 | 74.9 | 0 | 0 | 11.28 | 11.28 | 19.2 | 48.96 | 15 | 0 | 37.68 | 12.411 | 0 | Diesel-backup
2025-09-06 22:00 | 249 | 9 | Spring | 22 | 9.71 | -16.4 | 8.26 | 54.5 | 0 | 0 | 15.09 | 15.09 | 16.4 | 51.81 | 15 | 0 | 36.72 | 12.14 | 0 | Diesel-backup
2025-09-06 23:00 | 249 | 9 | Spring | 23 | 9.71 | -19.5 | 8.23 | 65.7 | 0 | 0 | 14.81 | 14.81 | 19.5 | 55.02 | 15 | 0 | 40.21 | 13.114 | 0 | Diesel-backup
2025-09-07 | 250 | 9 | Spring | 0 | 9.87 | -20.5 | 14.86 | 63.2 | 0 | 0 | 120 | 120 | 20.5 | 56.36 | 38.42 | 63.64 | 0 | 0 | 0 | Normal
2025-09-07 01:00 | 250 | 9 | Spring | 1 | 9.87 | -21.3 | 6.66 | 50 | 0 | 0 | 4.42 | 4.42 | 21.3 | 50.67 | 19.92 | -46.25 | 0 | 0 | 0 | Battery-supported
2025-09-07 02:00 | 250 | 9 | Spring | 2 | 9.87 | -21.6 | 11.25 | 72.7 | 0 | 0 | 65.15 | 65.15 | 21.6 | 60.52 | 21.62 | 4.63 | 0 | 0 | 0 | Normal
2025-09-07 03:00 | 250 | 9 | Spring | 3 | 9.87 | -23.9 | 22.83 | 35.6 | 0 | 0 | 120 | 120 | 23.9 | 56.91 | 44.84 | 63.09 | 0 | 0 | 0 | Normal
2025-09-07 04:00 | 250 | 9 | Spring | 4 | 9.87 | -22.8 | 18.13 | 68.6 | 0 | 0 | 120 | 120 | 22.8 | 53.19 | 69.43 | 66.81 | 0 | 0 | 0 | Normal
2025-09-07 05:00 | 250 | 9 | Spring | 5 | 9.87 | -18.2 | 6.28 | 65 | 0 | 0 | 3.01 | 3.01 | 18.2 | 53.48 | 49.24 | -50.47 | 0 | 0 | 0 | Battery-supported
2025-09-07 06:00 | 250 | 9 | Spring | 6 | 9.87 | -22.2 | 10.46 | 53.3 | 0 | 0 | 47.19 | 47.19 | 22.2 | 59.85 | 44.17 | -12.66 | 0 | 0 | 0 | Battery-supported
2025-09-07 07:00 | 250 | 9 | Spring | 7 | 9.87 | -20.3 | 1.04 | 24.3 | 0 | 0 | 0 | 0 | 20.3 | 57.69 | 21.1 | -57.69 | 0 | 0 | 0 | Battery-supported
2025-09-07 08:00 | 250 | 9 | Spring | 8 | 9.87 | -27.4 | 13.53 | 61.4 | 103.7 | 5.29 | 120 | 125.29 | 27.4 | 75.55 | 39.4 | 49.74 | 0 | 0 | 0 | Normal
2025-09-07 09:00 | 250 | 9 | Spring | 9 | 9.87 | -20.6 | 4.12 | 62.2 | 202.2 | 10.31 | 0.03 | 10.34 | 20.6 | 61.06 | 19.11 | -50.72 | 0 | 0 | 0 | Battery-supported
2025-09-07 10:00 | 250 | 9 | Spring | 10 | 9.87 | -22.1 | 9.6 | 56.8 | 302.8 | 15.44 | 31.77 | 47.21 | 22.1 | 58.62 | 15 | -10.29 | 1.12 | 0.422 | 0 | Diesel-backup
2025-09-07 11:00 | 250 | 9 | Spring | 11 | 9.87 | -22.5 | 8.83 | 55.8 | 362.1 | 18.47 | 21.19 | 39.66 | 22.5 | 64.19 | 15 | 0 | 24.53 | 8.492 | 0 | Diesel-backup
2025-09-07 12:00 | 250 | 9 | Spring | 12 | 9.87 | -20.8 | 17.61 | 35.8 | 480 | 24.48 | 120 | 144.48 | 20.8 | 52.49 | 48.85 | 91.99 | 0 | 0 | 0 | Normal
2025-09-07 13:00 | 250 | 9 | Spring | 13 | 9.87 | -21.9 | 11.3 | 61.8 | 334.1 | 17.04 | 66.42 | 83.46 | 21.9 | 61.57 | 56.91 | 21.89 | 0 | 0 | 0 | Normal
2025-09-07 14:00 | 250 | 9 | Spring | 14 | 9.87 | -25.1 | 8.79 | 63.2 | 277.4 | 14.15 | 20.72 | 34.87 | 25.1 | 66.76 | 44.15 | -31.89 | 0 | 0 | 0 | Battery-supported
2025-09-07 15:00 | 250 | 9 | Spring | 15 | 9.87 | -18 | 14.07 | 7 | 358.8 | 21.53 | 120 | 141.53 | 18 | 59.03 | 74.51 | 82.5 | 0 | 0 | 0 | Normal
2025-09-07 16:00 | 250 | 9 | Spring | 16 | 9.87 | -19.1 | 19.23 | 59 | 107.1 | 5.46 | 120 | 125.46 | 19.1 | 64.14 | 95 | 55.67 | 0 | 0 | 0 | Normal
2025-09-07 17:00 | 250 | 9 | Spring | 17 | 9.87 | -20.1 | 1.35 | 19.9 | 0 | 0 | 0 | 0 | 20.1 | 63.01 | 69.8 | -63.01 | 0 | 0 | 0 | Battery-supported
2025-09-07 18:00 | 250 | 9 | Spring | 18 | 9.87 | -21.3 | 6.52 | 38.7 | 0 | 0 | 3.86 | 3.86 | 21.3 | 66.09 | 44.9 | -62.23 | 0 | 0 | 0 | Battery-supported
2025-09-07 19:00 | 250 | 9 | Spring | 19 | 9.87 | -22.2 | 23.2 | 36.2 | 0 | 0 | 120 | 120 | 22.2 | 66.32 | 64.66 | 53.68 | 0 | 0 | 0 | Normal
2025-09-07 20:00 | 250 | 9 | Spring | 20 | 9.87 | -18.4 | 29.56 | 44.3 | 0 | 0 | 0 | 0 | 18.4 | 55.46 | 42.47 | -55.46 | 0 | 0 | 0 | Battery-supported
2025-09-07 21:00 | 250 | 9 | Spring | 21 | 9.87 | -15.4 | 5.73 | 20.4 | 0 | 0 | 1.55 | 1.55 | 15.4 | 52.81 | 21.97 | -51.26 | 0 | 0 | 0 | Battery-supported
2025-09-07 22:00 | 250 | 9 | Spring | 22 | 9.87 | -18.7 | 16.03 | 23.9 | 0 | 0 | 120 | 120 | 18.7 | 51.54 | 47.16 | 68.46 | 0 | 0 | 0 | Normal
2025-09-07 23:00 | 250 | 9 | Spring | 23 | 9.87 | -22.4 | 5.72 | 42.9 | 0 | 0 | 1.53 | 1.53 | 22.4 | 58.26 | 24.47 | -56.73 | 0 | 0 | 0 | Battery-supported
2025-09-08 | 251 | 9 | Spring | 0 | 10.02 | -19 | 4.68 | 84.2 | 0 | 0 | 0.23 | 0.23 | 19 | 55.85 | 15 | -23.68 | 31.94 | 10.755 | 0 | Diesel-backup
2025-09-08 01:00 | 251 | 9 | Spring | 1 | 10.02 | -20 | 8.98 | 46.3 | 0 | 0 | 23.03 | 23.03 | 20 | 51.82 | 15 | 0 | 28.79 | 9.81 | 0 | Diesel-backup
2025-09-08 02:00 | 251 | 9 | Spring | 2 | 10.02 | -18.4 | 17.07 | 63.4 | 0 | 0 | 120 | 120 | 18.4 | 50.64 | 40.52 | 69.36 | 0 | 0 | 0 | Normal
2025-09-08 03:00 | 251 | 9 | Spring | 3 | 10.02 | -19.3 | 8.29 | 11 | 0 | 0 | 15.38 | 15.38 | 19.3 | 54.44 | 24.9 | -39.06 | 0 | 0 | 0 | Battery-supported
2025-09-08 04:00 | 251 | 9 | Spring | 4 | 10.02 | -27.6 | 16.94 | 67 | 0 | 0 | 120 | 120 | 27.6 | 60.67 | 46.73 | 59.33 | 0 | 0 | 0 | Normal
2025-09-08 05:00 | 251 | 9 | Spring | 5 | 10.02 | -20.1 | 17.85 | 10.7 | 0 | 0 | 120 | 120 | 20.1 | 61.98 | 68.09 | 58.02 | 0 | 0 | 0 | Normal
2025-09-08 06:00 | 251 | 9 | Spring | 6 | 10.02 | -23.8 | 7.15 | 51.1 | 0 | 0 | 6.81 | 6.81 | 23.8 | 58.84 | 47.27 | -52.03 | 0 | 0 | 0 | Battery-supported
2025-09-08 07:00 | 251 | 9 | Spring | 7 | 10.02 | -24.8 | 7.02 | 68.3 | 1.2 | 0.06 | 6.1 | 6.16 | 24.8 | 55.15 | 27.68 | -48.99 | 0 | 0 | 0 | Battery-supported
2025-09-08 08:00 | 251 | 9 | Spring | 8 | 10.02 | -22.2 | 8.43 | 22.2 | 170.5 | 8.7 | 16.77 | 25.47 | 22.2 | 73.54 | 15 | -31.69 | 16.38 | 5.841 | 0 | Diesel-backup
2025-09-08 09:00 | 251 | 9 | Spring | 9 | 10.02 | -20.8 | 9.79 | 34.8 | 285.8 | 14.58 | 34.83 | 49.41 | 20.8 | 65.2 | 15 | 0 | 15.79 | 5.643 | 0 | Diesel-backup
2025-09-08 10:00 | 251 | 9 | Spring | 10 | 10.02 | -25.2 | 9.08 | 35.9 | 388.1 | 19.79 | 24.32 | 44.11 | 25.2 | 68.05 | 15 | 0 | 23.94 | 8.306 | 0 | Diesel-backup
2025-09-08 11:00 | 251 | 9 | Spring | 11 | 10.02 | -19.8 | 10.35 | 59.4 | 345.9 | 17.64 | 44.99 | 62.63 | 19.8 | 68.87 | 15 | 0 | 6.24 | 2.306 | 0 | Diesel-backup
2025-09-08 12:00 | 251 | 9 | Spring | 12 | 10.02 | -19.3 | 7.49 | 40 | 459.2 | 23.42 | 8.89 | 32.31 | 19.3 | 63.53 | 15 | 0 | 31.22 | 10.541 | 0 | Diesel-backup
2025-09-08 13:00 | 251 | 9 | Spring | 13 | 10.02 | -20.5 | 4.38 | 27.9 | 493.4 | 25.16 | 0.1 | 25.26 | 20.5 | 63.17 | 15 | 0 | 37.91 | 12.475 | 0 | Diesel-backup
2025-09-08 14:00 | 251 | 9 | Spring | 14 | 10.02 | -22.2 | 26.2 | 9.8 | 492.3 | 25.11 | 120 | 145.11 | 22.2 | 58.8 | 46.76 | 86.31 | 0 | 0 | 0 | Normal
2025-09-08 15:00 | 251 | 9 | Spring | 15 | 10.02 | -22 | 6.5 | 13.3 | 348.1 | 17.75 | 3.78 | 21.53 | 22 | 55.84 | 33.04 | -34.31 | 0 | 0 | 0 | Battery-supported
2025-09-08 16:00 | 251 | 9 | Spring | 16 | 10.02 | -17.3 | 2.91 | 45.6 | 134.6 | 8.08 | 0 | 8.08 | 17.3 | 65.18 | 15 | -45.1 | 12 | 4.349 | 0 | Diesel-backup
2025-09-08 17:00 | 251 | 9 | Spring | 17 | 10.02 | -22.5 | 14.67 | 70.4 | 1.2 | 0.06 | 120 | 120.06 | 22.5 | 66.7 | 34.64 | 53.36 | 0 | 0 | 0 | Normal
2025-09-08 18:00 | 251 | 9 | Spring | 18 | 10.02 | -16.6 | 4.96 | 56.5 | 0 | 0 | 0.44 | 0.44 | 16.6 | 58.8 | 15 | -49.09 | 9.27 | 3.39 | 0 | Diesel-backup
2025-09-08 19:00 | 251 | 9 | Spring | 19 | 10.02 | -19.2 | 13.83 | 55 | 0 | 0 | 120 | 120 | 19.2 | 61.64 | 36.48 | 58.36 | 0 | 0 | 0 | Normal
2025-09-08 20:00 | 251 | 9 | Spring | 20 | 10.02 | -19 | 6.31 | 7.7 | 0 | 0 | 3.11 | 3.11 | 19 | 63.23 | 15 | -53.69 | 6.43 | 2.375 | 0 | Diesel-backup
2025-09-08 21:00 | 251 | 9 | Spring | 21 | 10.02 | -22.6 | 29.04 | 59.3 | 0 | 0 | 0 | 0 | 22.6 | 60.14 | 15 | 0 | 60.14 | 19.245 | 0 | Diesel-backup
2025-09-08 22:00 | 251 | 9 | Spring | 22 | 10.02 | -19.3 | 20.91 | 7.2 | 0 | 0 | 120 | 120 | 19.3 | 51.19 | 40.32 | 68.81 | 0 | 0 | 0 | Normal
2025-09-08 23:00 | 251 | 9 | Spring | 23 | 10.02 | -17.9 | 8.67 | 39.4 | 0 | 0 | 19.34 | 19.34 | 17.9 | 53.67 | 26.59 | -34.33 | 0 | 0 | 0 | Battery-supported
2025-09-09 | 252 | 9 | Spring | 0 | 10.18 | -22.3 | 13.02 | 47.5 | 0 | 0 | 120 | 120 | 22.3 | 59.41 | 48.89 | 60.59 | 0 | 0 | 0 | Normal
2025-09-09 01:00 | 252 | 9 | Spring | 1 | 10.18 | -18.6 | 11.52 | 67.3 | 0 | 0 | 72.2 | 72.2 | 18.6 | 51.59 | 56.47 | 20.61 | 0 | 0 | 0 | Normal
2025-09-09 02:00 | 252 | 9 | Spring | 2 | 10.18 | -19.9 | 6.15 | 80.7 | 0 | 0 | 2.6 | 2.6 | 19.9 | 46 | 39.11 | -43.4 | 0 | 0 | 0 | Battery-supported
2025-09-09 03:00 | 252 | 9 | Spring | 3 | 10.18 | -21.9 | 14.33 | 51.2 | 0 | 0 | 120 | 120 | 21.9 | 53.82 | 63.47 | 66.18 | 0 | 0 | 0 | Normal
2025-09-09 04:00 | 252 | 9 | Spring | 4 | 10.18 | -19 | 10.27 | 37.8 | 0 | 0 | 43.43 | 43.43 | 19 | 48.79 | 61.32 | -5.36 | 0 | 0 | 0 | Battery-supported
2025-09-09 05:00 | 252 | 9 | Spring | 5 | 10.18 | -26 | 11.15 | 89.6 | 0 | 0 | 62.66 | 62.66 | 26 | 65.74 | 60.09 | -3.08 | 0 | 0 | 0 | Battery-supported
2025-09-09 06:00 | 252 | 9 | Spring | 6 | 10.18 | -20.6 | 13.65 | 77.4 | 0 | 0 | 120 | 120 | 20.6 | 51.75 | 85.21 | 68.25 | 0 | 0 | 0 | Normal
2025-09-09 07:00 | 252 | 9 | Spring | 7 | 10.18 | -18 | 9.21 | 14.5 | 16.3 | 0.98 | 26.06 | 27.04 | 18 | 49.01 | 76.42 | -21.97 | 0 | 0 | 0 | Battery-supported
2025-09-09 08:00 | 252 | 9 | Spring | 8 | 10.18 | -18.4 | 5.64 | 22.6 | 179.8 | 9.17 | 1.37 | 10.54 | 18.4 | 58.81 | 57.11 | -48.27 | 0 | 0 | 0 | Battery-supported
2025-09-09 09:00 | 252 | 9 | Spring | 9 | 10.18 | -20.7 | 13.02 | 32 | 299.8 | 15.29 | 120 | 135.29 | 20.7 | 67.04 | 82.23 | 68.25 | 0 | 0 | 0 | Normal
2025-09-09 10:00 | 252 | 9 | Spring | 10 | 10.18 | -22.1 | 15.06 | 80 | 213.9 | 10.91 | 120 | 130.91 | 22.1 | 68.62 | 95 | 34.71 | 0 | 0 | 0 | Normal
2025-09-09 11:00 | 252 | 9 | Spring | 11 | 10.18 | -22.6 | 15.1 | 22 | 521.9 | 26.62 | 120 | 146.62 | 22.6 | 62.38 | 95 | 0 | 0 | 0 | 0 | Normal
2025-09-09 12:00 | 252 | 9 | Spring | 12 | 10.18 | -21.5 | 15.29 | 53.7 | 391.7 | 19.98 | 120 | 139.98 | 21.5 | 62.7 | 95 | 0 | 0 | 0 | 0 | Normal
2025-09-09 13:00 | 252 | 9 | Spring | 13 | 10.18 | -19.3 | 12.08 | 77.5 | 261.7 | 13.35 | 88.4 | 101.75 | 19.3 | 61.6 | 95 | 0 | 0 | 0 | 0 | Normal
2025-09-09 14:00 | 252 | 9 | Spring | 14 | 10.18 | -21.9 | 3.03 | 72.3 | 244.8 | 12.48 | 0 | 12.48 | 21.9 | 70.46 | 71.81 | -57.98 | 0 | 0 | 0 | Battery-supported
2025-09-09 15:00 | 252 | 9 | Spring | 15 | 10.18 | -18 | 29.71 | 86.5 | 138.7 | 8.32 | 0 | 8.32 | 18 | 52.79 | 54.02 | -44.47 | 0 | 0 | 0 | Battery-supported
2025-09-09 16:00 | 252 | 9 | Spring | 16 | 10.18 | -14.7 | 14.99 | 53.1 | 130.4 | 7.82 | 120 | 127.82 | 14.7 | 52.02 | 81.91 | 75.8 | 0 | 0 | 0 | Normal
2025-09-09 17:00 | 252 | 9 | Spring | 17 | 10.18 | -19.2 | 7.74 | 96.4 | 5.1 | 0.26 | 10.67 | 10.93 | 19.2 | 71.92 | 57.52 | -60.99 | 0 | 0 | 0 | Battery-supported
2025-09-09 18:00 | 252 | 9 | Spring | 18 | 10.18 | -21.8 | 16.28 | 61.5 | 0 | 0 | 120 | 120 | 21.8 | 69.51 | 76.1 | 50.49 | 0 | 0 | 0 | Normal
2025-09-09 19:00 | 252 | 9 | Spring | 19 | 10.18 | -21.6 | 4.57 | 27.1 | 0 | 0 | 0.17 | 0.17 | 21.6 | 58.64 | 52.71 | -58.47 | 0 | 0 | 0 | Battery-supported
2025-09-09 20:00 | 252 | 9 | Spring | 20 | 10.18 | -16.9 | 13.85 | 36.3 | 0 | 0 | 120 | 120 | 16.9 | 72.44 | 70.21 | 47.56 | 0 | 0 | 0 | Normal
2025-09-09 21:00 | 252 | 9 | Spring | 21 | 10.18 | -18.8 | 8.24 | 39.6 | 0 | 0 | 14.91 | 14.91 | 18.8 | 56.35 | 53.64 | -41.44 | 0 | 0 | 0 | Battery-supported
2025-09-09 22:00 | 252 | 9 | Spring | 22 | 10.18 | -16.9 | 4.74 | 84.4 | 0 | 0 | 0.27 | 0.27 | 16.9 | 52.35 | 32.8 | -52.08 | 0 | 0 | 0 | Battery-supported
2025-09-09 23:00 | 252 | 9 | Spring | 23 | 10.18 | -20.2 | 4.69 | 54.8 | 0 | 0 | 0.24 | 0.24 | 20.2 | 61.11 | 15 | -44.51 | 16.36 | 5.834 | 0 | Diesel-backup
2025-09-10 | 253 | 9 | Spring | 0 | 10.34 | -17.4 | 12.58 | 37.4 | 0 | 0 | 104.78 | 104.78 | 17.4 | 48.9 | 35.56 | 55.88 | 0 | 0 | 0 | Normal
2025-09-10 01:00 | 253 | 9 | Spring | 1 | 10.34 | -19.9 | 13.46 | 54 | 0 | 0 | 120 | 120 | 19.9 | 52.96 | 60.23 | 67.04 | 0 | 0 | 0 | Normal
2025-09-10 02:00 | 253 | 9 | Spring | 2 | 10.34 | -21.5 | 5.38 | 44 | 0 | 0 | 0.93 | 0.93 | 21.5 | 56.81 | 37.88 | -55.88 | 0 | 0 | 0 | Battery-supported
2025-09-10 03:00 | 253 | 9 | Spring | 3 | 10.34 | -21.2 | 8.29 | 71.9 | 0 | 0 | 15.38 | 15.38 | 21.2 | 58.22 | 20.75 | -42.84 | 0 | 0 | 0 | Battery-supported
2025-09-10 04:00 | 253 | 9 | Spring | 4 | 10.34 | -23.3 | 11.86 | 87.8 | 0 | 0 | 81.78 | 81.78 | 23.3 | 59.65 | 28.89 | 22.13 | 0 | 0 | 0 | Normal
2025-09-10 05:00 | 253 | 9 | Spring | 5 | 10.34 | -16.6 | 7.02 | 38.1 | 0 | 0 | 6.1 | 6.1 | 16.6 | 52.42 | 15 | -34.73 | 11.59 | 4.206 | 0 | Diesel-backup
2025-09-10 06:00 | 253 | 9 | Spring | 6 | 10.34 | -21.4 | 26.85 | 35.5 | 0 | 0 | 120 | 120 | 21.4 | 54.82 | 38.99 | 65.18 | 0 | 0 | 0 | Normal
2025-09-10 07:00 | 253 | 9 | Spring | 7 | 10.34 | -20 | 12.67 | 49.3 | 21.2 | 1.08 | 107.92 | 109 | 20 | 56.41 | 58.34 | 52.59 | 0 | 0 | 0 | Normal
2025-09-10 08:00 | 253 | 9 | Spring | 8 | 10.34 | -22.6 | 9.2 | 19.5 | 194.8 | 9.93 | 25.92 | 35.85 | 22.6 | 66.68 | 46.01 | -30.83 | 0 | 0 | 0 | Battery-supported
2025-09-10 09:00 | 253 | 9 | Spring | 9 | 10.34 | -23.7 | 17.64 | 40.3 | 280.2 | 14.29 | 120 | 134.29 | 23.7 | 66.66 | 70.9 | 67.63 | 0 | 0 | 0 | Normal
2025-09-10 10:00 | 253 | 9 | Spring | 10 | 10.34 | -21.7 | 13.29 | 61.4 | 290.4 | 14.81 | 120 | 134.81 | 21.7 | 63.64 | 95 | 65.5 | 0 | 0 | 0 | Normal
2025-09-10 11:00 | 253 | 9 | Spring | 11 | 10.34 | -18.6 | 11.92 | 46.5 | 407.8 | 20.8 | 83.55 | 104.35 | 18.6 | 59.52 | 95 | 0 | 0 | 0 | 0 | Normal
2025-09-10 12:00 | 253 | 9 | Spring | 12 | 10.34 | -21.8 | 12.81 | 18.1 | 566.7 | 28.9 | 112.94 | 141.84 | 21.8 | 58.94 | 95 | 0 | 0 | 0 | 0 | Normal
2025-09-10 13:00 | 253 | 9 | Spring | 13 | 10.34 | -22.2 | 15.17 | 49.9 | 391.7 | 19.98 | 120 | 139.98 | 22.2 | 70.9 | 95 | 0 | 0 | 0 | 0 | Normal
2025-09-10 14:00 | 253 | 9 | Spring | 14 | 10.34 | -19.6 | 6.61 | 4.6 | 519.7 | 26.5 | 4.21 | 30.71 | 19.6 | 65.6 | 81.04 | -34.89 | 0 | 0 | 0 | Battery-supported
2025-09-10 15:00 | 253 | 9 | Spring | 15 | 10.34 | -18.4 | 2.47 | 79 | 163.6 | 8.34 | 0 | 8.34 | 18.4 | 65.43 | 58.21 | -57.09 | 0 | 0 | 0 | Battery-supported
2025-09-10 16:00 | 253 | 9 | Spring | 16 | 10.34 | -15.6 | 18.48 | 34.4 | 169.2 | 10.15 | 120 | 130.15 | 15.6 | 53.97 | 86.24 | 76.18 | 0 | 0 | 0 | Normal
2025-09-10 17:00 | 253 | 9 | Spring | 17 | 10.34 | -18.1 | 10.27 | 58.7 | 18.8 | 0.96 | 43.43 | 44.39 | 18.1 | 59.1 | 80.36 | -14.71 | 0 | 0 | 0 | Battery-supported
2025-09-10 18:00 | 253 | 9 | Spring | 18 | 10.34 | -17.2 | 7.41 | 26.1 | 0 | 0 | 8.37 | 8.37 | 17.2 | 59.92 | 59.74 | -51.55 | 0 | 0 | 0 | Battery-supported
2025-09-10 19:00 | 253 | 9 | Spring | 19 | 10.34 | -16.9 | 5.61 | 54.7 | 0 | 0 | 1.31 | 1.31 | 16.9 | 61.33 | 35.73 | -60.02 | 0 | 0 | 0 | Battery-supported
2025-09-10 20:00 | 253 | 9 | Spring | 20 | 10.34 | -21 | 5.13 | 54.1 | 0 | 0 | 0.61 | 0.61 | 21 | 60.92 | 15 | -51.83 | 8.48 | 3.112 | 0 | Diesel-backup
2025-09-10 21:00 | 253 | 9 | Spring | 21 | 10.34 | -20.6 | 10.93 | 86.5 | 0 | 0 | 57.41 | 57.41 | 20.6 | 62.54 | 15 | 0 | 5.13 | 1.903 | 0 | Diesel-backup
2025-09-10 22:00 | 253 | 9 | Spring | 22 | 10.34 | -21 | 9.69 | 90.9 | 0 | 0 | 33.2 | 33.2 | 21 | 59.52 | 15 | 0 | 26.32 | 9.052 | 0 | Diesel-backup
2025-09-10 23:00 | 253 | 9 | Spring | 23 | 10.34 | -21.8 | 17.77 | 12.1 | 0 | 0 | 120 | 120 | 21.8 | 57.52 | 37.99 | 62.48 | 0 | 0 | 0 | Normal
2025-09-11 | 254 | 9 | Spring | 0 | 10.49 | -17.3 | 13.62 | 23.5 | 0 | 0 | 120 | 120 | 17.3 | 53.51 | 62.46 | 66.49 | 0 | 0 | 0 | Normal
2025-09-11 01:00 | 254 | 9 | Spring | 1 | 10.49 | -18.7 | 14.98 | 24.8 | 0 | 0 | 120 | 120 | 18.7 | 52.82 | 87.18 | 67.18 | 0 | 0 | 0 | Normal
2025-09-11 02:00 | 254 | 9 | Spring | 2 | 10.49 | -19.6 | 17.21 | 52.6 | 0 | 0 | 120 | 120 | 19.6 | 51.87 | 95 | 21.24 | 0 | 0 | 0 | Normal
2025-09-11 03:00 | 254 | 9 | Spring | 3 | 10.49 | -25.9 | 11.24 | 55.7 | 0 | 0 | 64.9 | 64.9 | 25.9 | 51.26 | 95 | 0 | 0 | 0 | 0 | Normal
2025-09-11 04:00 | 254 | 9 | Spring | 4 | 10.49 | -16 | 22.3 | 34.5 | 0 | 0 | 120 | 120 | 16 | 54.51 | 95 | 0 | 0 | 0 | 0 | Normal
2025-09-11 05:00 | 254 | 9 | Spring | 5 | 10.49 | -22.8 | 6.37 | 43.1 | 0 | 0 | 3.31 | 3.31 | 22.8 | 58.03 | 73.11 | -54.72 | 0 | 0 | 0 | Battery-supported
2025-09-11 06:00 | 254 | 9 | Spring | 6 | 10.49 | -16.5 | 17.01 | 73.1 | 0 | 0 | 120 | 120 | 16.5 | 56.23 | 95 | 59.48 | 0 | 0 | 0 | Normal
2025-09-11 07:00 | 254 | 9 | Spring | 7 | 10.49 | -24.4 | 2.44 | 51 | 29.9 | 1.52 | 0 | 1.52 | 24.4 | 61.73 | 70.92 | -60.21 | 0 | 0 | 0 | Battery-supported
2025-09-11 08:00 | 254 | 9 | Spring | 8 | 10.49 | -23 | 2.54 | 41.4 | 164.9 | 8.41 | 0 | 8.41 | 23 | 65.89 | 47.92 | -57.48 | 0 | 0 | 0 | Battery-supported
2025-09-11 09:00 | 254 | 9 | Spring | 9 | 10.49 | -26.1 | 4.46 | 43.6 | 275.1 | 14.03 | 0.12 | 14.15 | 26.1 | 69.46 | 25.8 | -55.31 | 0 | 0 | 0 | Battery-supported
2025-09-11 10:00 | 254 | 9 | Spring | 10 | 10.49 | -20.3 | 9.21 | 43.2 | 366.2 | 18.68 | 26.06 | 44.74 | 20.3 | 60.36 | 19.55 | -15.62 | 0 | 0 | 0 | Battery-supported
2025-09-11 11:00 | 254 | 9 | Spring | 11 | 10.49 | -23.2 | 2.23 | 32.2 | 475.2 | 24.24 | 0 | 24.24 | 23.2 | 61.42 | 15 | -11.38 | 25.8 | 8.89 | 0 | Diesel-backup
2025-09-11 12:00 | 254 | 9 | Spring | 12 | 10.49 | -22.9 | 9.02 | 64.4 | 339.1 | 17.29 | 23.54 | 40.83 | 22.9 | 61.94 | 15 | 0 | 21.11 | 7.401 | 0 | Diesel-backup
2025-09-11 13:00 | 254 | 9 | Spring | 13 | 10.49 | -23.2 | 7.67 | 49.8 | 392.7 | 20.03 | 10.15 | 30.18 | 23.2 | 62.36 | 15 | 0 | 32.18 | 10.826 | 0 | Diesel-backup
2025-09-11 14:00 | 254 | 9 | Spring | 14 | 10.49 | -18 | 28.1 | 22.3 | 451.2 | 27.07 | 0 | 27.07 | 18 | 60.22 | 15 | 0 | 33.15 | 11.111 | 0 | Diesel-backup
2025-09-11 15:00 | 254 | 9 | Spring | 15 | 10.49 | -17.8 | 3.68 | 53.3 | 245.4 | 14.72 | 0 | 14.72 | 17.8 | 63.93 | 15 | 0 | 49.21 | 15.747 | 0 | Diesel-backup
2025-09-11 16:00 | 254 | 9 | Spring | 16 | 10.49 | -15 | 10.61 | 23.2 | 197.6 | 11.86 | 50.31 | 62.17 | 15 | 60.74 | 15.53 | 1.43 | 0 | 0 | 0 | Normal
2025-09-11 17:00 | 254 | 9 | Spring | 17 | 10.49 | -20.2 | 13.44 | 29.5 | 37.7 | 1.92 | 120 | 121.92 | 20.2 | 57.13 | 39.37 | 64.79 | 0 | 0 | 0 | Normal
2025-09-11 18:00 | 254 | 9 | Spring | 18 | 10.49 | -18 | 2.6 | 51.6 | 0 | 0 | 0 | 0 | 18 | 64.44 | 15 | -60.92 | 3.52 | 1.312 | 0 | Diesel-backup
2025-09-11 19:00 | 254 | 9 | Spring | 19 | 10.49 | -21.1 | 21.46 | 40.5 | 0 | 0 | 120 | 120 | 21.1 | 64.67 | 35.36 | 55.33 | 0 | 0 | 0 | Normal
2025-09-11 20:00 | 254 | 9 | Spring | 20 | 10.49 | -19 | 14.79 | 34.1 | 0 | 0 | 120 | 120 | 19 | 64.8 | 55.68 | 55.2 | 0 | 0 | 0 | Normal
2025-09-11 21:00 | 254 | 9 | Spring | 21 | 10.49 | -19.5 | 18.56 | 28.7 | 0 | 0 | 120 | 120 | 19.5 | 56.56 | 79.02 | 63.44 | 0 | 0 | 0 | Normal
2025-09-11 22:00 | 254 | 9 | Spring | 22 | 10.49 | -17.4 | 11.51 | 95.1 | 0 | 0 | 71.93 | 71.93 | 17.4 | 45.7 | 88.67 | 26.23 | 0 | 0 | 0 | Normal
2025-09-11 23:00 | 254 | 9 | Spring | 23 | 10.49 | -16.5 | 5.95 | 61.7 | 0 | 0 | 2.06 | 2.06 | 16.5 | 52.29 | 68.58 | -50.23 | 0 | 0 | 0 | Battery-supported
2025-09-12 | 255 | 9 | Spring | 0 | 10.65 | -16.7 | 3.39 | 87.1 | 0 | 0 | 0 | 0 | 16.7 | 57.59 | 45.55 | -57.59 | 0 | 0 | 0 | Battery-supported
2025-09-12 01:00 | 255 | 9 | Spring | 1 | 10.65 | -21.1 | 15.52 | 74.4 | 0 | 0 | 120 | 120 | 21.1 | 51.35 | 70.81 | 68.65 | 0 | 0 | 0 | Normal
2025-09-12 02:00 | 255 | 9 | Spring | 2 | 10.65 | -17.4 | 7.41 | 17.6 | 0 | 0 | 8.37 | 8.37 | 17.4 | 48.7 | 54.68 | -40.33 | 0 | 0 | 0 | Battery-supported
2025-09-12 03:00 | 255 | 9 | Spring | 3 | 10.65 | -20.1 | 1.96 | 20.5 | 0 | 0 | 0 | 0 | 20.1 | 47.14 | 35.82 | -47.14 | 0 | 0 | 0 | Battery-supported
2025-09-12 04:00 | 255 | 9 | Spring | 4 | 10.65 | -21.1 | 7.88 | 73.8 | 0 | 0 | 11.76 | 11.76 | 21.1 | 54.3 | 18.8 | -42.54 | 0 | 0 | 0 | Battery-supported
2025-09-12 05:00 | 255 | 9 | Spring | 5 | 10.65 | -22.2 | 9.6 | 38.9 | 0 | 0 | 31.77 | 31.77 | 22.2 | 51.31 | 15 | -9.51 | 10.03 | 3.658 | 0 | Diesel-backup
2025-09-12 06:00 | 255 | 9 | Spring | 6 | 10.65 | -22.1 | 20.07 | 41 | 0 | 0 | 120 | 120 | 22.1 | 53.66 | 39.41 | 66.34 | 0 | 0 | 0 | Normal
2025-09-12 07:00 | 255 | 9 | Spring | 7 | 10.65 | -17.2 | 8.31 | 31.3 | 48 | 2.88 | 15.58 | 18.46 | 17.2 | 53.19 | 25.52 | -34.73 | 0 | 0 | 0 | Battery-supported
2025-09-12 08:00 | 255 | 9 | Spring | 8 | 10.65 | -20.4 | 9.64 | 61.5 | 134.6 | 6.86 | 32.4 | 39.26 | 20.4 | 66.66 | 15 | -26.3 | 1.1 | 0.413 | 0 | Diesel-backup
2025-09-12 09:00 | 255 | 9 | Spring | 9 | 10.65 | -20.7 | 9.74 | 13.9 | 372.1 | 18.98 | 34.01 | 52.99 | 20.7 | 55.94 | 15 | 0 | 2.95 | 1.103 | 0 | Diesel-backup
2025-09-12 10:00 | 255 | 9 | Spring | 10 | 10.65 | -21.5 | 16.74 | 57.6 | 309.4 | 15.78 | 120 | 135.78 | 21.5 | 62.66 | 41.91 | 73.12 | 0 | 0 | 0 | Normal
2025-09-12 11:00 | 255 | 9 | Spring | 11 | 10.65 | -15.3 | 6.04 | 39.8 | 440.1 | 26.41 | 2.29 | 28.7 | 15.3 | 57.37 | 30.44 | -28.67 | 0 | 0 | 0 | Battery-supported
2025-09-12 12:00 | 255 | 9 | Spring | 12 | 10.65 | -17.5 | 12.37 | 64 | 341 | 20.46 | 97.67 | 118.13 | 17.5 | 59.98 | 51.84 | 58.15 | 0 | 0 | 0 | Normal
2025-09-12 13:00 | 255 | 9 | Spring | 13 | 10.65 | -21.6 | 6.99 | 63.4 | 329.3 | 16.79 | 5.95 | 22.74 | 21.6 | 67.8 | 33.82 | -45.06 | 0 | 0 | 0 | Battery-supported
2025-09-12 14:00 | 255 | 9 | Spring | 14 | 10.65 | -20.2 | 19.8 | 28.6 | 427.9 | 21.82 | 120 | 141.82 | 20.2 | 66.41 | 61.57 | 75.41 | 0 | 0 | 0 | Normal
2025-09-12 15:00 | 255 | 9 | Spring | 15 | 10.65 | -19.7 | 22.4 | 69.6 | 198.7 | 10.13 | 120 | 130.13 | 19.7 | 66.24 | 85.08 | 63.89 | 0 | 0 | 0 | Normal
2025-09-12 16:00 | 255 | 9 | Spring | 16 | 10.65 | -18.5 | 10.62 | 55 | 146.7 | 7.48 | 50.52 | 58 | 18.5 | 62.47 | 83.29 | -4.47 | 0 | 0 | 0 | Battery-supported
2025-09-12 17:00 | 255 | 9 | Spring | 17 | 10.65 | -20.1 | 11.86 | 47.9 | 40.1 | 2.05 | 81.78 | 83.83 | 20.1 | 62.1 | 91.29 | 21.73 | 0 | 0 | 0 | Normal
2025-09-12 18:00 | 255 | 9 | Spring | 18 | 10.65 | -17.3 | 8.43 | 79.7 | 0 | 0 | 16.77 | 16.77 | 17.3 | 58.26 | 74.69 | -41.49 | 0 | 0 | 0 | Battery-supported
2025-09-12 19:00 | 255 | 9 | Spring | 19 | 10.65 | -14.9 | 2.52 | 61.4 | 0 | 0 | 0 | 0 | 14.9 | 60.31 | 50.57 | -60.31 | 0 | 0 | 0 | Battery-supported
2025-09-12 20:00 | 255 | 9 | Spring | 20 | 10.65 | -21 | 9.79 | 31.9 | 0 | 0 | 34.83 | 34.83 | 21 | 60.63 | 40.25 | -25.8 | 0 | 0 | 0 | Battery-supported
2025-09-12 21:00 | 255 | 9 | Spring | 21 | 10.65 | -20.6 | 9.24 | 94 | 0 | 0 | 26.47 | 26.47 | 20.6 | 52.26 | 29.93 | -25.79 | 0 | 0 | 0 | Battery-supported
2025-09-12 22:00 | 255 | 9 | Spring | 22 | 10.65 | -19.4 | 7.76 | 72.6 | 0 | 0 | 10.82 | 10.82 | 19.4 | 56.4 | 15 | -37.33 | 8.25 | 3.03 | 0 | Diesel-backup
2025-09-12 23:00 | 255 | 9 | Spring | 23 | 10.65 | -19.5 | 8.33 | 40.9 | 0 | 0 | 15.77 | 15.77 | 19.5 | 57.49 | 15 | 0 | 41.72 | 13.526 | 0 | Diesel-backup
2025-09-13 | 256 | 9 | Spring | 0 | 10.8 | -14.3 | 12.43 | 55.1 | 0 | 0 | 99.67 | 99.67 | 14.3 | 49.31 | 33.53 | 50.36 | 0 | 0 | 0 | Normal
2025-09-13 01:00 | 256 | 9 | Spring | 1 | 10.8 | -16.8 | 11.84 | 72.9 | 0 | 0 | 81.19 | 81.19 | 16.8 | 54.34 | 43.41 | 26.85 | 0 | 0 | 0 | Normal
2025-09-13 02:00 | 256 | 9 | Spring | 2 | 10.8 | -17.3 | 8.45 | 54.4 | 0 | 0 | 16.98 | 16.98 | 17.3 | 51.23 | 29.71 | -34.25 | 0 | 0 | 0 | Battery-supported
2025-09-13 03:00 | 256 | 9 | Spring | 3 | 10.8 | -20.4 | 20.76 | 67.4 | 0 | 0 | 120 | 120 | 20.4 | 54.8 | 53.71 | 65.2 | 0 | 0 | 0 | Normal
2025-09-13 04:00 | 256 | 9 | Spring | 4 | 10.8 | -20.8 | 2.21 | 33.5 | 0 | 0 | 0 | 0 | 20.8 | 57.27 | 30.8 | -57.27 | 0 | 0 | 0 | Battery-supported
2025-09-13 05:00 | 256 | 9 | Spring | 5 | 10.8 | -23.7 | 6.22 | 75.1 | 0 | 0 | 2.82 | 2.82 | 23.7 | 55.56 | 15 | -39.5 | 13.24 | 4.776 | 0 | Diesel-backup
2025-09-13 06:00 | 256 | 9 | Spring | 6 | 10.8 | -19 | 15.46 | 51.6 | 0 | 0 | 120 | 120 | 19 | 56.87 | 38.23 | 63.13 | 0 | 0 | 0 | Normal
2025-09-13 07:00 | 256 | 9 | Spring | 7 | 10.8 | -19.8 | 2.84 | 43.5 | 51.5 | 2.63 | 0 | 2.63 | 19.8 | 53.83 | 17.75 | -51.2 | 0 | 0 | 0 | Battery-supported
2025-09-13 08:00 | 256 | 9 | Spring | 8 | 10.8 | -18.1 | 2.18 | 72.8 | 118.1 | 6.02 | 0 | 6.02 | 18.1 | 60.39 | 15 | -6.88 | 47.49 | 15.197 | 0 | Diesel-backup
2025-09-13 09:00 | 256 | 9 | Spring | 9 | 10.8 | -21.3 | 6.17 | 24.8 | 343.3 | 17.51 | 2.66 | 20.17 | 21.3 | 64.65 | 15 | 0 | 44.48 | 14.263 | 0 | Diesel-backup
2025-09-13 10:00 | 256 | 9 | Spring | 10 | 10.8 | -21 | 9.29 | 52.3 | 333.2 | 16.99 | 27.17 | 44.16 | 21 | 67.32 | 15 | 0 | 23.16 | 8.059 | 0 | Diesel-backup
2025-09-13 11:00 | 256 | 9 | Spring | 11 | 10.8 | -20.1 | 7.13 | 60.6 | 342.9 | 17.49 | 6.69 | 24.18 | 20.1 | 54.28 | 15 | 0 | 30.1 | 10.206 | 0 | Diesel-backup
2025-09-13 12:00 | 256 | 9 | Spring | 12 | 10.8 | -18.2 | 10.83 | 18.6 | 564.4 | 28.78 | 55.12 | 83.9 | 18.2 | 56.13 | 25.22 | 27.77 | 0 | 0 | 0 | Normal
2025-09-13 13:00 | 256 | 9 | Spring | 13 | 10.8 | -23 | 2.33 | 71.6 | 290.8 | 14.83 | 0 | 14.83 | 23 | 70.11 | 15 | -25.55 | 29.73 | 10.095 | 0 | Diesel-backup
2025-09-13 14:00 | 256 | 9 | Spring | 14 | 10.8 | -17.8 | 5.76 | 50.4 | 341 | 20.46 | 1.62 | 22.08 | 17.8 | 62.75 | 15 | 0 | 40.67 | 13.24 | 0 | Diesel-backup
2025-09-13 15:00 | 256 | 9 | Spring | 15 | 10.8 | -19.1 | 14.08 | 24.2 | 345.4 | 17.62 | 120 | 137.62 | 19.1 | 60.34 | 43.44 | 77.28 | 0 | 0 | 0 | Normal
2025-09-13 16:00 | 256 | 9 | Spring | 16 | 10.8 | -21 | 12.37 | 25.6 | 210.1 | 10.72 | 97.67 | 108.39 | 21 | 64.27 | 59.68 | 44.12 | 0 | 0 | 0 | Normal
2025-09-13 17:00 | 256 | 9 | Spring | 17 | 10.8 | -22.9 | 6.5 | 31.1 | 58.6 | 2.99 | 3.78 | 6.77 | 22.9 | 68.29 | 35.07 | -61.52 | 0 | 0 | 0 | Battery-supported
2025-09-13 18:00 | 256 | 9 | Spring | 18 | 10.8 | -18.4 | 10.38 | 78.8 | 0 | 0 | 45.58 | 45.58 | 18.4 | 67.61 | 26.26 | -22.03 | 0 | 0 | 0 | Battery-supported
2025-09-13 19:00 | 256 | 9 | Spring | 19 | 10.8 | -14.8 | 9.18 | 33.3 | 0 | 0 | 25.65 | 25.65 | 14.8 | 56.12 | 15 | -28.14 | 2.33 | 0.874 | 0 | Diesel-backup
2025-09-13 20:00 | 256 | 9 | Spring | 20 | 10.8 | -14.2 | 9.34 | 55.6 | 0 | 0 | 27.88 | 27.88 | 14.2 | 62.47 | 15 | 0 | 34.59 | 11.53 | 0 | Diesel-backup
2025-09-13 21:00 | 256 | 9 | Spring | 21 | 10.8 | -17.2 | 11.35 | 63.9 | 0 | 0 | 67.7 | 67.7 | 17.2 | 54.47 | 19.87 | 13.23 | 0 | 0 | 0 | Normal
2025-09-13 22:00 | 256 | 9 | Spring | 22 | 10.8 | -13.8 | 23.1 | 29.1 | 0 | 0 | 120 | 120 | 13.8 | 45.11 | 47.43 | 74.89 | 0 | 0 | 0 | Normal
2025-09-13 23:00 | 256 | 9 | Spring | 23 | 10.8 | -18.4 | 23.39 | 60.6 | 0 | 0 | 120 | 120 | 18.4 | 50.97 | 72.83 | 69.03 | 0 | 0 | 0 | Normal
2025-09-14 | 257 | 9 | Spring | 0 | 10.96 | -16.4 | 2.88 | 47.7 | 0 | 0 | 0 | 0 | 16.4 | 56.24 | 50.34 | -56.24 | 0 | 0 | 0 | Battery-supported
2025-09-14 01:00 | 257 | 9 | Spring | 1 | 10.96 | -19.8 | 8.13 | 84.4 | 0 | 0 | 13.89 | 13.89 | 19.8 | 60.46 | 31.71 | -46.57 | 0 | 0 | 0 | Battery-supported
2025-09-14 02:00 | 257 | 9 | Spring | 2 | 10.96 | -20.4 | 4.27 | 57.3 | 0 | 0 | 0.06 | 0.06 | 20.4 | 55.2 | 15 | -41.77 | 13.37 | 4.82 | 0 | Diesel-backup
2025-09-14 03:00 | 257 | 9 | Spring | 3 | 10.96 | -21.1 | 11.89 | 52.4 | 0 | 0 | 82.66 | 82.66 | 21.1 | 60.5 | 23.15 | 22.16 | 0 | 0 | 0 | Normal
2025-09-14 04:00 | 257 | 9 | Spring | 4 | 10.96 | -24.5 | 8.42 | 49.5 | 0 | 0 | 16.67 | 16.67 | 24.5 | 60.92 | 15 | -20.39 | 23.86 | 8.282 | 0 | Diesel-backup
2025-09-14 05:00 | 257 | 9 | Spring | 5 | 10.96 | -17.5 | 17.02 | 75 | 0 | 0 | 120 | 120 | 17.5 | 52.23 | 39.94 | 67.77 | 0 | 0 | 0 | Normal
2025-09-14 06:00 | 257 | 9 | Spring | 6 | 10.96 | -21.9 | 9.56 | 10.3 | 0 | 0 | 31.15 | 31.15 | 21.9 | 57.66 | 29.34 | -26.51 | 0 | 0 | 0 | Battery-supported
2025-09-14 07:00 | 257 | 9 | Spring | 7 | 10.96 | -22.4 | 21.22 | 45.3 | 59.3 | 3.02 | 120 | 123.02 | 22.4 | 51.82 | 55.54 | 71.2 | 0 | 0 | 0 | Normal
2025-09-14 08:00 | 257 | 9 | Spring | 8 | 10.96 | -23.3 | 23.85 | 86.1 | 95.6 | 4.88 | 120 | 124.88 | 23.3 | 65.22 | 77.49 | 59.66 | 0 | 0 | 0 | Normal
2025-09-14 09:00 | 257 | 9 | Spring | 9 | 10.96 | -21.1 | 20.77 | 39.8 | 300.3 | 15.32 | 120 | 135.32 | 21.1 | 62 | 95 | 47.58 | 0 | 0 | 0 | Normal
2025-09-14 10:00 | 257 | 9 | Spring | 10 | 10.96 | -16.7 | 1.72 | 60.5 | 300.8 | 18.05 | 0 | 18.05 | 16.7 | 63.71 | 76.74 | -45.66 | 0 | 0 | 0 | Battery-supported
2025-09-14 11:00 | 257 | 9 | Spring | 11 | 10.96 | -15.7 | 11.24 | 83.2 | 236.7 | 14.2 | 64.9 | 79.1 | 15.7 | 59.7 | 83.88 | 19.4 | 0 | 0 | 0 | Normal
2025-09-14 12:00 | 257 | 9 | Spring | 12 | 10.96 | -23.6 | 7.67 | 100 | 164 | 8.36 | 10.15 | 18.51 | 23.6 | 65.65 | 65.02 | -47.14 | 0 | 0 | 0 | Battery-supported
2025-09-14 13:00 | 257 | 9 | Spring | 13 | 10.96 | -20.4 | 8.43 | 8.9 | 587.1 | 29.94 | 16.77 | 46.71 | 20.4 | 67.85 | 56.56 | -21.14 | 0 | 0 | 0 | Battery-supported
2025-09-14 14:00 | 257 | 9 | Spring | 14 | 10.96 | -21.5 | 15.42 | 41.1 | 381 | 19.43 | 120 | 139.43 | 21.5 | 58.45 | 86.36 | 80.98 | 0 | 0 | 0 | Normal
2025-09-14 15:00 | 257 | 9 | Spring | 15 | 10.96 | -16.7 | 8.01 | 15.4 | 378.4 | 22.7 | 12.84 | 35.54 | 16.7 | 55.89 | 78.22 | -20.35 | 0 | 0 | 0 | Battery-supported
2025-09-14 16:00 | 257 | 9 | Spring | 16 | 10.96 | -17.9 | 9.92 | 24 | 221.3 | 13.28 | 37.04 | 50.32 | 17.9 | 65.96 | 71.97 | -15.64 | 0 | 0 | 0 | Battery-supported
2025-09-14 17:00 | 257 | 9 | Spring | 17 | 10.96 | -19.6 | 10.26 | 46 | 58.8 | 3 | 43.24 | 46.24 | 19.6 | 65.17 | 64.4 | -18.93 | 0 | 0 | 0 | Battery-supported
2025-09-14 18:00 | 257 | 9 | Spring | 18 | 10.96 | -17.8 | 2.21 | 28 | 0 | 0 | 0 | 0 | 17.8 | 54.46 | 42.61 | -54.46 | 0 | 0 | 0 | Battery-supported
2025-09-14 19:00 | 257 | 9 | Spring | 19 | 10.96 | -18.8 | 7.27 | 62.3 | 0 | 0 | 7.5 | 7.5 | 18.8 | 62.67 | 20.54 | -55.17 | 0 | 0 | 0 | Battery-supported
2025-09-14 20:00 | 257 | 9 | Spring | 20 | 10.96 | -14.2 | 17.71 | 77.8 | 0 | 0 | 120 | 120 | 14.2 | 52.13 | 45.52 | 67.87 | 0 | 0 | 0 | Normal
2025-09-14 21:00 | 257 | 9 | Spring | 21 | 10.96 | -16.6 | 1.93 | 56.3 | 0 | 0 | 0 | 0 | 16.6 | 49.9 | 25.56 | -49.9 | 0 | 0 | 0 | Battery-supported
2025-09-14 22:00 | 257 | 9 | Spring | 22 | 10.96 | -16.5 | 13.21 | 46.6 | 0 | 0 | 120 | 120 | 16.5 | 53.33 | 50.09 | 66.67 | 0 | 0 | 0 | Normal
2025-09-14 23:00 | 257 | 9 | Spring | 23 | 10.96 | -24 | 5.35 | 64.4 | 0 | 0 | 0.89 | 0.89 | 24 | 58.86 | 26.91 | -57.97 | 0 | 0 | 0 | Battery-supported
2025-09-15 | 258 | 9 | Spring | 0 | 11.11 | -18.5 | 7.54 | 62.8 | 0 | 0 | 9.23 | 9.23 | 18.5 | 53.22 | 15 | -29.77 | 14.22 | 5.112 | 0 | Diesel-backup
2025-09-15 01:00 | 258 | 9 | Spring | 1 | 11.11 | -14.1 | 14.68 | 62.5 | 0 | 0 | 120 | 120 | 14.1 | 45.81 | 42.3 | 74.19 | 0 | 0 | 0 | Normal
2025-09-15 02:00 | 258 | 9 | Spring | 2 | 11.11 | -16.1 | 4.5 | 45.4 | 0 | 0 | 0.14 | 0.14 | 16.1 | 55.72 | 20.07 | -55.58 | 0 | 0 | 0 | Battery-supported
2025-09-15 03:00 | 258 | 9 | Spring | 3 | 11.11 | -23.5 | 7.96 | 57.1 | 0 | 0 | 12.42 | 12.42 | 23.5 | 60.49 | 15 | -12.67 | 35.4 | 11.762 | 0 | Diesel-backup
2025-09-15 04:00 | 258 | 9 | Spring | 4 | 11.11 | -20.5 | 2.88 | 59.9 | 0 | 0 | 0 | 0 | 20.5 | 52.28 | 15 | 0 | 52.28 | 16.73 | 0 | Diesel-backup
2025-09-15 05:00 | 258 | 9 | Spring | 5 | 11.11 | -22.8 | 12.14 | 54.5 | 0 | 0 | 90.27 | 90.27 | 22.8 | 58.29 | 26.77 | 31.98 | 0 | 0 | 0 | Normal
2025-09-15 06:00 | 258 | 9 | Spring | 6 | 11.11 | -16.6 | 5.76 | 37.2 | 0 | 0 | 1.62 | 1.62 | 16.6 | 50.36 | 15 | -29.42 | 19.32 | 6.817 | 0 | Diesel-backup
2025-09-15 07:00 | 258 | 9 | Spring | 7 | 11.11 | -20 | 3.48 | 51.4 | 63.1 | 3.22 | 0 | 3.22 | 20 | 52.81 | 15 | 0 | 49.59 | 15.869 | 0 | Diesel-backup
2025-09-15 08:00 | 258 | 9 | Spring | 8 | 11.11 | -22.2 | 9.54 | 91.1 | 88.6 | 4.52 | 30.84 | 35.36 | 22.2 | 65.78 | 15 | 0 | 30.42 | 10.302 | 0 | Diesel-backup
2025-09-15 09:00 | 258 | 9 | Spring | 9 | 11.11 | -20.4 | 2.78 | 52.7 | 262.4 | 13.38 | 0 | 13.38 | 20.4 | 70.09 | 15 | 0 | 56.71 | 18.147 | 0 | Diesel-backup
2025-09-15 10:00 | 258 | 9 | Spring | 10 | 11.11 | -26.1 | 7.4 | 57.3 | 315.9 | 16.11 | 8.3 | 24.41 | 26.1 | 65.63 | 15 | 0 | 41.22 | 13.39 | 0 | Diesel-backup
2025-09-15 11:00 | 258 | 9 | Spring | 11 | 11.11 | -22.5 | 5.42 | 30.7 | 484.8 | 24.72 | 0.99 | 25.71 | 22.5 | 67.75 | 15 | 0 | 42.04 | 13.612 | 0 | Diesel-backup
2025-09-15 12:00 | 258 | 9 | Spring | 12 | 11.11 | -19.7 | 10.82 | 30.1 | 508 | 25.91 | 54.9 | 80.81 | 19.7 | 66.12 | 20.41 | 14.69 | 0 | 0 | 0 | Normal
2025-09-15 13:00 | 258 | 9 | Spring | 13 | 11.11 | -17.6 | 10.96 | 55.2 | 369.3 | 22.16 | 58.11 | 80.27 | 17.6 | 62.55 | 26.93 | 17.72 | 0 | 0 | 0 | Normal
2025-09-15 14:00 | 258 | 9 | Spring | 14 | 11.11 | -23.3 | 6.07 | 32 | 421.1 | 21.48 | 2.38 | 23.86 | 23.3 | 69.95 | 15 | -29.82 | 16.27 | 5.806 | 0 | Diesel-backup
2025-09-15 15:00 | 258 | 9 | Spring | 15 | 11.11 | -19.5 | 20.87 | 39.4 | 305.8 | 15.6 | 120 | 135.6 | 19.5 | 62.23 | 42 | 73.37 | 0 | 0 | 0 | Normal
2025-09-15 16:00 | 258 | 9 | Spring | 16 | 11.11 | -16.1 | 17.16 | 11.2 | 255.9 | 15.35 | 120 | 135.35 | 16.1 | 61.07 | 69.34 | 74.28 | 0 | 0 | 0 | Normal
2025-09-15 17:00 | 258 | 9 | Spring | 17 | 11.11 | -21.2 | 4.9 | 75.3 | 44.7 | 2.28 | 0.38 | 2.66 | 21.2 | 64.69 | 44.52 | -62.03 | 0 | 0 | 0 | Battery-supported
2025-09-15 18:00 | 258 | 9 | Spring | 18 | 11.11 | -17.3 | 31.1 | 46 | 0 | 0 | 0 | 0 | 17.3 | 55.17 | 22.46 | -55.17 | 0 | 0 | 0 | Battery-supported
2025-09-15 19:00 | 258 | 9 | Spring | 19 | 11.11 | -17.5 | 14.28 | 57.1 | 0 | 0 | 120 | 120 | 17.5 | 56.34 | 45.88 | 63.66 | 0 | 0 | 0 | Normal
2025-09-15 20:00 | 258 | 9 | Spring | 20 | 11.11 | -13.8 | 11.53 | 17.2 | 0 | 0 | 72.47 | 72.47 | 13.8 | 61.02 | 50.1 | 11.45 | 0 | 0 | 0 | Normal
2025-09-15 21:00 | 258 | 9 | Spring | 21 | 11.11 | -18.1 | 11.99 | 37.6 | 0 | 0 | 85.65 | 85.65 | 18.1 | 51.26 | 62.75 | 34.39 | 0 | 0 | 0 | Normal
2025-09-15 22:00 | 258 | 9 | Spring | 22 | 11.11 | -18.1 | 4.02 | 32.1 | 0 | 0 | 0.02 | 0.02 | 18.1 | 51.8 | 42.04 | -51.78 | 0 | 0 | 0 | Battery-supported
2025-09-15 23:00 | 258 | 9 | Spring | 23 | 11.11 | -16.1 | 18.76 | 45.9 | 0 | 0 | 120 | 120 | 16.1 | 54.16 | 66.27 | 65.84 | 0 | 0 | 0 | Normal
2025-09-16 | 259 | 9 | Spring | 0 | 11.27 | -21 | 2.21 | 49.9 | 0 | 0 | 0 | 0 | 21 | 55.51 | 44.06 | -55.51 | 0 | 0 | 0 | Battery-supported
2025-09-16 01:00 | 259 | 9 | Spring | 1 | 11.27 | -19 | 11.91 | 34.2 | 0 | 0 | 83.25 | 83.25 | 19 | 56.84 | 53.78 | 26.41 | 0 | 0 | 0 | Normal
2025-09-16 02:00 | 259 | 9 | Spring | 2 | 11.27 | -19.9 | 17.24 | 27.5 | 0 | 0 | 120 | 120 | 19.9 | 54.47 | 77.9 | 65.53 | 0 | 0 | 0 | Normal
2025-09-16 03:00 | 259 | 9 | Spring | 3 | 11.27 | -19.6 | 5.16 | 73.4 | 0 | 0 | 0.64 | 0.64 | 19.6 | 50.48 | 57.96 | -49.84 | 0 | 0 | 0 | Battery-supported
2025-09-16 04:00 | 259 | 9 | Spring | 4 | 11.27 | -17.8 | 14.83 | 23.9 | 0 | 0 | 120 | 120 | 17.8 | 56.87 | 81.19 | 63.13 | 0 | 0 | 0 | Normal
2025-09-16 05:00 | 259 | 9 | Spring | 5 | 11.27 | -18.7 | 10.07 | 52.9 | 0 | 0 | 39.69 | 39.69 | 18.7 | 50.41 | 76.91 | -10.72 | 0 | 0 | 0 | Battery-supported
2025-09-16 06:00 | 259 | 9 | Spring | 6 | 11.27 | -21.8 | 15.38 | 41.8 | 0 | 0 | 120 | 120 | 21.8 | 61.85 | 95 | 49.17 | 0 | 0 | 0 | Normal
2025-09-16 07:00 | 259 | 9 | Spring | 7 | 11.27 | -20 | 16.79 | 59.8 | 63.6 | 3.24 | 120 | 123.24 | 20 | 57.29 | 95 | 0 | 0 | 0 | 0 | Normal
2025-09-16 08:00 | 259 | 9 | Spring | 8 | 11.27 | -17.1 | 21.88 | 27.3 | 229.5 | 13.77 | 120 | 133.77 | 17.1 | 58.01 | 95 | 0 | 0 | 0 | 0 | Normal
2025-09-16 09:00 | 259 | 9 | Spring | 9 | 11.27 | -22.2 | 19.19 | 100 | 109.9 | 5.6 | 120 | 125.6 | 22.2 | 67.58 | 95 | 0 | 0 | 0 | 0 | Normal
2025-09-16 10:00 | 259 | 9 | Spring | 10 | 11.27 | -19.9 | 2.47 | 25 | 452.2 | 23.06 | 0 | 23.06 | 19.9 | 61.04 | 79.81 | -37.98 | 0 | 0 | 0 | Battery-supported
2025-09-16 11:00 | 259 | 9 | Spring | 11 | 11.27 | -20.4 | 4.97 | 41.9 | 432.5 | 22.06 | 0.44 | 22.5 | 20.4 | 60.34 | 64.67 | -37.84 | 0 | 0 | 0 | Battery-supported
2025-09-16 12:00 | 259 | 9 | Spring | 12 | 11.27 | -19.8 | 12.66 | 81.3 | 256.2 | 13.07 | 107.57 | 120.64 | 19.8 | 63.65 | 85.64 | 56.99 | 0 | 0 | 0 | Normal
2025-09-16 13:00 | 259 | 9 | Spring | 13 | 11.27 | -22.9 | 16.92 | 62.9 | 333.2 | 16.99 | 120 | 136.99 | 22.9 | 69.01 | 95 | 25.42 | 0 | 0 | 0 | Normal
2025-09-16 14:00 | 259 | 9 | Spring | 14 | 11.27 | -15.8 | 4.5 | 61.4 | 300.3 | 18.02 | 0.14 | 18.16 | 15.8 | 59.91 | 78.3 | -41.75 | 0 | 0 | 0 | Battery-supported
2025-09-16 15:00 | 259 | 9 | Spring | 15 | 11.27 | -20.2 | 14.08 | 5.8 | 420.4 | 21.44 | 120 | 141.44 | 20.2 | 60.25 | 95 | 45.38 | 0 | 0 | 0 | Normal
2025-09-16 16:00 | 259 | 9 | Spring | 16 | 11.27 | -15.9 | 19.98 | 56.8 | 165.6 | 9.94 | 120 | 129.94 | 15.9 | 53.51 | 95 | 0 | 0 | 0 | 0 | Normal
2025-09-16 17:00 | 259 | 9 | Spring | 17 | 11.27 | -19.2 | 16.55 | 67.3 | 57.1 | 2.91 | 120 | 122.91 | 19.2 | 61.5 | 95 | 0 | 0 | 0 | 0 | Normal
2025-09-16 18:00 | 259 | 9 | Spring | 18 | 11.27 | -19 | 13.95 | 61 | 0 | 0 | 120 | 120 | 19 | 57.62 | 95 | 0 | 0 | 0 | 0 | Normal
2025-09-16 19:00 | 259 | 9 | Spring | 19 | 11.27 | -14.8 | 9.11 | 61.4 | 0 | 0 | 24.71 | 24.71 | 14.8 | 57.4 | 81.92 | -32.69 | 0 | 0 | 0 | Battery-supported
2025-09-16 20:00 | 259 | 9 | Spring | 20 | 11.27 | -15.2 | 8.83 | 41.1 | 0 | 0 | 21.19 | 21.19 | 15.2 | 58.06 | 67.18 | -36.87 | 0 | 0 | 0 | Battery-supported
2025-09-16 21:00 | 259 | 9 | Spring | 21 | 11.27 | -17 | 28.17 | 28.2 | 0 | 0 | 0 | 0 | 17 | 54.85 | 45.24 | -54.85 | 0 | 0 | 0 | Battery-supported
2025-09-16 22:00 | 259 | 9 | Spring | 22 | 11.27 | -15.9 | 0.4 | 52.9 | 0 | 0 | 0 | 0 | 15.9 | 53.48 | 23.84 | -53.48 | 0 | 0 | 0 | Battery-supported
2025-09-16 23:00 | 259 | 9 | Spring | 23 | 11.27 | -18.5 | 6.82 | 77 | 0 | 0 | 5.12 | 5.12 | 18.5 | 57.43 | 15 | -22.11 | 30.2 | 10.236 | 0 | Diesel-backup
2025-09-17 | 260 | 9 | Spring | 0 | 11.42 | -18 | 4.95 | 35.2 | 0 | 0 | 0.43 | 0.43 | 18 | 52.93 | 15 | 0 | 52.5 | 16.8 | 0 | Diesel-backup
2025-09-17 01:00 | 260 | 9 | Spring | 1 | 11.42 | -19.8 | 3.44 | 42.3 | 0 | 0 | 0 | 0 | 19.8 | 53.19 | 15 | 0 | 53.19 | 17.021 | 0 | Diesel-backup
2025-09-17 02:00 | 260 | 9 | Spring | 2 | 11.42 | -16.7 | 13.41 | 52.6 | 0 | 0 | 120 | 120 | 16.7 | 53.46 | 39.49 | 66.54 | 0 | 0 | 0 | Normal
2025-09-17 03:00 | 260 | 9 | Spring | 3 | 11.42 | -20.6 | 12.34 | 61 | 0 | 0 | 96.69 | 96.69 | 20.6 | 57.29 | 53.99 | 39.4 | 0 | 0 | 0 | Normal
2025-09-17 04:00 | 260 | 9 | Spring | 4 | 11.42 | -16.2 | 9.6 | 66.6 | 0 | 0 | 31.77 | 31.77 | 16.2 | 52.72 | 45.61 | -20.95 | 0 | 0 | 0 | Battery-supported
2025-09-17 05:00 | 260 | 9 | Spring | 5 | 11.42 | -20.5 | 12.34 | 46.2 | 0 | 0 | 96.69 | 96.69 | 20.5 | 63.14 | 57.95 | 33.55 | 0 | 0 | 0 | Normal
2025-09-17 06:00 | 260 | 9 | Spring | 6 | 11.42 | -20 | 15.32 | 56.9 | 0 | 0 | 120 | 120 | 20 | 57.66 | 80.89 | 62.34 | 0 | 0 | 0 | Normal
2025-09-17 07:00 | 260 | 9 | Spring | 7 | 11.42 | -18.5 | 8.28 | 36.3 | 92.8 | 4.73 | 15.29 | 20.02 | 18.5 | 58.23 | 65.61 | -38.21 | 0 | 0 | 0 | Battery-supported
2025-09-17 08:00 | 260 | 9 | Spring | 8 | 11.42 | -20.1 | 12.86 | 78.9 | 121.3 | 6.19 | 114.77 | 120.96 | 20.1 | 58.76 | 88.5 | 62.2 | 0 | 0 | 0 | Normal
2025-09-17 09:00 | 260 | 9 | Spring | 9 | 11.42 | -20.8 | 7.81 | 45.6 | 292.9 | 14.94 | 11.21 | 26.15 | 20.8 | 59.9 | 75 | -33.75 | 0 | 0 | 0 | Battery-supported
2025-09-17 10:00 | 260 | 9 | Spring | 10 | 11.42 | -20.1 | 13.12 | 49 | 353.9 | 18.05 | 120 | 138.05 | 20.1 | 60 | 95 | 54.35 | 0 | 0 | 0 | Normal
2025-09-17 11:00 | 260 | 9 | Spring | 11 | 11.42 | -17.8 | 19.99 | 52.6 | 382.3 | 22.94 | 120 | 142.94 | 17.8 | 60.86 | 95 | 0 | 0 | 0 | 0 | Normal
2025-09-17 12:00 | 260 | 9 | Spring | 12 | 11.42 | -20.9 | 16.22 | 23.6 | 540.1 | 27.55 | 120 | 147.55 | 20.9 | 63.33 | 95 | 0 | 0 | 0 | 0 | Normal
2025-09-17 13:00 | 260 | 9 | Spring | 13 | 11.42 | -19.4 | 24.02 | 96.3 | 175.3 | 8.94 | 120 | 128.94 | 19.4 | 63.45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-09-17 14:00 | 260 | 9 | Spring | 14 | 11.42 | -18.7 | 6.82 | 41.1 | 386.9 | 19.73 | 5.12 | 24.85 | 18.7 | 68.31 | 77.62 | -43.46 | 0 | 0 | 0 | Battery-supported
2025-09-17 15:00 | 260 | 9 | Spring | 15 | 11.42 | -16.4 | 5.83 | 53.2 | 267.6 | 16.06 | 1.77 | 17.83 | 16.4 | 59.04 | 61.13 | -41.21 | 0 | 0 | 0 | Battery-supported
2025-09-17 16:00 | 260 | 9 | Spring | 16 | 11.42 | -18.2 | 12.18 | 49.1 | 187.8 | 9.58 | 91.53 | 101.11 | 18.2 | 63.14 | 75.1 | 37.97 | 0 | 0 | 0 | Normal
2025-09-17 17:00 | 260 | 9 | Spring | 17 | 11.42 | -13.7 | 6.96 | 59.5 | 70.6 | 4.24 | 5.8 | 10.04 | 13.7 | 57.01 | 56.32 | -46.97 | 0 | 0 | 0 | Battery-supported
2025-09-17 18:00 | 260 | 9 | Spring | 18 | 11.42 | -17.7 | 13.45 | 53.2 | 0 | 0 | 120 | 120 | 17.7 | 65.03 | 76.55 | 54.97 | 0 | 0 | 0 | Normal
2025-09-17 19:00 | 260 | 9 | Spring | 19 | 11.42 | -17.8 | 10.75 | 74.1 | 0 | 0 | 53.34 | 53.34 | 17.8 | 63.35 | 72.54 | -10.01 | 0 | 0 | 0 | Battery-supported
2025-09-17 20:00 | 260 | 9 | Spring | 20 | 11.42 | -17.6 | 5.01 | 68.7 | 0 | 0 | 0.48 | 0.48 | 17.6 | 60.4 | 48.57 | -59.92 | 0 | 0 | 0 | Battery-supported
2025-09-17 21:00 | 260 | 9 | Spring | 21 | 11.42 | -20.1 | 12.51 | 33.8 | 0 | 0 | 102.37 | 102.37 | 20.1 | 58.95 | 64.55 | 43.42 | 0 | 0 | 0 | Normal
2025-09-17 22:00 | 260 | 9 | Spring | 22 | 11.42 | -19.7 | 5.25 | 48.5 | 0 | 0 | 0.75 | 0.75 | 19.7 | 57.14 | 42 | -56.39 | 0 | 0 | 0 | Battery-supported
2025-09-17 23:00 | 260 | 9 | Spring | 23 | 11.42 | -18.8 | 20.82 | 89.5 | 0 | 0 | 120 | 120 | 18.8 | 57.26 | 65.08 | 62.74 | 0 | 0 | 0 | Normal
2025-09-18 | 261 | 9 | Spring | 0 | 11.58 | -15.3 | 8.37 | 87.3 | 0 | 0 | 16.17 | 16.17 | 15.3 | 50.48 | 51.36 | -34.31 | 0 | 0 | 0 | Battery-supported
2025-09-18 01:00 | 261 | 9 | Spring | 1 | 11.58 | -18.2 | 5.78 | 66.9 | 0 | 0 | 1.66 | 1.66 | 18.2 | 55.86 | 29.68 | -54.2 | 0 | 0 | 0 | Battery-supported
2025-09-18 02:00 | 261 | 9 | Spring | 2 | 11.58 | -19.6 | 10.92 | 27.5 | 0 | 0 | 57.18 | 57.18 | 19.6 | 53.69 | 30.97 | 3.49 | 0 | 0 | 0 | Normal
2025-09-18 03:00 | 261 | 9 | Spring | 3 | 11.58 | -16.2 | 11.64 | 48.6 | 0 | 0 | 75.49 | 75.49 | 16.2 | 47.13 | 41.4 | 28.36 | 0 | 0 | 0 | Normal
2025-09-18 04:00 | 261 | 9 | Spring | 4 | 11.58 | -15.9 | 6.65 | 11.1 | 0 | 0 | 4.37 | 4.37 | 15.9 | 49.07 | 23.52 | -44.7 | 0 | 0 | 0 | Battery-supported
2025-09-18 05:00 | 261 | 9 | Spring | 5 | 11.58 | -16.8 | 6.45 | 51.8 | 0 | 0 | 3.59 | 3.59 | 16.8 | 54.25 | 15 | -21.3 | 29.36 | 9.982 | 0 | Diesel-backup
2025-09-18 06:00 | 261 | 9 | Spring | 6 | 11.58 | -21.7 | 2.73 | 33.4 | 0 | 0 | 0 | 0 | 21.7 | 58.84 | 15 | 0 | 58.84 | 18.829 | 0 | Diesel-backup
2025-09-18 07:00 | 261 | 9 | Spring | 7 | 11.58 | -21.1 | 15.68 | 60.9 | 75.7 | 3.86 | 120 | 123.86 | 21.1 | 53.35 | 40.95 | 70.51 | 0 | 0 | 0 | Normal
2025-09-18 08:00 | 261 | 9 | Spring | 8 | 11.58 | -16 | 20.42 | 44.7 | 203.4 | 12.2 | 120 | 132.2 | 16 | 64.5 | 65.86 | 67.7 | 0 | 0 | 0 | Normal
2025-09-18 09:00 | 261 | 9 | Spring | 9 | 11.58 | -19.4 | 17.09 | 14.4 | 401.6 | 20.48 | 120 | 140.48 | 19.4 | 58.43 | 95 | 79.18 | 0 | 0 | 0 | Normal
2025-09-18 10:00 | 261 | 9 | Spring | 10 | 11.58 | -20.4 | 5.66 | 31.7 | 428.2 | 21.84 | 1.41 | 23.25 | 20.4 | 64.06 | 78.68 | -40.81 | 0 | 0 | 0 | Battery-supported
2025-09-18 11:00 | 261 | 9 | Spring | 11 | 11.58 | -18 | 12.28 | 38.1 | 451.4 | 27.08 | 94.73 | 121.81 | 18 | 59.35 | 95 | 44.36 | 0 | 0 | 0 | Normal
2025-09-18 12:00 | 261 | 9 | Spring | 12 | 11.58 | -17.1 | 11.02 | 45.1 | 433.8 | 26.03 | 59.52 | 85.55 | 17.1 | 60.88 | 95 | 0 | 0 | 0 | 0 | Normal
2025-09-18 13:00 | 261 | 9 | Spring | 13 | 11.58 | -20.2 | 3.32 | 33.4 | 473.7 | 24.16 | 0 | 24.16 | 20.2 | 58.19 | 81.39 | -34.03 | 0 | 0 | 0 | Battery-supported
2025-09-18 14:00 | 261 | 9 | Spring | 14 | 11.58 | -18 | 6.62 | 43.9 | 376.6 | 22.6 | 4.25 | 26.85 | 18 | 54.33 | 70.4 | -27.48 | 0 | 0 | 0 | Battery-supported
2025-09-18 15:00 | 261 | 9 | Spring | 15 | 11.58 | -16.1 | 11.77 | 58 | 254.6 | 15.28 | 79.16 | 94.44 | 16.1 | 56.66 | 84.3 | 37.78 | 0 | 0 | 0 | Normal
2025-09-18 16:00 | 261 | 9 | Spring | 16 | 11.58 | -20.3 | 1.91 | 34.9 | 225.8 | 11.52 | 0 | 11.52 | 20.3 | 66.02 | 62.5 | -54.5 | 0 | 0 | 0 | Battery-supported
2025-09-18 17:00 | 261 | 9 | Spring | 17 | 11.58 | -17.4 | 4.44 | 64.6 | 71.7 | 4.3 | 0.12 | 4.42 | 17.4 | 61.15 | 39.81 | -56.73 | 0 | 0 | 0 | Battery-supported
2025-09-18 18:00 | 261 | 9 | Spring | 18 | 11.58 | -19.7 | 14.62 | 28.6 | 0 | 0 | 120 | 120 | 19.7 | 57.28 | 62.89 | 62.72 | 0 | 0 | 0 | Normal
2025-09-18 19:00 | 261 | 9 | Spring | 19 | 11.58 | -19.2 | 5.53 | 11.2 | 0 | 0 | 1.17 | 1.17 | 19.2 | 66.07 | 36.93 | -64.9 | 0 | 0 | 0 | Battery-supported
2025-09-18 20:00 | 261 | 9 | Spring | 20 | 11.58 | -18.3 | 3.35 | 86.7 | 0 | 0 | 0 | 0 | 18.3 | 62.18 | 15 | -54.82 | 7.36 | 2.71 | 0 | Diesel-backup
2025-09-18 21:00 | 261 | 9 | Spring | 21 | 11.58 | -16 | 16.58 | 53.1 | 0 | 0 | 120 | 120 | 16 | 54.01 | 39.28 | 65.99 | 0 | 0 | 0 | Normal
2025-09-18 22:00 | 261 | 9 | Spring | 22 | 11.58 | -17.9 | 5.53 | 23.2 | 0 | 0 | 1.17 | 1.17 | 17.9 | 51.55 | 19.13 | -50.38 | 0 | 0 | 0 | Battery-supported
2025-09-18 23:00 | 261 | 9 | Spring | 23 | 11.58 | -18.9 | 14.69 | 71.9 | 0 | 0 | 120 | 120 | 18.9 | 46.73 | 46.1 | 73.27 | 0 | 0 | 0 | Normal
2025-09-19 | 262 | 9 | Spring | 0 | 11.73 | -17.5 | 23.57 | 77.6 | 0 | 0 | 120 | 120 | 17.5 | 58.45 | 68.75 | 61.55 | 0 | 0 | 0 | Normal
2025-09-19 01:00 | 262 | 9 | Spring | 1 | 11.73 | -20.5 | 4.33 | 31.4 | 0 | 0 | 0.08 | 0.08 | 20.5 | 54.81 | 46.85 | -54.73 | 0 | 0 | 0 | Battery-supported
2025-09-19 02:00 | 262 | 9 | Spring | 2 | 11.73 | -17.4 | 8.54 | 36.2 | 0 | 0 | 17.92 | 17.92 | 17.4 | 56.35 | 31.48 | -38.43 | 0 | 0 | 0 | Battery-supported
2025-09-19 03:00 | 262 | 9 | Spring | 3 | 11.73 | -16.2 | 11.05 | 5.6 | 0 | 0 | 60.24 | 60.24 | 16.2 | 49.66 | 35.38 | 10.58 | 0 | 0 | 0 | Normal
2025-09-19 04:00 | 262 | 9 | Spring | 4 | 11.73 | -19.3 | 16.36 | 51.9 | 0 | 0 | 120 | 120 | 19.3 | 54.67 | 59.42 | 65.33 | 0 | 0 | 0 | Normal
2025-09-19 05:00 | 262 | 9 | Spring | 5 | 11.73 | -19.8 | 6.58 | 37.3 | 0 | 0 | 4.09 | 4.09 | 19.8 | 48.29 | 41.74 | -44.2 | 0 | 0 | 0 | Battery-supported
2025-09-19 06:00 | 262 | 9 | Spring | 6 | 11.73 | -18.8 | 1.09 | 47.1 | 0 | 0 | 0 | 0 | 18.8 | 50.49 | 21.54 | -50.49 | 0 | 0 | 0 | Battery-supported
2025-09-19 07:00 | 262 | 9 | Spring | 7 | 11.73 | -24.2 | 4.33 | 34 | 112.2 | 5.72 | 0.08 | 5.8 | 24.2 | 65.13 | 15 | -16.35 | 42.98 | 13.864 | 0 | Diesel-backup
2025-09-19 08:00 | 262 | 9 | Spring | 8 | 11.73 | -18.7 | 7.46 | 67.7 | 154.7 | 7.89 | 8.69 | 16.58 | 18.7 | 65.19 | 15 | 0 | 48.61 | 15.555 | 0 | Diesel-backup
2025-09-19 09:00 | 262 | 9 | Spring | 9 | 11.73 | -13 | 14.63 | 48 | 291.5 | 17.49 | 120 | 137.49 | 13 | 60.74 | 43.24 | 76.75 | 0 | 0 | 0 | Normal
2025-09-19 10:00 | 262 | 9 | Spring | 10 | 11.73 | -19.9 | 8.59 | 50.7 | 349.7 | 17.83 | 18.46 | 36.29 | 19.9 | 64.85 | 31.82 | -28.56 | 0 | 0 | 0 | Battery-supported
2025-09-19 11:00 | 262 | 9 | Spring | 11 | 11.73 | -19.7 | 14.07 | 35.4 | 464.6 | 23.69 | 120 | 143.69 | 19.7 | 63.7 | 61.26 | 79.99 | 0 | 0 | 0 | Normal
2025-09-19 12:00 | 262 | 9 | Spring | 12 | 11.73 | -17.4 | 7.29 | 87.4 | 226.2 | 13.57 | 7.62 | 21.19 | 17.4 | 64.22 | 44.04 | -43.03 | 0 | 0 | 0 | Battery-supported
2025-09-19 13:00 | 262 | 9 | Spring | 13 | 11.73 | -15.1 | 10.43 | 37.6 | 454.1 | 27.25 | 46.58 | 73.83 | 15.1 | 61.76 | 48.49 | 12.07 | 0 | 0 | 0 | Normal
2025-09-19 14:00 | 262 | 9 | Spring | 14 | 11.73 | -16.2 | 15.27 | 34.6 | 417.9 | 25.07 | 120 | 145.07 | 16.2 | 60.41 | 79.64 | 84.66 | 0 | 0 | 0 | Normal
2025-09-19 15:00 | 262 | 9 | Spring | 15 | 11.73 | -22.7 | 17.66 | 62.2 | 242.9 | 12.39 | 120 | 132.39 | 22.7 | 66.08 | 95 | 41.74 | 0 | 0 | 0 | Normal
2025-09-19 16:00 | 262 | 9 | Spring | 16 | 11.73 | -16.3 | 26.57 | 93.7 | 93.5 | 5.61 | 120 | 125.61 | 16.3 | 63.13 | 95 | 0 | 0 | 0 | 0 | Normal
2025-09-19 17:00 | 262 | 9 | Spring | 17 | 11.73 | -11.6 | 11.3 | 0 | 150.6 | 9.04 | 66.42 | 75.46 | 11.6 | 50.46 | 95 | 0 | 0 | 0 | 0 | Normal
2025-09-19 18:00 | 262 | 9 | Spring | 18 | 11.73 | -15.7 | 2.27 | 34.4 | 0 | 0 | 0 | 0 | 15.7 | 57.5 | 72 | -57.5 | 0 | 0 | 0 | Battery-supported
2025-09-19 19:00 | 262 | 9 | Spring | 19 | 11.73 | -19.4 | 12.49 | 19.5 | 0 | 0 | 101.69 | 101.69 | 19.4 | 56.82 | 88.51 | 44.87 | 0 | 0 | 0 | Normal
2025-09-19 20:00 | 262 | 9 | Spring | 20 | 11.73 | -16.2 | 2.14 | 37.6 | 0 | 0 | 0 | 0 | 16.2 | 55.39 | 66.36 | -55.39 | 0 | 0 | 0 | Battery-supported
2025-09-19 21:00 | 262 | 9 | Spring | 21 | 11.73 | -19.7 | 13.39 | 41.1 | 0 | 0 | 120 | 120 | 19.7 | 55.54 | 90.08 | 64.46 | 0 | 0 | 0 | Normal
2025-09-19 22:00 | 262 | 9 | Spring | 22 | 11.73 | -14.3 | 10.2 | 14.2 | 0 | 0 | 42.1 | 42.1 | 14.3 | 52.4 | 85.96 | -10.3 | 0 | 0 | 0 | Battery-supported
2025-09-19 23:00 | 262 | 9 | Spring | 23 | 11.73 | -19.4 | 17.11 | 72.4 | 0 | 0 | 120 | 120 | 19.4 | 61.7 | 95 | 24.57 | 0 | 0 | 0 | Normal
2025-09-20 | 263 | 9 | Spring | 0 | 11.88 | -17.2 | 7.24 | 52.6 | 0 | 0 | 7.32 | 7.32 | 17.2 | 51.75 | 77.23 | -44.43 | 0 | 0 | 0 | Battery-supported
2025-09-20 01:00 | 263 | 9 | Spring | 1 | 11.88 | -19.6 | 10.47 | 41.9 | 0 | 0 | 47.39 | 47.39 | 19.6 | 52.99 | 74.99 | -5.6 | 0 | 0 | 0 | Battery-supported
2025-09-20 02:00 | 263 | 9 | Spring | 2 | 11.88 | -19.3 | 12.58 | 40.5 | 0 | 0 | 104.78 | 104.78 | 19.3 | 54.01 | 93.67 | 50.77 | 0 | 0 | 0 | Normal
2025-09-20 03:00 | 263 | 9 | Spring | 3 | 11.88 | -15.3 | 1.33 | 39.4 | 0 | 0 | 0 | 0 | 15.3 | 51.27 | 73.16 | -51.27 | 0 | 0 | 0 | Battery-supported
2025-09-20 04:00 | 263 | 9 | Spring | 4 | 11.88 | -18.7 | 12.24 | 61.9 | 0 | 0 | 93.44 | 93.44 | 18.7 | 60.91 | 85.13 | 32.53 | 0 | 0 | 0 | Normal
2025-09-20 05:00 | 263 | 9 | Spring | 5 | 11.88 | -20.4 | 1.43 | 7.3 | 0 | 0 | 0 | 0 | 20.4 | 55.43 | 62.96 | -55.43 | 0 | 0 | 0 | Battery-supported
2025-09-20 06:00 | 263 | 9 | Spring | 6 | 11.88 | -22 | 5.75 | 27.2 | 0 | 0 | 1.59 | 1.59 | 22 | 52.62 | 42.55 | -51.03 | 0 | 0 | 0 | Battery-supported
2025-09-20 07:00 | 263 | 9 | Spring | 7 | 11.88 | -23.7 | 11.49 | 29.9 | 125.4 | 6.4 | 71.39 | 77.79 | 23.7 | 60.25 | 49.01 | 17.54 | 0 | 0 | 0 | Normal
2025-09-20 08:00 | 263 | 9 | Spring | 8 | 11.88 | -22.4 | 1.81 | 24 | 264.1 | 13.47 | 0 | 13.47 | 22.4 | 65.74 | 28.1 | -52.27 | 0 | 0 | 0 | Battery-supported
2025-09-20 09:00 | 263 | 9 | Spring | 9 | 11.88 | -19.3 | 13.72 | 43.8 | 309 | 15.76 | 120 | 135.76 | 19.3 | 62.15 | 55.19 | 73.61 | 0 | 0 | 0 | Normal
2025-09-20 10:00 | 263 | 9 | Spring | 10 | 11.88 | -17.3 | 13.05 | 33.8 | 422.8 | 25.37 | 120 | 145.37 | 17.3 | 59.23 | 86.89 | 86.14 | 0 | 0 | 0 | Normal
2025-09-20 11:00 | 263 | 9 | Spring | 11 | 11.88 | -20.4 | 16.63 | 55.1 | 371.4 | 18.94 | 120 | 138.94 | 20.4 | 71.68 | 95 | 22.05 | 0 | 0 | 0 | Normal
2025-09-20 12:00 | 263 | 9 | Spring | 12 | 11.88 | -15.4 | 2.71 | 41 | 454 | 27.24 | 0 | 27.24 | 15.4 | 56.38 | 83.34 | -29.14 | 0 | 0 | 0 | Battery-supported
2025-09-20 13:00 | 263 | 9 | Spring | 13 | 11.88 | -20.1 | 26.06 | 62.9 | 334.4 | 17.05 | 120 | 137.05 | 20.1 | 56.96 | 95 | 31.67 | 0 | 0 | 0 | Normal
2025-09-20 14:00 | 263 | 9 | Spring | 14 | 11.88 | -18.7 | 3.77 | 25.4 | 458.3 | 23.37 | 0 | 23.37 | 18.7 | 59.3 | 80.63 | -35.93 | 0 | 0 | 0 | Battery-supported
2025-09-20 15:00 | 263 | 9 | Spring | 15 | 11.88 | -20.1 | 10.43 | 52.3 | 279.9 | 14.27 | 46.58 | 60.85 | 20.1 | 61.14 | 80.51 | -0.29 | 0 | 0 | 0 | Battery-supported
2025-09-20 16:00 | 263 | 9 | Spring | 16 | 11.88 | -15.2 | 7.53 | 37.2 | 232.3 | 13.94 | 9.16 | 23.1 | 15.2 | 53.14 | 68.5 | -30.04 | 0 | 0 | 0 | Battery-supported
2025-09-20 17:00 | 263 | 9 | Spring | 17 | 11.88 | -12.5 | 8.71 | 77.2 | 68.1 | 4.09 | 19.79 | 23.88 | 12.5 | 54.74 | 56.15 | -30.86 | 0 | 0 | 0 | Battery-supported
2025-09-20 18:00 | 263 | 9 | Spring | 18 | 11.88 | -20.7 | 23.91 | 24.9 | 0 | 0 | 120 | 120 | 20.7 | 70.15 | 74.5 | 49.85 | 0 | 0 | 0 | Normal
2025-09-20 19:00 | 263 | 9 | Spring | 19 | 11.88 | -17.5 | 4.19 | 39 | 0 | 0 | 0.05 | 0.05 | 17.5 | 55.42 | 52.35 | -55.37 | 0 | 0 | 0 | Battery-supported
2025-09-20 20:00 | 263 | 9 | Spring | 20 | 11.88 | -13.9 | 21.81 | 37.1 | 0 | 0 | 120 | 120 | 13.9 | 51.36 | 77.61 | 68.64 | 0 | 0 | 0 | Normal
2025-09-20 21:00 | 263 | 9 | Spring | 21 | 11.88 | -19.9 | 14.88 | 95.7 | 0 | 0 | 120 | 120 | 19.9 | 57.88 | 95 | 47.26 | 0 | 0 | 0 | Normal
2025-09-20 22:00 | 263 | 9 | Spring | 22 | 11.88 | -15.6 | 9.33 | 69.7 | 0 | 0 | 27.73 | 27.73 | 15.6 | 49.8 | 86.17 | -22.07 | 0 | 0 | 0 | Battery-supported
2025-09-20 23:00 | 263 | 9 | Spring | 23 | 11.88 | -14.4 | 9.27 | 85.7 | 0 | 0 | 26.89 | 26.89 | 14.4 | 47.87 | 77.78 | -20.98 | 0 | 0 | 0 | Battery-supported
2025-09-21 | 264 | 9 | Spring | 0 | 12.04 | -17 | 13.04 | 64.9 | 0 | 0 | 120 | 120 | 17 | 56.32 | 95 | 46.79 | 0 | 0 | 0 | Normal
2025-09-21 01:00 | 264 | 9 | Spring | 1 | 12.04 | -16.4 | 7.16 | 51.4 | 0 | 0 | 6.86 | 6.86 | 16.4 | 49.18 | 78.07 | -42.32 | 0 | 0 | 0 | Battery-supported
2025-09-21 02:00 | 264 | 9 | Spring | 2 | 12.04 | -14.1 | 8.09 | 32 | 0 | 0 | 13.53 | 13.53 | 14.1 | 45 | 65.48 | -31.47 | 0 | 0 | 0 | Battery-supported
2025-09-21 03:00 | 264 | 9 | Spring | 3 | 12.04 | -14.1 | 10.36 | 52.1 | 0 | 0 | 45.18 | 45.18 | 14.1 | 52.3 | 62.64 | -7.12 | 0 | 0 | 0 | Battery-supported
2025-09-21 04:00 | 264 | 9 | Spring | 4 | 12.04 | -18.8 | 20.34 | 56.8 | 0 | 0 | 120 | 120 | 18.8 | 53.56 | 87.09 | 66.44 | 0 | 0 | 0 | Normal
2025-09-21 05:00 | 264 | 9 | Spring | 5 | 12.04 | -20.2 | 8.6 | 54.4 | 0 | 0 | 18.57 | 18.57 | 20.2 | 54.74 | 72.62 | -36.17 | 0 | 0 | 0 | Battery-supported
2025-09-21 06:00 | 264 | 9 | Spring | 6 | 12.04 | -21.3 | 2.45 | 52.1 | 2 | 0.1 | 0 | 0.1 | 21.3 | 48.5 | 53.26 | -48.4 | 0 | 0 | 0 | Battery-supported
2025-09-21 07:00 | 264 | 9 | Spring | 7 | 12.04 | -17.3 | 10.63 | 75.9 | 74.3 | 4.46 | 50.73 | 55.19 | 17.3 | 48.3 | 55.79 | 6.89 | 0 | 0 | 0 | Normal
2025-09-21 08:00 | 264 | 9 | Spring | 8 | 12.04 | -22.5 | 8.93 | 59.8 | 182 | 9.28 | 22.41 | 31.69 | 22.5 | 64.7 | 42.59 | -33.01 | 0 | 0 | 0 | Battery-supported
2025-09-21 09:00 | 264 | 9 | Spring | 9 | 12.04 | -20 | 6.1 | 16.6 | 407.2 | 20.77 | 2.46 | 23.23 | 20 | 58.74 | 28.39 | -35.51 | 0 | 0 | 0 | Battery-supported
2025-09-21 10:00 | 264 | 9 | Spring | 10 | 12.04 | -19 | 11.65 | 38.6 | 403.8 | 20.59 | 75.77 | 96.36 | 19 | 65.82 | 39.62 | 30.54 | 0 | 0 | 0 | Normal
2025-09-21 11:00 | 264 | 9 | Spring | 11 | 12.04 | -20.1 | 6.24 | 53 | 381.8 | 19.47 | 2.88 | 22.35 | 20.1 | 62.84 | 23.43 | -40.49 | 0 | 0 | 0 | Battery-supported
2025-09-21 12:00 | 264 | 9 | Spring | 12 | 12.04 | -18.1 | 8.47 | 23.6 | 540 | 27.54 | 17.18 | 44.72 | 18.1 | 60.14 | 17.26 | -15.42 | 0 | 0 | 0 | Battery-supported
2025-09-21 13:00 | 264 | 9 | Spring | 13 | 12.04 | -12.7 | 10.39 | 67.7 | 312 | 18.72 | 45.78 | 64.5 | 12.7 | 59.6 | 19.06 | 4.9 | 0 | 0 | 0 | Normal
2025-09-21 14:00 | 264 | 9 | Spring | 14 | 12.04 | -18.2 | 11.02 | 7 | 538.8 | 27.48 | 59.52 | 87 | 18.2 | 58.87 | 29.42 | 28.13 | 0 | 0 | 0 | Normal
2025-09-21 15:00 | 264 | 9 | Spring | 15 | 12.04 | -18.5 | 12.22 | 66.1 | 234.4 | 11.95 | 92.8 | 104.75 | 18.5 | 63.04 | 44.76 | 41.71 | 0 | 0 | 0 | Normal
2025-09-21 16:00 | 264 | 9 | Spring | 16 | 12.04 | -15 | 13.26 | 25.2 | 267.5 | 16.05 | 120 | 136.05 | 15 | 58 | 73.49 | 78.05 | 0 | 0 | 0 | Normal
2025-09-21 17:00 | 264 | 9 | Spring | 17 | 12.04 | -16.4 | 10.25 | 72.2 | 79 | 4.74 | 43.04 | 47.78 | 16.4 | 62.76 | 67.49 | -14.98 | 0 | 0 | 0 | Battery-supported
2025-09-21 18:00 | 264 | 9 | Spring | 18 | 12.04 | -13.5 | 2.93 | 68.9 | 1.6 | 0.1 | 0 | 0.1 | 13.5 | 58.25 | 44.23 | -58.15 | 0 | 0 | 0 | Battery-supported
2025-09-21 19:00 | 264 | 9 | Spring | 19 | 12.04 | -16.1 | 11.27 | 21.2 | 0 | 0 | 65.66 | 65.66 | 16.1 | 61.61 | 45.73 | 4.05 | 0 | 0 | 0 | Normal
2025-09-21 20:00 | 264 | 9 | Spring | 20 | 12.04 | -17 | 16.32 | 82.2 | 0 | 0 | 120 | 120 | 17 | 57.96 | 68.56 | 62.04 | 0 | 0 | 0 | Normal
2025-09-21 21:00 | 264 | 9 | Spring | 21 | 12.04 | -20.4 | 2.39 | 75.2 | 0 | 0 | 0 | 0 | 20.4 | 53.16 | 47.29 | -53.16 | 0 | 0 | 0 | Battery-supported
2025-09-21 22:00 | 264 | 9 | Spring | 22 | 12.04 | -20.2 | 2.96 | 100 | 0 | 0 | 0 | 0 | 20.2 | 54.84 | 25.36 | -54.84 | 0 | 0 | 0 | Battery-supported
2025-09-21 23:00 | 264 | 9 | Spring | 23 | 12.04 | -20.9 | 5.57 | 30.7 | 0 | 0 | 1.24 | 1.24 | 20.9 | 58.38 | 15 | -25.89 | 31.25 | 10.55 | 0 | Diesel-backup
2025-09-22 | 265 | 9 | Spring | 0 | 12.19 | -16.2 | 15.68 | 55.8 | 0 | 0 | 120 | 120 | 16.2 | 52.73 | 39.76 | 67.27 | 0 | 0 | 0 | Normal
2025-09-22 01:00 | 265 | 9 | Spring | 1 | 12.19 | -20.4 | 5.33 | 55.3 | 0 | 0 | 0.86 | 0.86 | 20.4 | 58.52 | 16.69 | -57.66 | 0 | 0 | 0 | Battery-supported
2025-09-22 02:00 | 265 | 9 | Spring | 2 | 12.19 | -15 | 15.81 | 14.5 | 0 | 0 | 120 | 120 | 15 | 46.64 | 43.69 | 73.36 | 0 | 0 | 0 | Normal
2025-09-22 03:00 | 265 | 9 | Spring | 3 | 12.19 | -18.1 | 10.82 | 57.8 | 0 | 0 | 54.9 | 54.9 | 18.1 | 47.78 | 46.31 | 7.12 | 0 | 0 | 0 | Normal
2025-09-22 04:00 | 265 | 9 | Spring | 4 | 12.19 | -19.1 | 6.41 | 50.2 | 0 | 0 | 3.45 | 3.45 | 19.1 | 52.19 | 26.81 | -48.74 | 0 | 0 | 0 | Battery-supported
2025-09-22 05:00 | 265 | 9 | Spring | 5 | 12.19 | -20.7 | 38.5 | 85.1 | 0 | 0 | 0 | 0 | 20.7 | 53.1 | 15 | -29.53 | 23.57 | 8.189 | 0 | Diesel-backup
2025-09-22 06:00 | 265 | 9 | Spring | 6 | 12.19 | -17.7 | 3.79 | 57.9 | 9.2 | 0.55 | 0 | 0.55 | 17.7 | 48.93 | 15 | 0 | 48.38 | 15.482 | 0 | Diesel-backup
2025-09-22 07:00 | 265 | 9 | Spring | 7 | 12.19 | -21 | 9.53 | 25.3 | 148.1 | 7.55 | 30.69 | 38.24 | 21 | 55.17 | 15 | 0 | 16.93 | 6.026 | 0 | Diesel-backup
2025-09-22 08:00 | 265 | 9 | Spring | 8 | 12.19 | -21.4 | 4.89 | 59.8 | 185.9 | 9.48 | 0.38 | 9.86 | 21.4 | 59.3 | 15 | 0 | 49.44 | 15.821 | 0 | Diesel-backup
2025-09-22 09:00 | 265 | 9 | Spring | 9 | 12.19 | -16.6 | 11.55 | 16.5 | 411.4 | 24.68 | 73.01 | 97.69 | 16.6 | 57.38 | 29.83 | 40.31 | 0 | 0 | 0 | Normal
2025-09-22 10:00 | 265 | 9 | Spring | 10 | 12.19 | -18.3 | 5.05 | 42.6 | 388.2 | 19.8 | 0.52 | 20.32 | 18.3 | 57.44 | 15 | -37.09 | 0.03 | 0.013 | 0 | Diesel-backup
2025-09-22 11:00 | 265 | 9 | Spring | 11 | 12.19 | -19.3 | 7.02 | 41.8 | 435.2 | 22.2 | 6.1 | 28.3 | 19.3 | 57.63 | 15 | 0 | 29.33 | 9.974 | 0 | Diesel-backup
2025-09-22 12:00 | 265 | 9 | Spring | 12 | 12.19 | -17.1 | 5.73 | 55.5 | 382.7 | 22.96 | 1.55 | 24.51 | 17.1 | 55.18 | 15 | 0 | 30.67 | 10.377 | 0 | Diesel-backup
2025-09-22 13:00 | 265 | 9 | Spring | 13 | 12.19 | -18.1 | 7.92 | 26.5 | 508.2 | 25.92 | 12.09 | 38.01 | 18.1 | 57.18 | 15 | 0 | 19.17 | 6.768 | 0 | Diesel-backup
2025-09-22 14:00 | 265 | 9 | Spring | 14 | 12.19 | -16.9 | 16.18 | 77.3 | 239.7 | 14.38 | 120 | 134.38 | 16.9 | 61.96 | 41.65 | 72.42 | 0 | 0 | 0 | Normal
2025-09-22 15:00 | 265 | 9 | Spring | 15 | 12.19 | -19.2 | 3.38 | 13.9 | 420.6 | 21.45 | 0 | 21.45 | 19.2 | 61.07 | 25.8 | -39.62 | 0 | 0 | 0 | Battery-supported
2025-09-22 16:00 | 265 | 9 | Spring | 16 | 12.19 | -12.5 | 5.39 | 53 | 203.1 | 12.19 | 0.94 | 13.13 | 12.5 | 55.94 | 15 | -27.01 | 15.8 | 5.648 | 0 | Diesel-backup
2025-09-22 17:00 | 265 | 9 | Spring | 17 | 12.19 | -18 | 7.22 | 56.6 | 105.2 | 6.31 | 7.21 | 13.52 | 18 | 60.18 | 15 | 0 | 46.66 | 14.931 | 0 | Diesel-backup
2025-09-22 18:00 | 265 | 9 | Spring | 18 | 12.19 | -13 | 8.13 | 58.2 | 9.2 | 0.55 | 13.89 | 14.44 | 13 | 58.54 | 15 | 0 | 44.1 | 14.163 | 0 | Diesel-backup
2025-09-22 19:00 | 265 | 9 | Spring | 19 | 12.19 | -16.7 | 19.5 | 41.8 | 0 | 0 | 120 | 120 | 16.7 | 61.71 | 36.45 | 58.29 | 0 | 0 | 0 | Normal
2025-09-22 20:00 | 265 | 9 | Spring | 20 | 12.19 | -14.5 | 5.57 | 67.7 | 0 | 0 | 1.24 | 1.24 | 14.5 | 59.62 | 15 | -53.63 | 4.75 | 1.766 | 0 | Diesel-backup
2025-09-22 21:00 | 265 | 9 | Spring | 21 | 12.19 | -14.7 | 15.77 | 47 | 0 | 0 | 120 | 120 | 14.7 | 48.96 | 41.14 | 71.04 | 0 | 0 | 0 | Normal
2025-09-22 22:00 | 265 | 9 | Spring | 22 | 12.19 | -13.9 | 20.94 | 81 | 0 | 0 | 120 | 120 | 13.9 | 48.76 | 67.36 | 71.24 | 0 | 0 | 0 | Normal
2025-09-22 23:00 | 265 | 9 | Spring | 23 | 12.19 | -18.6 | 8.46 | 92 | 0 | 0 | 17.08 | 17.08 | 18.6 | 48.88 | 54.64 | -31.8 | 0 | 0 | 0 | Battery-supported
2025-09-23 | 266 | 9 | Spring | 0 | 12.35 | -14.5 | 4.64 | 78.7 | 0 | 0 | 0.21 | 0.21 | 14.5 | 46.69 | 36.05 | -46.48 | 0 | 0 | 0 | Battery-supported
2025-09-23 01:00 | 266 | 9 | Spring | 1 | 12.35 | -13.1 | 18.02 | 50.4 | 0 | 0 | 120 | 120 | 13.1 | 51.04 | 61.42 | 68.96 | 0 | 0 | 0 | Normal
2025-09-23 02:00 | 266 | 9 | Spring | 2 | 12.35 | -18.1 | 14.94 | 16.9 | 0 | 0 | 120 | 120 | 18.1 | 50.89 | 86.86 | 69.11 | 0 | 0 | 0 | Normal
2025-09-23 03:00 | 266 | 9 | Spring | 3 | 12.35 | -17.9 | 4.32 | 90.1 | 0 | 0 | 0.08 | 0.08 | 17.9 | 51.88 | 66.14 | -51.8 | 0 | 0 | 0 | Battery-supported
2025-09-23 04:00 | 266 | 9 | Spring | 4 | 12.35 | -19.5 | 22.75 | 62.5 | 0 | 0 | 120 | 120 | 19.5 | 56.89 | 89.36 | 63.11 | 0 | 0 | 0 | Normal
2025-09-23 05:00 | 266 | 9 | Spring | 5 | 12.35 | -19.4 | 5.91 | 27.9 | 0 | 0 | 1.96 | 1.96 | 19.4 | 55.34 | 68.01 | -53.38 | 0 | 0 | 0 | Battery-supported
2025-09-23 06:00 | 266 | 9 | Spring | 6 | 12.35 | -15.1 | 8.36 | 70.7 | 13.6 | 0.82 | 16.07 | 16.89 | 15.1 | 50.12 | 54.72 | -33.23 | 0 | 0 | 0 | Battery-supported
2025-09-23 07:00 | 266 | 9 | Spring | 7 | 12.35 | -21.2 | 13.51 | 93.6 | 57.5 | 2.93 | 120 | 122.93 | 21.2 | 55.21 | 79.64 | 67.72 | 0 | 0 | 0 | Normal
2025-09-23 08:00 | 266 | 9 | Spring | 8 | 12.35 | -21.2 | 21.19 | 62 | 184.3 | 9.4 | 120 | 129.4 | 21.2 | 67.43 | 95 | 41.74 | 0 | 0 | 0 | Normal
2025-09-23 09:00 | 266 | 9 | Spring | 9 | 12.35 | -15.5 | 11.12 | 38.4 | 337.4 | 20.24 | 61.93 | 82.17 | 15.5 | 55.83 | 95 | 0 | 0 | 0 | 0 | Normal
2025-09-23 10:00 | 266 | 9 | Spring | 10 | 12.35 | -17.5 | 7.81 | 36.2 | 417.4 | 25.04 | 11.21 | 36.25 | 17.5 | 61.75 | 84.8 | -25.5 | 0 | 0 | 0 | Battery-supported
2025-09-23 11:00 | 266 | 9 | Spring | 11 | 12.35 | -14 | 7.1 | 80.9 | 249.8 | 14.99 | 6.53 | 21.52 | 14 | 55.86 | 71.06 | -34.34 | 0 | 0 | 0 | Battery-supported
2025-09-23 12:00 | 266 | 9 | Spring | 12 | 12.35 | -19.3 | 7.8 | 27.1 | 522.4 | 26.64 | 11.13 | 37.77 | 19.3 | 64.43 | 60.4 | -26.66 | 0 | 0 | 0 | Battery-supported
2025-09-23 13:00 | 266 | 9 | Spring | 13 | 12.35 | -17.7 | 30.05 | 49.1 | 400.8 | 24.05 | 0 | 24.05 | 17.7 | 63.17 | 44.75 | -39.12 | 0 | 0 | 0 | Battery-supported
2025-09-23 14:00 | 266 | 9 | Spring | 14 | 12.35 | -19 | 12.05 | 74 | 255 | 13 | 87.48 | 100.48 | 19 | 62.42 | 58.76 | 38.06 | 0 | 0 | 0 | Normal
2025-09-23 15:00 | 266 | 9 | Spring | 15 | 12.35 | -16.9 | 10.22 | 61.8 | 254.4 | 15.26 | 42.47 | 57.73 | 16.9 | 64.07 | 56.22 | -6.34 | 0 | 0 | 0 | Battery-supported
2025-09-23 16:00 | 266 | 9 | Spring | 16 | 12.35 | -20.7 | 15.03 | 87.5 | 118.4 | 6.04 | 120 | 126.04 | 20.7 | 66.44 | 78.15 | 59.6 | 0 | 0 | 0 | Normal
2025-09-23 17:00 | 266 | 9 | Spring | 17 | 12.35 | -15 | 8.16 | 48.1 | 123.4 | 7.4 | 14.16 | 21.56 | 15 | 56.82 | 64.05 | -35.26 | 0 | 0 | 0 | Battery-supported
2025-09-23 18:00 | 266 | 9 | Spring | 18 | 12.35 | -15.6 | 20.55 | 84.1 | 10.7 | 0.64 | 120 | 120.64 | 15.6 | 59.44 | 86.57 | 61.2 | 0 | 0 | 0 | Normal
2025-09-23 19:00 | 266 | 9 | Spring | 19 | 12.35 | -16.3 | 12.66 | 34.2 | 0 | 0 | 107.57 | 107.57 | 16.3 | 60.31 | 95 | 22.9 | 0 | 0 | 0 | Normal
2025-09-23 20:00 | 266 | 9 | Spring | 20 | 12.35 | -16.9 | 7.69 | 49.1 | 0 | 0 | 10.3 | 10.3 | 16.9 | 63.67 | 73.65 | -53.37 | 0 | 0 | 0 | Battery-supported
2025-09-23 21:00 | 266 | 9 | Spring | 21 | 12.35 | -18.1 | 6.7 | 55.2 | 0 | 0 | 4.59 | 4.59 | 18.1 | 47.24 | 56.59 | -42.65 | 0 | 0 | 0 | Battery-supported
2025-09-23 22:00 | 266 | 9 | Spring | 22 | 12.35 | -14.7 | 2.64 | 53.2 | 0 | 0 | 0 | 0 | 14.7 | 53.96 | 35.01 | -53.96 | 0 | 0 | 0 | Battery-supported
2025-09-23 23:00 | 266 | 9 | Spring | 23 | 12.35 | -19.1 | 16.11 | 71.4 | 0 | 0 | 120 | 120 | 19.1 | 47.86 | 61.56 | 72.14 | 0 | 0 | 0 | Normal
2025-09-24 | 267 | 9 | Spring | 0 | 12.5 | -15.5 | 3.33 | 71.7 | 0 | 0 | 0 | 0 | 15.5 | 52.25 | 40.66 | -52.25 | 0 | 0 | 0 | Battery-supported
2025-09-24 01:00 | 267 | 9 | Spring | 1 | 12.5 | -12.4 | 19.81 | 43.8 | 0 | 0 | 120 | 120 | 12.4 | 49.12 | 66.74 | 70.88 | 0 | 0 | 0 | Normal
2025-09-24 02:00 | 267 | 9 | Spring | 2 | 12.5 | -14.1 | 5.26 | 92.4 | 0 | 0 | 0.76 | 0.76 | 14.1 | 48.28 | 47.73 | -47.52 | 0 | 0 | 0 | Battery-supported
2025-09-24 03:00 | 267 | 9 | Spring | 3 | 12.5 | -21.1 | 5.72 | 73.9 | 0 | 0 | 1.53 | 1.53 | 21.1 | 58.42 | 24.98 | -56.89 | 0 | 0 | 0 | Battery-supported
2025-09-24 04:00 | 267 | 9 | Spring | 4 | 12.5 | -19.3 | 25.76 | 52.2 | 0 | 0 | 120 | 120 | 19.3 | 49.54 | 50.9 | 70.46 | 0 | 0 | 0 | Normal
2025-09-24 05:00 | 267 | 9 | Spring | 5 | 12.5 | -17.5 | 15.35 | 85 | 0 | 0 | 120 | 120 | 17.5 | 49.31 | 76.92 | 70.69 | 0 | 0 | 0 | Normal
2025-09-24 06:00 | 267 | 9 | Spring | 6 | 12.5 | -18.8 | 10.03 | 94.5 | 12 | 0.61 | 38.97 | 39.58 | 18.8 | 49.56 | 72.93 | -9.98 | 0 | 0 | 0 | Battery-supported
2025-09-24 07:00 | 267 | 9 | Spring | 7 | 12.5 | -21.9 | 24.37 | 20.5 | 171.5 | 8.75 | 120 | 128.75 | 21.9 | 54.25 | 95 | 59.98 | 0 | 0 | 0 | Normal
2025-09-24 08:00 | 267 | 9 | Spring | 8 | 12.5 | -18 | 8.9 | 82.7 | 133.4 | 8 | 22.04 | 30.04 | 18 | 65.12 | 80.97 | -35.08 | 0 | 0 | 0 | Battery-supported
2025-09-24 09:00 | 267 | 9 | Spring | 9 | 12.5 | -18.9 | 6.91 | 14.7 | 425.6 | 21.71 | 5.55 | 27.26 | 18.9 | 66.8 | 65.15 | -39.54 | 0 | 0 | 0 | Battery-supported
2025-09-24 10:00 | 267 | 9 | Spring | 10 | 12.5 | -14.5 | 10.6 | 59.9 | 316.6 | 19 | 50.09 | 69.09 | 14.5 | 57.12 | 69.56 | 11.97 | 0 | 0 | 0 | Normal
2025-09-24 11:00 | 267 | 9 | Spring | 11 | 12.5 | -19 | 16.7 | 54.8 | 374.4 | 19.09 | 120 | 139.09 | 19 | 62.72 | 95 | 69.14 | 0 | 0 | 0 | Normal
2025-09-24 12:00 | 267 | 9 | Spring | 12 | 12.5 | -15.6 | 3.92 | 78.9 | 267.6 | 16.06 | 0.01 | 16.07 | 15.6 | 66.22 | 74.94 | -50.15 | 0 | 0 | 0 | Battery-supported
2025-09-24 13:00 | 267 | 9 | Spring | 13 | 12.5 | -20.6 | 5.63 | 13.8 | 569.8 | 29.06 | 1.35 | 30.41 | 20.6 | 61.93 | 62.33 | -31.52 | 0 | 0 | 0 | Battery-supported
2025-09-24 14:00 | 267 | 9 | Spring | 14 | 12.5 | -19.7 | 4.7 | 39.6 | 404.2 | 20.61 | 0.24 | 20.85 | 19.7 | 60 | 46.67 | -39.15 | 0 | 0 | 0 | Battery-supported
2025-09-24 15:00 | 267 | 9 | Spring | 15 | 12.5 | -15.4 | 4.17 | 90 | 155.4 | 9.32 | 0.04 | 9.36 | 15.4 | 62.04 | 25.6 | -52.68 | 0 | 0 | 0 | Battery-supported
2025-09-24 16:00 | 267 | 9 | Spring | 16 | 12.5 | -14.3 | 8.33 | 51.3 | 216.2 | 12.97 | 15.77 | 28.74 | 14.3 | 55.19 | 15.02 | -26.45 | 0 | 0 | 0 | Battery-supported
2025-09-24 17:00 | 267 | 9 | Spring | 17 | 12.5 | -18.4 | 4.11 | 7.9 | 190.7 | 9.73 | 0.03 | 9.76 | 18.4 | 57.52 | 15 | -0.05 | 47.71 | 15.267 | 0 | Diesel-backup
2025-09-24 18:00 | 267 | 9 | Spring | 18 | 12.5 | -16 | 2.36 | 52.1 | 25.1 | 1.51 | 0 | 1.51 | 16 | 62.46 | 15 | 0 | 60.95 | 19.504 | 0 | Diesel-backup
2025-09-24 19:00 | 267 | 9 | Spring | 19 | 12.5 | -19 | 5.6 | 86 | 0 | 0 | 1.3 | 1.3 | 19 | 67.42 | 15 | 0 | 66.12 | 21.158 | 0 | Diesel-backup
2025-09-24 20:00 | 267 | 9 | Spring | 20 | 12.5 | -16.3 | 5.35 | 53.7 | 0 | 0 | 0.89 | 0.89 | 16.3 | 57.32 | 15 | 0 | 56.43 | 18.058 | 0 | Diesel-backup
2025-09-24 21:00 | 267 | 9 | Spring | 21 | 12.5 | -14.1 | 12.19 | 51.8 | 0 | 0 | 91.85 | 91.85 | 14.1 | 48.96 | 30.78 | 42.89 | 0 | 0 | 0 | Normal
2025-09-24 22:00 | 267 | 9 | Spring | 22 | 12.5 | -17 | 15.86 | 74.9 | 0 | 0 | 120 | 120 | 17 | 55.54 | 54.5 | 64.46 | 0 | 0 | 0 | Normal
2025-09-24 23:00 | 267 | 9 | Spring | 23 | 12.5 | -16.9 | 6.19 | 51.5 | 0 | 0 | 2.72 | 2.72 | 16.9 | 48.86 | 36.05 | -46.14 | 0 | 0 | 0 | Battery-supported
2025-09-25 | 268 | 9 | Spring | 0 | 12.66 | -18.9 | 5.66 | 59.7 | 0 | 0 | 1.41 | 1.41 | 18.9 | 57.64 | 15 | -52.62 | 3.61 | 1.346 | 0 | Diesel-backup
2025-09-25 01:00 | 268 | 9 | Spring | 1 | 12.66 | -18.2 | 24.86 | 77.8 | 0 | 0 | 120 | 120 | 18.2 | 58.99 | 37.45 | 61.01 | 0 | 0 | 0 | Normal
2025-09-25 02:00 | 268 | 9 | Spring | 2 | 12.66 | -13.3 | 15.48 | 28.4 | 0 | 0 | 120 | 120 | 13.3 | 45 | 65.05 | 75 | 0 | 0 | 0 | Normal
2025-09-25 03:00 | 268 | 9 | Spring | 3 | 12.66 | -17.4 | 11.36 | 58.9 | 0 | 0 | 67.96 | 67.96 | 17.4 | 47.03 | 72.75 | 20.93 | 0 | 0 | 0 | Normal
2025-09-25 04:00 | 268 | 9 | Spring | 4 | 12.66 | -20.2 | 7.49 | 100 | 0 | 0 | 8.89 | 8.89 | 20.2 | 48.75 | 56.81 | -39.86 | 0 | 0 | 0 | Battery-supported
2025-09-25 05:00 | 268 | 9 | Spring | 5 | 12.66 | -18.9 | 15.27 | 98 | 0 | 0 | 120 | 120 | 18.9 | 51.82 | 81.9 | 68.18 | 0 | 0 | 0 | Normal
2025-09-25 06:00 | 268 | 9 | Spring | 6 | 12.66 | -22 | 4.41 | 71.3 | 24.8 | 1.26 | 0.11 | 1.37 | 22 | 51.97 | 61.66 | -50.6 | 0 | 0 | 0 | Battery-supported
2025-09-25 07:00 | 268 | 9 | Spring | 7 | 12.66 | -20.9 | 15.68 | 47.9 | 136.1 | 6.94 | 120 | 126.94 | 20.9 | 60.24 | 86.21 | 66.7 | 0 | 0 | 0 | Normal
2025-09-25 08:00 | 268 | 9 | Spring | 8 | 12.66 | -15.7 | 12.51 | 31.5 | 273.7 | 16.42 | 102.37 | 118.79 | 15.7 | 54.85 | 95 | 23.9 | 0 | 0 | 0 | Normal
2025-09-25 09:00 | 268 | 9 | Spring | 9 | 12.66 | -19 | 13.93 | 49.3 | 303.9 | 15.5 | 120 | 135.5 | 19 | 60.38 | 95 | 0 | 0 | 0 | 0 | Normal
2025-09-25 10:00 | 268 | 9 | Spring | 10 | 12.66 | -14.3 | 10.06 | 64 | 299.8 | 17.99 | 39.51 | 57.5 | 14.3 | 58.74 | 94.5 | -1.24 | 0 | 0 | 0 | Battery-supported
2025-09-25 11:00 | 268 | 9 | Spring | 11 | 12.66 | -18.5 | 3.53 | 24.2 | 520.3 | 26.54 | 0 | 26.54 | 18.5 | 58.2 | 81.84 | -31.66 | 0 | 0 | 0 | Battery-supported
2025-09-25 12:00 | 268 | 9 | Spring | 12 | 12.66 | -18 | 4.5 | 69.6 | 313.5 | 18.81 | 0.14 | 18.95 | 18 | 61.03 | 65.01 | -42.08 | 0 | 0 | 0 | Battery-supported
2025-09-25 13:00 | 268 | 9 | Spring | 13 | 12.66 | -16.2 | 12.91 | 65 | 325.9 | 19.55 | 116.62 | 136.17 | 16.2 | 61.78 | 92.38 | 74.39 | 0 | 0 | 0 | Normal
2025-09-25 14:00 | 268 | 9 | Spring | 14 | 12.66 | -23.1 | 12.13 | 60.5 | 314.9 | 16.06 | 89.96 | 106.02 | 23.1 | 78.49 | 95 | 7.11 | 0 | 0 | 0 | Normal
2025-09-25 15:00 | 268 | 9 | Spring | 15 | 12.66 | -16.4 | 6.6 | 39.1 | 340.9 | 20.45 | 4.17 | 24.62 | 16.4 | 60.91 | 80.48 | -36.29 | 0 | 0 | 0 | Battery-supported
2025-09-25 16:00 | 268 | 9 | Spring | 16 | 12.66 | -16.6 | 6.52 | 38.2 | 255.6 | 15.34 | 3.86 | 19.2 | 16.6 | 53.27 | 66.86 | -34.07 | 0 | 0 | 0 | Battery-supported
2025-09-25 17:00 | 268 | 9 | Spring | 17 | 12.66 | -12.9 | 18.15 | 53.6 | 126.9 | 7.61 | 120 | 127.61 | 12.9 | 58.66 | 92.23 | 68.95 | 0 | 0 | 0 | Normal
2025-09-25 18:00 | 268 | 9 | Spring | 18 | 12.66 | -13.8 | 9.28 | 65.8 | 27 | 1.62 | 27.03 | 28.65 | 13.8 | 58.03 | 80.48 | -29.38 | 0 | 0 | 0 | Battery-supported
2025-09-25 19:00 | 268 | 9 | Spring | 19 | 12.66 | -18.2 | 5.38 | 92.7 | 0 | 0 | 0.93 | 0.93 | 18.2 | 63.2 | 55.57 | -62.27 | 0 | 0 | 0 | Battery-supported
2025-09-25 20:00 | 268 | 9 | Spring | 20 | 12.66 | -13 | 19.84 | 70.1 | 0 | 0 | 120 | 120 | 13 | 55.6 | 79.27 | 64.4 | 0 | 0 | 0 | Normal
2025-09-25 21:00 | 268 | 9 | Spring | 21 | 12.66 | -16.3 | 18.79 | 52.5 | 0 | 0 | 120 | 120 | 16.3 | 54.81 | 95 | 42.75 | 0 | 0 | 0 | Normal
2025-09-25 22:00 | 268 | 9 | Spring | 22 | 12.66 | -17.9 | 9.27 | 74.1 | 0 | 0 | 26.89 | 26.89 | 17.9 | 51.89 | 85 | -25 | 0 | 0 | 0 | Battery-supported
2025-09-25 23:00 | 268 | 9 | Spring | 23 | 12.66 | -15.7 | 10.46 | 57.2 | 0 | 0 | 47.19 | 47.19 | 15.7 | 51.92 | 83.11 | -4.73 | 0 | 0 | 0 | Battery-supported
2025-09-26 | 269 | 9 | Spring | 0 | 12.81 | -16.7 | 15.46 | 28.3 | 0 | 0 | 120 | 120 | 16.7 | 52.51 | 95 | 32.32 | 0 | 0 | 0 | Normal
2025-09-26 01:00 | 269 | 9 | Spring | 1 | 12.81 | -13.2 | 13.41 | 36.9 | 0 | 0 | 120 | 120 | 13.2 | 48.62 | 95 | 0 | 0 | 0 | 0 | Normal
2025-09-26 02:00 | 269 | 9 | Spring | 2 | 12.81 | -16.3 | 3.43 | 19.1 | 0 | 0 | 0 | 0 | 16.3 | 49.99 | 75 | -49.99 | 0 | 0 | 0 | Battery-supported
2025-09-26 03:00 | 269 | 9 | Spring | 3 | 12.81 | -16.9 | 20.14 | 80.1 | 0 | 0 | 120 | 120 | 16.9 | 56.37 | 95 | 54.34 | 0 | 0 | 0 | Normal
2025-09-26 04:00 | 269 | 9 | Spring | 4 | 12.81 | -15.8 | 2.95 | 37.2 | 0 | 0 | 0 | 0 | 15.8 | 56.31 | 72.48 | -56.31 | 0 | 0 | 0 | Battery-supported
2025-09-26 05:00 | 269 | 9 | Spring | 5 | 12.81 | -15.7 | 12.03 | 51.1 | 0 | 0 | 86.87 | 86.87 | 15.7 | 58.43 | 82.94 | 28.44 | 0 | 0 | 0 | Normal
2025-09-26 06:00 | 269 | 9 | Spring | 6 | 12.81 | -16.6 | 3.99 | 39.2 | 45.9 | 2.75 | 0.02 | 2.77 | 16.6 | 52.12 | 63.2 | -49.35 | 0 | 0 | 0 | Battery-supported
2025-09-26 07:00 | 269 | 9 | Spring | 7 | 12.81 | -15.3 | 13.4 | 49.4 | 139.5 | 8.37 | 120 | 128.37 | 15.3 | 51.21 | 91.6 | 77.16 | 0 | 0 | 0 | Normal
2025-09-26 08:00 | 269 | 9 | Spring | 8 | 12.81 | -17.2 | 5.77 | 59 | 203.4 | 12.2 | 1.64 | 13.84 | 17.2 | 61.36 | 72.59 | -47.52 | 0 | 0 | 0 | Battery-supported
2025-09-26 09:00 | 269 | 9 | Spring | 9 | 12.81 | -18.1 | 6.04 | 55.5 | 283.7 | 14.47 | 2.29 | 16.76 | 18.1 | 57.95 | 56.11 | -41.19 | 0 | 0 | 0 | Battery-supported
2025-09-26 10:00 | 269 | 9 | Spring | 10 | 12.81 | -15.6 | 14.95 | 46.2 | 377.9 | 22.67 | 120 | 142.67 | 15.6 | 62.15 | 85.74 | 80.52 | 0 | 0 | 0 | Normal
2025-09-26 11:00 | 269 | 9 | Spring | 11 | 12.81 | -18.3 | 3.99 | 57.5 | 361.8 | 18.45 | 0.02 | 18.47 | 18.3 | 60.24 | 69.04 | -41.77 | 0 | 0 | 0 | Battery-supported
2025-09-26 12:00 | 269 | 9 | Spring | 12 | 12.81 | -17.7 | 6.58 | 39.7 | 460.6 | 27.64 | 4.09 | 31.73 | 17.7 | 63.08 | 56.5 | -31.35 | 0 | 0 | 0 | Battery-supported
2025-09-26 13:00 | 269 | 9 | Spring | 13 | 12.81 | -13.6 | 4.1 | 21.7 | 532.8 | 31.97 | 0.03 | 32 | 13.6 | 52 | 48.5 | -20 | 0 | 0 | 0 | Battery-supported
2025-09-26 14:00 | 269 | 9 | Spring | 14 | 12.81 | -13.4 | 9.97 | 53.9 | 344.5 | 20.67 | 37.91 | 58.58 | 13.4 | 58.68 | 48.46 | -0.1 | 0 | 0 | 0 | Battery-supported
2025-09-26 15:00 | 269 | 9 | Spring | 15 | 12.81 | -16.6 | 4.04 | 34.7 | 359.6 | 21.58 | 0.02 | 21.6 | 16.6 | 64.76 | 31.19 | -43.16 | 0 | 0 | 0 | Battery-supported
2025-09-26 16:00 | 269 | 9 | Spring | 16 | 12.81 | -17.2 | 11.42 | 26.3 | 292.8 | 17.57 | 69.53 | 87.1 | 17.2 | 57.63 | 42.04 | 29.47 | 0 | 0 | 0 | Normal
2025-09-26 17:00 | 269 | 9 | Spring | 17 | 12.81 | -12.7 | 18.59 | 45.5 | 145.9 | 8.75 | 120 | 128.75 | 12.7 | 54.01 | 69.54 | 74.74 | 0 | 0 | 0 | Normal
2025-09-26 18:00 | 269 | 9 | Spring | 18 | 12.81 | -13.9 | 1.91 | 34.5 | 48.2 | 2.89 | 0 | 2.89 | 13.9 | 55.09 | 48.66 | -52.2 | 0 | 0 | 0 | Battery-supported
2025-09-26 19:00 | 269 | 9 | Spring | 19 | 12.81 | -14.9 | 5.79 | 59.3 | 0 | 0 | 1.68 | 1.68 | 14.9 | 56.1 | 26.89 | -54.42 | 0 | 0 | 0 | Battery-supported
2025-09-26 20:00 | 269 | 9 | Spring | 20 | 12.81 | -16.2 | 4.37 | 71.5 | 0 | 0 | 0.09 | 0.09 | 16.2 | 64.66 | 15 | -29.73 | 34.84 | 11.601 | 0 | Diesel-backup
2025-09-26 21:00 | 269 | 9 | Spring | 21 | 12.81 | -14.8 | 3.48 | 72.6 | 0 | 0 | 0 | 0 | 14.8 | 50.4 | 15 | 0 | 50.4 | 16.128 | 0 | Diesel-backup
2025-09-26 22:00 | 269 | 9 | Spring | 22 | 12.81 | -15.8 | 11.24 | 69.8 | 0 | 0 | 64.9 | 64.9 | 15.8 | 47.1 | 21.55 | 17.8 | 0 | 0 | 0 | Normal
2025-09-26 23:00 | 269 | 9 | Spring | 23 | 12.81 | -17.4 | 10.47 | 33.2 | 0 | 0 | 47.39 | 47.39 | 17.4 | 49.29 | 20.79 | -1.9 | 0 | 0 | 0 | Battery-supported
2025-09-27 | 270 | 9 | Spring | 0 | 12.96 | -15.8 | 20.01 | 53.9 | 0 | 0 | 120 | 120 | 15.8 | 45 | 48.39 | 75 | 0 | 0 | 0 | Normal
2025-09-27 01:00 | 270 | 9 | Spring | 1 | 12.96 | -15.8 | 13.98 | 28.3 | 0 | 0 | 120 | 120 | 15.8 | 47.9 | 74.92 | 72.1 | 0 | 0 | 0 | Normal
2025-09-27 02:00 | 270 | 9 | Spring | 2 | 12.96 | -17.6 | 9.52 | 31.8 | 0 | 0 | 30.54 | 30.54 | 17.6 | 47.75 | 68.04 | -17.21 | 0 | 0 | 0 | Battery-supported
2025-09-27 03:00 | 270 | 9 | Spring | 3 | 12.96 | -15.2 | 10.91 | 62.2 | 0 | 0 | 56.95 | 56.95 | 15.2 | 45.53 | 72.24 | 11.42 | 0 | 0 | 0 | Normal
2025-09-27 04:00 | 270 | 9 | Spring | 4 | 12.96 | -14.7 | 6.55 | 69.9 | 0 | 0 | 3.97 | 3.97 | 14.7 | 48.18 | 54.56 | -44.21 | 0 | 0 | 0 | Battery-supported
2025-09-27 05:00 | 270 | 9 | Spring | 5 | 12.96 | -15.7 | 11.12 | 43.4 | 0 | 0 | 61.93 | 61.93 | 15.7 | 46.53 | 60.22 | 15.4 | 0 | 0 | 0 | Normal
2025-09-27 06:00 | 270 | 9 | Spring | 6 | 12.96 | -18.7 | 2.96 | 76.6 | 32.6 | 1.66 | 0 | 1.66 | 18.7 | 53.21 | 39.6 | -51.55 | 0 | 0 | 0 | Battery-supported
2025-09-27 07:00 | 270 | 9 | Spring | 7 | 12.96 | -16.6 | 8.43 | 27.3 | 183.4 | 11 | 16.77 | 27.77 | 16.6 | 53.19 | 29.44 | -25.42 | 0 | 0 | 0 | Battery-supported
2025-09-27 08:00 | 270 | 9 | Spring | 8 | 12.96 | -18.1 | 12.2 | 72.9 | 168.3 | 8.58 | 92.17 | 100.75 | 18.1 | 62.43 | 43.54 | 38.32 | 0 | 0 | 0 | Normal
2025-09-27 09:00 | 270 | 9 | Spring | 9 | 12.96 | -21 | 8.15 | 45.5 | 322.8 | 16.46 | 14.07 | 30.53 | 21 | 64.99 | 29.75 | -34.46 | 0 | 0 | 0 | Battery-supported
2025-09-27 10:00 | 270 | 9 | Spring | 10 | 12.96 | -16.6 | 5.92 | 60.6 | 316.7 | 19 | 1.98 | 20.98 | 16.6 | 49.58 | 18.31 | -28.6 | 0 | 0 | 0 | Battery-supported
2025-09-27 11:00 | 270 | 9 | Spring | 11 | 12.96 | -17.5 | 9.78 | 19.9 | 541.6 | 32.5 | 34.66 | 67.16 | 17.5 | 58.61 | 21.46 | 8.55 | 0 | 0 | 0 | Normal
2025-09-27 12:00 | 270 | 9 | Spring | 12 | 12.96 | -11.9 | 5.34 | 79.1 | 267 | 16.02 | 0.87 | 16.89 | 11.9 | 60.02 | 15 | -16.15 | 26.98 | 9.255 | 0 | Diesel-backup
2025-09-27 13:00 | 270 | 9 | Spring | 13 | 12.96 | -14 | 7.84 | 85.7 | 227.7 | 13.66 | 11.44 | 25.1 | 14 | 65.54 | 15 | 0 | 40.44 | 13.177 | 0 | Diesel-backup
2025-09-27 14:00 | 270 | 9 | Spring | 14 | 12.96 | -15.2 | 14.78 | 74.2 | 257.5 | 15.45 | 120 | 135.45 | 15.2 | 61.44 | 42.24 | 74.01 | 0 | 0 | 0 | Normal
2025-09-27 15:00 | 270 | 9 | Spring | 15 | 12.96 | -15.9 | 15.33 | 56.6 | 282.1 | 16.93 | 120 | 136.93 | 15.9 | 59.14 | 70.86 | 77.79 | 0 | 0 | 0 | Normal
2025-09-27 16:00 | 270 | 9 | Spring | 16 | 12.96 | -15.7 | 10.57 | 21.9 | 310.2 | 18.61 | 49.46 | 68.07 | 15.7 | 55.37 | 75.54 | 12.7 | 0 | 0 | 0 | Normal
2025-09-27 17:00 | 270 | 9 | Spring | 17 | 12.96 | -18 | 4.64 | 77.1 | 97.2 | 5.83 | 0.21 | 6.04 | 18 | 66 | 51.55 | -59.96 | 0 | 0 | 0 | Battery-supported
2025-09-27 18:00 | 270 | 9 | Spring | 18 | 12.96 | -19.3 | 7.36 | 19 | 65.5 | 3.34 | 8.05 | 11.39 | 19.3 | 61.68 | 31.44 | -50.29 | 0 | 0 | 0 | Battery-supported
2025-09-27 19:00 | 270 | 9 | Spring | 19 | 12.96 | -17.3 | 9.89 | 27.5 | 0 | 0 | 36.52 | 36.52 | 17.3 | 59.31 | 22.32 | -22.79 | 0 | 0 | 0 | Battery-supported
2025-09-27 20:00 | 270 | 9 | Spring | 20 | 12.96 | -15.4 | 5.73 | 54.1 | 0 | 0 | 1.55 | 1.55 | 15.4 | 63 | 15 | -18.3 | 43.15 | 13.91 | 0 | Diesel-backup
2025-09-27 21:00 | 270 | 9 | Spring | 21 | 12.96 | -20 | 23.13 | 57.5 | 0 | 0 | 120 | 120 | 20 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-09-27 22:00 | 270 | 9 | Spring | 22 | 12.96 | -16.7 | 5.82 | 82.5 | 0 | 0 | 1.75 | 1.75 | 16.7 | 51.42 | 22.73 | -49.67 | 0 | 0 | 0 | Battery-supported
2025-09-27 23:00 | 270 | 9 | Spring | 23 | 12.96 | -16.3 | 9.49 | 40.8 | 0 | 0 | 30.08 | 30.08 | 16.3 | 45.4 | 16.6 | -15.32 | 0 | 0 | 0 | Battery-supported
2025-09-28 | 271 | 9 | Spring | 0 | 13.12 | -16.3 | 2.43 | 19.2 | 0 | 0 | 0 | 0 | 16.3 | 53.51 | 15 | -4.01 | 49.5 | 15.84 | 0 | Diesel-backup
2025-09-28 01:00 | 271 | 9 | Spring | 1 | 13.12 | -17.7 | 15.84 | 36.6 | 0 | 0 | 120 | 120 | 17.7 | 59.17 | 37.39 | 60.83 | 0 | 0 | 0 | Normal
2025-09-28 02:00 | 271 | 9 | Spring | 2 | 13.12 | -17.4 | 20.96 | 51.5 | 0 | 0 | 120 | 120 | 17.4 | 54.37 | 61.54 | 65.63 | 0 | 0 | 0 | Normal
2025-09-28 03:00 | 271 | 9 | Spring | 3 | 13.12 | -13.2 | 4.56 | 28 | 0 | 0 | 0.17 | 0.17 | 13.2 | 56.08 | 39.17 | -55.91 | 0 | 0 | 0 | Battery-supported
2025-09-28 04:00 | 271 | 9 | Spring | 4 | 13.12 | -15.9 | 3.02 | 69.2 | 0 | 0 | 0 | 0 | 15.9 | 51.74 | 18.48 | -51.74 | 0 | 0 | 0 | Battery-supported
2025-09-28 05:00 | 271 | 9 | Spring | 5 | 13.12 | -18.9 | 10.46 | 27.7 | 0 | 0 | 47.19 | 47.19 | 18.9 | 59.67 | 15 | -8.69 | 3.79 | 1.412 | 0 | Diesel-backup
2025-09-28 06:00 | 271 | 9 | Spring | 6 | 13.12 | -18.1 | 24.63 | 67.6 | 43.2 | 2.2 | 120 | 122.2 | 18.1 | 46.74 | 42.77 | 75.46 | 0 | 0 | 0 | Normal
2025-09-28 07:00 | 271 | 9 | Spring | 7 | 13.12 | -18.1 | 3.39 | 96.9 | 65.4 | 3.34 | 0 | 3.34 | 18.1 | 53.94 | 22.53 | -50.6 | 0 | 0 | 0 | Battery-supported
2025-09-28 08:00 | 271 | 9 | Spring | 8 | 13.12 | -19.8 | 7.51 | 56.8 | 216.5 | 11.04 | 9.02 | 20.06 | 19.8 | 57.5 | 15 | -18.82 | 18.62 | 6.586 | 0 | Diesel-backup
2025-09-28 09:00 | 271 | 9 | Spring | 9 | 13.12 | -19.8 | 11.01 | 57 | 282.8 | 14.42 | 59.28 | 73.7 | 19.8 | 64.33 | 18.45 | 9.37 | 0 | 0 | 0 | Normal
2025-09-28 10:00 | 271 | 9 | Spring | 10 | 13.12 | -15.7 | 9.72 | 37.7 | 417.7 | 25.06 | 33.68 | 58.74 | 15.7 | 57.42 | 18.93 | 1.32 | 0 | 0 | 0 | Normal
2025-09-28 11:00 | 271 | 9 | Spring | 11 | 13.12 | -18.6 | 12.04 | 52.1 | 388.4 | 19.81 | 87.17 | 106.98 | 18.6 | 60.81 | 35.92 | 46.17 | 0 | 0 | 0 | Normal
2025-09-28 12:00 | 271 | 9 | Spring | 12 | 13.12 | -19.8 | 19.27 | 57.8 | 371.5 | 18.95 | 120 | 138.95 | 19.8 | 61.95 | 64.26 | 77 | 0 | 0 | 0 | Normal
2025-09-28 13:00 | 271 | 9 | Spring | 13 | 13.12 | -17.1 | 16.02 | 92 | 197.8 | 11.87 | 120 | 131.87 | 17.1 | 64.3 | 89.13 | 67.57 | 0 | 0 | 0 | Normal
2025-09-28 14:00 | 271 | 9 | Spring | 14 | 13.12 | -16.4 | 7.41 | 62.9 | 307.5 | 18.45 | 8.37 | 26.82 | 16.4 | 60.17 | 75.79 | -33.35 | 0 | 0 | 0 | Battery-supported
2025-09-28 15:00 | 271 | 9 | Spring | 15 | 13.12 | -20.6 | 3.35 | 36.4 | 358.9 | 18.3 | 0 | 18.3 | 20.6 | 64.35 | 57.37 | -46.05 | 0 | 0 | 0 | Battery-supported
2025-09-28 16:00 | 271 | 9 | Spring | 16 | 13.12 | -15.9 | 16.72 | 16.4 | 330.9 | 19.85 | 120 | 139.85 | 15.9 | 58.97 | 87.13 | 80.88 | 0 | 0 | 0 | Normal
2025-09-28 17:00 | 271 | 9 | Spring | 17 | 13.12 | -13.6 | 7.5 | 72.4 | 109.4 | 6.56 | 8.96 | 15.52 | 13.6 | 59.47 | 69.55 | -43.95 | 0 | 0 | 0 | Battery-supported
2025-09-28 18:00 | 271 | 9 | Spring | 18 | 13.12 | -14.3 | 9.64 | 54.7 | 51.7 | 3.1 | 32.4 | 35.5 | 14.3 | 56.42 | 61.18 | -20.92 | 0 | 0 | 0 | Battery-supported
2025-09-28 19:00 | 271 | 9 | Spring | 19 | 13.12 | -10.3 | 15.08 | 53.4 | 0 | 0 | 120 | 120 | 10.3 | 48.88 | 87.35 | 71.12 | 0 | 0 | 0 | Normal
2025-09-28 20:00 | 271 | 9 | Spring | 20 | 13.12 | -12.4 | 16.42 | 86.7 | 0 | 0 | 120 | 120 | 12.4 | 59.24 | 95 | 20.78 | 0 | 0 | 0 | Normal
2025-09-28 21:00 | 271 | 9 | Spring | 21 | 13.12 | -12 | 14.58 | 39.5 | 0 | 0 | 120 | 120 | 12 | 45.24 | 95 | 0 | 0 | 0 | 0 | Normal
2025-09-28 22:00 | 271 | 9 | Spring | 22 | 13.12 | -9.2 | 22.33 | 66.7 | 0 | 0 | 120 | 120 | 9.2 | 45.32 | 95 | 0 | 0 | 0 | 0 | Normal
2025-09-28 23:00 | 271 | 9 | Spring | 23 | 13.12 | -13.9 | 9.01 | 66.3 | 0 | 0 | 23.41 | 23.41 | 13.9 | 51.95 | 83.58 | -28.54 | 0 | 0 | 0 | Battery-supported
2025-09-29 | 272 | 9 | Spring | 0 | 13.27 | -15.3 | 6.02 | 19.8 | 0 | 0 | 2.24 | 2.24 | 15.3 | 46.02 | 66.07 | -43.78 | 0 | 0 | 0 | Battery-supported
2025-09-29 01:00 | 272 | 9 | Spring | 1 | 13.27 | -13.9 | 4.91 | 8 | 0 | 0 | 0.39 | 0.39 | 13.9 | 45.63 | 47.98 | -45.24 | 0 | 0 | 0 | Battery-supported
2025-09-29 02:00 | 272 | 9 | Spring | 2 | 13.27 | -17.6 | 6.25 | 22.4 | 0 | 0 | 2.91 | 2.91 | 17.6 | 46.88 | 30.39 | -43.97 | 0 | 0 | 0 | Battery-supported
2025-09-29 03:00 | 272 | 9 | Spring | 3 | 13.27 | -16.6 | 6.41 | 56.7 | 0 | 0 | 3.45 | 3.45 | 16.6 | 50.21 | 15 | -38.47 | 8.29 | 3.042 | 0 | Diesel-backup
2025-09-29 04:00 | 272 | 9 | Spring | 4 | 13.27 | -18.6 | 10.52 | 34.1 | 0 | 0 | 48.42 | 48.42 | 18.6 | 57.83 | 15 | 0 | 9.41 | 3.44 | 0 | Diesel-backup
2025-09-29 05:00 | 272 | 9 | Spring | 5 | 13.27 | -16.6 | 12.73 | 21 | 0 | 0 | 110.06 | 110.06 | 16.6 | 51.5 | 36.55 | 58.56 | 0 | 0 | 0 | Normal
2025-09-29 06:00 | 272 | 9 | Spring | 6 | 13.27 | -19.1 | 4.44 | 60.1 | 54.1 | 2.76 | 0.12 | 2.88 | 19.1 | 59.75 | 15 | -53.88 | 2.99 | 1.119 | 0 | Diesel-backup
2025-09-29 07:00 | 272 | 9 | Spring | 7 | 13.27 | -19.4 | 15.06 | 57.7 | 140.5 | 7.17 | 120 | 127.17 | 19.4 | 55.7 | 41.3 | 71.47 | 0 | 0 | 0 | Normal
2025-09-29 08:00 | 272 | 9 | Spring | 8 | 13.27 | -17 | 15.9 | 51.6 | 235 | 14.1 | 120 | 134.1 | 17 | 57.72 | 69.41 | 76.38 | 0 | 0 | 0 | Normal
2025-09-29 09:00 | 272 | 9 | Spring | 9 | 13.27 | -18.2 | 1.26 | 63.4 | 260.9 | 13.31 | 0 | 13.31 | 18.2 | 58.47 | 51.34 | -45.16 | 0 | 0 | 0 | Battery-supported
2025-09-29 10:00 | 272 | 9 | Spring | 10 | 13.27 | -22 | 12.91 | 15.2 | 517.3 | 26.38 | 116.62 | 143 | 22 | 71.33 | 77.72 | 71.67 | 0 | 0 | 0 | Normal
2025-09-29 11:00 | 272 | 9 | Spring | 11 | 13.27 | -20.7 | 6.84 | 36.6 | 462.7 | 23.6 | 5.21 | 28.81 | 20.7 | 66.82 | 62.52 | -38.01 | 0 | 0 | 0 | Battery-supported
2025-09-29 12:00 | 272 | 9 | Spring | 12 | 13.27 | -19.7 | 18.81 | 39.7 | 460.8 | 23.5 | 120 | 143.5 | 19.7 | 61.98 | 92.51 | 81.52 | 0 | 0 | 0 | Normal
2025-09-29 13:00 | 272 | 9 | Spring | 13 | 13.27 | -18.7 | 8.88 | 51 | 393.9 | 20.09 | 21.8 | 41.89 | 18.7 | 62.24 | 84.37 | -20.35 | 0 | 0 | 0 | Battery-supported
2025-09-29 14:00 | 272 | 9 | Spring | 14 | 13.27 | -15.5 | 5.54 | 65 | 299.1 | 17.95 | 1.19 | 19.14 | 15.5 | 56.72 | 69.34 | -37.58 | 0 | 0 | 0 | Battery-supported
2025-09-29 15:00 | 272 | 9 | Spring | 15 | 13.27 | -15.5 | 4.41 | 22.1 | 415 | 24.9 | 0.11 | 25.01 | 15.5 | 48.4 | 59.99 | -23.39 | 0 | 0 | 0 | Battery-supported
2025-09-29 16:00 | 272 | 9 | Spring | 16 | 13.27 | -13.3 | 10.01 | 69.5 | 183.5 | 11.01 | 38.61 | 49.62 | 13.3 | 56.65 | 57.17 | -7.03 | 0 | 0 | 0 | Battery-supported
2025-09-29 17:00 | 272 | 9 | Spring | 17 | 13.27 | -13.7 | 6.92 | 28.3 | 195.1 | 11.71 | 5.6 | 17.31 | 13.7 | 51.72 | 43.41 | -34.41 | 0 | 0 | 0 | Battery-supported
2025-09-29 18:00 | 272 | 9 | Spring | 18 | 13.27 | -12.8 | 3.61 | 65.7 | 49.9 | 2.99 | 0 | 2.99 | 12.8 | 54.35 | 22.87 | -51.36 | 0 | 0 | 0 | Battery-supported
2025-09-29 19:00 | 272 | 9 | Spring | 19 | 13.27 | -13.6 | 2.89 | 47.7 | 0 | 0 | 0 | 0 | 13.6 | 51.56 | 15 | -19.67 | 31.89 | 10.741 | 0 | Diesel-backup
2025-09-29 20:00 | 272 | 9 | Spring | 20 | 13.27 | -14.5 | 10.92 | 25.5 | 0 | 0 | 57.18 | 57.18 | 14.5 | 56.76 | 15.15 | 0.42 | 0 | 0 | 0 | Normal
2025-09-29 21:00 | 272 | 9 | Spring | 21 | 13.27 | -12.5 | 3.23 | 13.3 | 0 | 0 | 0 | 0 | 12.5 | 45 | 15 | -0.39 | 44.61 | 14.298 | 0 | Diesel-backup
2025-09-29 22:00 | 272 | 9 | Spring | 22 | 13.27 | -13.1 | 1.44 | 60.3 | 0 | 0 | 0 | 0 | 13.1 | 48.37 | 15 | 0 | 48.37 | 15.478 | 0 | Diesel-backup
2025-09-29 23:00 | 272 | 9 | Spring | 23 | 13.27 | -14.5 | 16.03 | 71.6 | 0 | 0 | 120 | 120 | 14.5 | 52.28 | 39.92 | 67.72 | 0 | 0 | 0 | Normal
2025-09-30 | 273 | 9 | Spring | 0 | 13.43 | -12.7 | 4.79 | 38.5 | 0 | 0 | 0.3 | 0.3 | 12.7 | 48.95 | 20.46 | -48.65 | 0 | 0 | 0 | Battery-supported
2025-09-30 01:00 | 273 | 9 | Spring | 1 | 13.43 | -21 | 11.92 | 51.8 | 0 | 0 | 83.55 | 83.55 | 21 | 50.11 | 32.77 | 33.44 | 0 | 0 | 0 | Normal
2025-09-30 02:00 | 273 | 9 | Spring | 2 | 13.43 | -16.9 | 9.85 | 27.6 | 0 | 0 | 35.84 | 35.84 | 16.9 | 45.24 | 29.01 | -9.4 | 0 | 0 | 0 | Battery-supported
2025-09-30 03:00 | 273 | 9 | Spring | 3 | 13.43 | -17.3 | 5.91 | 58.2 | 0 | 0 | 1.96 | 1.96 | 17.3 | 47.17 | 15 | -35.02 | 10.19 | 3.716 | 0 | Diesel-backup
2025-09-30 04:00 | 273 | 9 | Spring | 4 | 13.43 | -14.4 | 19.95 | 90.5 | 0 | 0 | 120 | 120 | 14.4 | 53.5 | 39.47 | 66.5 | 0 | 0 | 0 | Normal
2025-09-30 05:00 | 273 | 9 | Spring | 5 | 13.43 | -13.8 | 13.04 | 62.1 | 0 | 0 | 120 | 120 | 13.8 | 57.55 | 62.45 | 62.45 | 0 | 0 | 0 | Normal
2025-09-30 06:00 | 273 | 9 | Spring | 6 | 13.43 | -20.7 | 8.52 | 65.2 | 55.8 | 2.85 | 17.71 | 20.56 | 20.7 | 53.01 | 49.47 | -32.45 | 0 | 0 | 0 | Battery-supported
2025-09-30 07:00 | 273 | 9 | Spring | 7 | 13.43 | -14.6 | 5.09 | 23.1 | 211.7 | 12.7 | 0.56 | 13.26 | 14.6 | 45.51 | 36.57 | -32.25 | 0 | 0 | 0 | Battery-supported
2025-09-30 08:00 | 273 | 9 | Spring | 8 | 13.43 | -20.3 | 12.44 | 48.2 | 248.4 | 12.67 | 100.01 | 112.68 | 20.3 | 68.85 | 52.7 | 43.83 | 0 | 0 | 0 | Normal
2025-09-30 09:00 | 273 | 9 | Spring | 9 | 13.43 | -20.2 | 13.58 | 34.6 | 371 | 18.92 | 120 | 138.92 | 20.2 | 61.53 | 81.18 | 77.39 | 0 | 0 | 0 | Normal
2025-09-30 10:00 | 273 | 9 | Spring | 10 | 13.43 | -18 | 9.32 | 21.2 | 492.2 | 29.53 | 27.59 | 57.12 | 18 | 60.68 | 79.76 | -3.56 | 0 | 0 | 0 | Battery-supported
2025-09-30 11:00 | 273 | 9 | Spring | 11 | 13.43 | -18 | 8.65 | 31.4 | 487.6 | 29.26 | 19.12 | 48.38 | 18 | 61.65 | 74.45 | -13.27 | 0 | 0 | 0 | Battery-supported
2025-09-30 12:00 | 273 | 9 | Spring | 12 | 13.43 | -20.4 | 13.02 | 78.6 | 269.1 | 13.72 | 120 | 133.72 | 20.4 | 60.66 | 95 | 55.84 | 0 | 0 | 0 | Normal
2025-09-30 13:00 | 273 | 9 | Spring | 13 | 13.43 | -15.2 | 8.39 | 37.5 | 458.8 | 27.53 | 16.37 | 43.9 | 15.2 | 55.1 | 90.52 | -11.2 | 0 | 0 | 0 | Battery-supported
2025-09-30 14:00 | 273 | 9 | Spring | 14 | 13.43 | -14.7 | 5.45 | 34 | 436.3 | 26.18 | 1.04 | 27.22 | 14.7 | 57.39 | 78.45 | -30.17 | 0 | 0 | 0 | Battery-supported
2025-09-30 15:00 | 273 | 9 | Spring | 15 | 13.43 | -13.5 | 3.4 | 46.5 | 326.3 | 19.58 | 0 | 19.58 | 13.5 | 54.86 | 64.34 | -35.28 | 0 | 0 | 0 | Battery-supported
2025-09-30 16:00 | 273 | 9 | Spring | 16 | 13.43 | -16.4 | 8.43 | 49.8 | 243.7 | 14.62 | 16.77 | 31.39 | 16.4 | 52.28 | 55.98 | -20.89 | 0 | 0 | 0 | Battery-supported
2025-09-30 17:00 | 273 | 9 | Spring | 17 | 13.43 | -15.2 | 3.32 | 34.8 | 189.3 | 11.36 | 0 | 11.36 | 15.2 | 54.61 | 38.68 | -43.25 | 0 | 0 | 0 | Battery-supported
2025-09-30 18:00 | 273 | 9 | Spring | 18 | 13.43 | -15 | 13.68 | 42.9 | 74 | 4.44 | 120 | 124.44 | 15 | 57.45 | 63.34 | 66.99 | 0 | 0 | 0 | Normal
2025-09-30 19:00 | 273 | 9 | Spring | 19 | 13.43 | -11.1 | 8.43 | 39.8 | 0 | 0 | 16.77 | 16.77 | 11.1 | 51.88 | 49.29 | -35.11 | 0 | 0 | 0 | Battery-supported
2025-09-30 20:00 | 273 | 9 | Spring | 20 | 13.43 | -20.9 | 14.89 | 60.4 | 0 | 0 | 120 | 120 | 20.9 | 65.89 | 69.2 | 54.11 | 0 | 0 | 0 | Normal
2025-09-30 21:00 | 273 | 9 | Spring | 21 | 13.43 | -16.9 | 10.3 | 10.9 | 0 | 0 | 44.01 | 44.01 | 16.9 | 48.78 | 67.3 | -4.77 | 0 | 0 | 0 | Battery-supported
2025-09-30 22:00 | 273 | 9 | Spring | 22 | 13.43 | -14.9 | 11.95 | 19.1 | 0 | 0 | 84.45 | 84.45 | 14.9 | 57.15 | 77.34 | 27.3 | 0 | 0 | 0 | Normal
2025-09-30 23:00 | 273 | 9 | Spring | 23 | 13.43 | -17.5 | 5.79 | 60 | 0 | 0 | 1.68 | 1.68 | 17.5 | 52.71 | 56.93 | -51.03 | 0 | 0 | 0 | Battery-supported
2025-10-01 | 274 | 10 | Spring | 0 | 13.58 | -15.8 | 8.07 | 23 | 0 | 0 | 13.36 | 13.36 | 15.8 | 51.1 | 41.84 | -37.74 | 0 | 0 | 0 | Battery-supported
2025-10-01 01:00 | 274 | 10 | Spring | 1 | 13.58 | -15.9 | 10.18 | 16.9 | 0 | 0 | 41.72 | 41.72 | 15.9 | 48.84 | 38.99 | -7.12 | 0 | 0 | 0 | Battery-supported
2025-10-01 02:00 | 274 | 10 | Spring | 2 | 13.58 | -17.5 | 9.5 | 7.3 | 0 | 0 | 30.23 | 30.23 | 17.5 | 51.44 | 30.5 | -21.21 | 0 | 0 | 0 | Battery-supported
2025-10-01 03:00 | 274 | 10 | Spring | 3 | 13.58 | -16.3 | 9.26 | 52.2 | 0 | 0 | 26.75 | 26.75 | 16.3 | 45 | 23.2 | -18.25 | 0 | 0 | 0 | Battery-supported
2025-10-01 04:00 | 274 | 10 | Spring | 4 | 13.58 | -15.4 | 4.35 | 45.5 | 0 | 0 | 0.09 | 0.09 | 15.4 | 50.4 | 15 | -20.51 | 29.8 | 10.116 | 0 | Diesel-backup
2025-10-01 05:00 | 274 | 10 | Spring | 5 | 13.58 | -17.6 | 2.35 | 33.5 | 0 | 0 | 0 | 0 | 17.6 | 60.47 | 15 | 0 | 60.47 | 19.35 | 0 | Diesel-backup
2025-10-01 06:00 | 274 | 10 | Spring | 6 | 13.58 | -18.3 | 4.14 | 55.8 | 69.5 | 3.54 | 0.04 | 3.58 | 18.3 | 56.89 | 15 | 0 | 53.31 | 17.059 | 0 | Diesel-backup
2025-10-01 07:00 | 274 | 10 | Spring | 7 | 13.58 | -17.8 | 1.12 | 87.7 | 90.5 | 5.43 | 0 | 5.43 | 17.8 | 46.27 | 15 | 0 | 40.84 | 13.286 | 0 | Diesel-backup
2025-10-01 08:00 | 274 | 10 | Spring | 8 | 13.58 | -17.5 | 2.62 | 33.4 | 295.8 | 17.75 | 0 | 17.75 | 17.5 | 61.66 | 15 | 0 | 43.91 | 14.112 | 0 | Diesel-backup
2025-10-01 09:00 | 274 | 10 | Spring | 9 | 13.58 | -21.3 | 10.62 | 7.1 | 477.5 | 24.35 | 50.52 | 74.87 | 21.3 | 66.08 | 18.23 | 8.79 | 0 | 0 | 0 | Normal
2025-10-01 10:00 | 274 | 10 | Spring | 10 | 13.58 | -16.3 | 7.44 | 53.2 | 352.8 | 21.17 | 8.56 | 29.73 | 16.3 | 65.37 | 15 | -8.09 | 27.55 | 9.432 | 0 | Diesel-backup
2025-10-01 11:00 | 274 | 10 | Spring | 11 | 13.58 | -18.1 | 5.22 | 13.7 | 572.9 | 29.22 | 0.71 | 29.93 | 18.1 | 57.95 | 15 | 0 | 28.02 | 9.575 | 0 | Diesel-backup
2025-10-01 12:00 | 274 | 10 | Spring | 12 | 13.58 | -14 | 7.35 | 42.8 | 445.4 | 26.72 | 7.99 | 34.71 | 14 | 66.14 | 15 | 0 | 31.43 | 10.604 | 0 | Diesel-backup
2025-10-01 13:00 | 274 | 10 | Spring | 13 | 13.58 | -15.1 | 1.97 | 54.6 | 377.2 | 22.63 | 0 | 22.63 | 15.1 | 58.55 | 15 | 0 | 35.92 | 11.912 | 0 | Diesel-backup
2025-10-01 14:00 | 274 | 10 | Spring | 14 | 13.58 | -13.4 | 8.28 | 46.4 | 382.9 | 22.97 | 15.29 | 38.26 | 13.4 | 53.08 | 15 | 0 | 14.82 | 5.315 | 0 | Diesel-backup
2025-10-01 15:00 | 274 | 10 | Spring | 15 | 13.58 | -17.9 | 3.57 | 65.9 | 255.1 | 15.31 | 0 | 15.31 | 17.9 | 54.37 | 15 | 0 | 39.06 | 12.796 | 0 | Diesel-backup
2025-10-01 16:00 | 274 | 10 | Spring | 16 | 13.58 | -16.1 | 17.19 | 40.6 | 274.6 | 16.48 | 120 | 136.48 | 16.1 | 58.62 | 43.65 | 77.86 | 0 | 0 | 0 | Normal
2025-10-01 17:00 | 274 | 10 | Spring | 17 | 13.58 | -17.7 | 12.23 | 55.9 | 153.4 | 9.2 | 93.12 | 102.32 | 17.7 | 61.53 | 58.66 | 40.79 | 0 | 0 | 0 | Normal
2025-10-01 18:00 | 274 | 10 | Spring | 18 | 13.58 | -16.3 | 11.62 | 38.5 | 85 | 5.1 | 74.93 | 80.03 | 16.3 | 54.73 | 67.97 | 25.3 | 0 | 0 | 0 | Normal
2025-10-01 19:00 | 274 | 10 | Spring | 19 | 13.58 | -11.8 | 9.4 | 89 | 0 | 0 | 28.75 | 28.75 | 11.8 | 57.3 | 56.55 | -28.55 | 0 | 0 | 0 | Battery-supported
2025-10-01 20:00 | 274 | 10 | Spring | 20 | 13.58 | -11.2 | 12.84 | 95.8 | 0 | 0 | 114.04 | 114.04 | 11.2 | 56.31 | 77.8 | 57.73 | 0 | 0 | 0 | Normal
2025-10-01 21:00 | 274 | 10 | Spring | 21 | 13.58 | -17.1 | 8.31 | 90.5 | 0 | 0 | 15.58 | 15.58 | 17.1 | 52.13 | 63.18 | -36.55 | 0 | 0 | 0 | Battery-supported
2025-10-01 22:00 | 274 | 10 | Spring | 22 | 13.58 | -15.7 | 5.13 | 23.3 | 0 | 0 | 0.61 | 0.61 | 15.7 | 47.27 | 44.51 | -46.66 | 0 | 0 | 0 | Battery-supported
2025-10-01 23:00 | 274 | 10 | Spring | 23 | 13.58 | -15.1 | 11.74 | 73.3 | 0 | 0 | 78.31 | 78.31 | 15.1 | 50.18 | 54.87 | 28.13 | 0 | 0 | 0 | Normal
2025-10-02 | 275 | 10 | Spring | 0 | 13.74 | -13.8 | 15.26 | 80.4 | 0 | 0 | 120 | 120 | 13.8 | 56.17 | 78.36 | 63.83 | 0 | 0 | 0 | Normal
2025-10-02 01:00 | 275 | 10 | Spring | 1 | 13.74 | -19.3 | 4.5 | 30.9 | 0 | 0 | 0.14 | 0.14 | 19.3 | 50.6 | 58.17 | -50.46 | 0 | 0 | 0 | Battery-supported
2025-10-02 02:00 | 275 | 10 | Spring | 2 | 13.74 | -19.3 | 2.88 | 16.8 | 0 | 0 | 0 | 0 | 19.3 | 47.27 | 39.26 | -47.27 | 0 | 0 | 0 | Battery-supported
2025-10-02 03:00 | 275 | 10 | Spring | 3 | 13.74 | -15.1 | 23.18 | 73 | 0 | 0 | 120 | 120 | 15.1 | 48.61 | 65.54 | 71.39 | 0 | 0 | 0 | Normal
2025-10-02 04:00 | 275 | 10 | Spring | 4 | 13.74 | -20.9 | 18.36 | 73.2 | 0 | 0 | 120 | 120 | 20.9 | 52.66 | 90.32 | 67.34 | 0 | 0 | 0 | Normal
2025-10-02 05:00 | 275 | 10 | Spring | 5 | 13.74 | -17.9 | 8.82 | 47.8 | 0 | 0 | 21.07 | 21.07 | 17.9 | 45.49 | 80.55 | -24.42 | 0 | 0 | 0 | Battery-supported
2025-10-02 06:00 | 275 | 10 | Spring | 6 | 13.74 | -16.8 | 1.62 | 49.7 | 81.4 | 4.88 | 0 | 4.88 | 16.8 | 53.43 | 61.13 | -48.55 | 0 | 0 | 0 | Battery-supported
2025-10-02 07:00 | 275 | 10 | Spring | 7 | 13.74 | -16.3 | 10.18 | 12.5 | 246.4 | 14.78 | 41.72 | 56.5 | 16.3 | 46.02 | 64.98 | 10.48 | 0 | 0 | 0 | Normal
2025-10-02 08:00 | 275 | 10 | Spring | 8 | 13.74 | -17.6 | 30.11 | 56.4 | 230.9 | 13.85 | 0 | 13.85 | 17.6 | 54.91 | 48.56 | -41.06 | 0 | 0 | 0 | Battery-supported
2025-10-02 09:00 | 275 | 10 | Spring | 9 | 13.74 | -18.1 | 12.74 | 22.4 | 422.2 | 21.53 | 110.41 | 131.94 | 18.1 | 64.38 | 73.42 | 67.56 | 0 | 0 | 0 | Normal
2025-10-02 10:00 | 275 | 10 | Spring | 10 | 13.74 | -15.3 | 12.13 | 57.7 | 333.8 | 20.03 | 89.96 | 109.99 | 15.3 | 63.9 | 90.38 | 46.09 | 0 | 0 | 0 | Normal
2025-10-02 11:00 | 275 | 10 | Spring | 11 | 13.74 | -16.2 | 8.43 | 22.2 | 532.4 | 31.94 | 16.77 | 48.71 | 16.2 | 69.55 | 82.05 | -20.84 | 0 | 0 | 0 | Battery-supported
2025-10-02 12:00 | 275 | 10 | Spring | 12 | 13.74 | -18 | 11.5 | 57.3 | 374 | 22.44 | 71.66 | 94.1 | 18 | 54.77 | 95 | 35.2 | 0 | 0 | 0 | Normal
2025-10-02 13:00 | 275 | 10 | Spring | 13 | 13.74 | -16.1 | 12.7 | 59.1 | 355.8 | 21.35 | 108.99 | 130.34 | 16.1 | 60.67 | 95 | 0 | 0 | 0 | 0 | Normal
2025-10-02 14:00 | 275 | 10 | Spring | 14 | 13.74 | -15 | 9.68 | 74.3 | 260.4 | 15.62 | 33.04 | 48.66 | 15 | 52.39 | 93.51 | -3.73 | 0 | 0 | 0 | Battery-supported
2025-10-02 15:00 | 275 | 10 | Spring | 15 | 13.74 | -11.6 | 7.7 | 36.4 | 368.9 | 22.13 | 10.37 | 32.5 | 11.6 | 54.89 | 84.55 | -22.39 | 0 | 0 | 0 | Battery-supported
2025-10-02 16:00 | 275 | 10 | Spring | 16 | 13.74 | -13.3 | 9.78 | 28.8 | 313.6 | 18.82 | 34.66 | 53.48 | 13.3 | 55.67 | 83.68 | -2.19 | 0 | 0 | 0 | Battery-supported
2025-10-02 17:00 | 275 | 10 | Spring | 17 | 13.74 | -12.1 | 9.51 | 19.2 | 232.9 | 13.97 | 30.38 | 44.35 | 12.1 | 46.53 | 82.8 | -2.18 | 0 | 0 | 0 | Battery-supported
2025-10-02 18:00 | 275 | 10 | Spring | 18 | 13.74 | -15.9 | 1.87 | 25.9 | 104.5 | 6.27 | 0 | 6.27 | 15.9 | 61.01 | 60.91 | -54.74 | 0 | 0 | 0 | Battery-supported
2025-10-02 19:00 | 275 | 10 | Spring | 19 | 13.74 | -15.5 | 26.88 | 27.2 | 0 | 0 | 120 | 120 | 15.5 | 58.49 | 83.54 | 61.51 | 0 | 0 | 0 | Normal
2025-10-02 20:00 | 275 | 10 | Spring | 20 | 13.74 | -14.8 | 12.14 | 55.6 | 0 | 0 | 90.27 | 90.27 | 14.8 | 60.22 | 94.6 | 30.05 | 0 | 0 | 0 | Normal
2025-10-02 21:00 | 275 | 10 | Spring | 21 | 13.74 | -14.7 | 16.75 | 73.7 | 0 | 0 | 120 | 120 | 14.7 | 45 | 95 | 1.08 | 0 | 0 | 0 | Normal
2025-10-02 22:00 | 275 | 10 | Spring | 22 | 13.74 | -16.7 | 10.39 | 38.3 | 0 | 0 | 45.78 | 45.78 | 16.7 | 60.16 | 89.25 | -14.38 | 0 | 0 | 0 | Battery-supported
2025-10-02 23:00 | 275 | 10 | Spring | 23 | 13.74 | -12 | 6.29 | 29.1 | 0 | 0 | 3.04 | 3.04 | 12 | 48.06 | 71.24 | -45.02 | 0 | 0 | 0 | Battery-supported
2025-10-03 | 276 | 10 | Spring | 0 | 13.9 | -12.9 | 14.7 | 59.1 | 0 | 0 | 120 | 120 | 12.9 | 49.23 | 95 | 64.57 | 0 | 0 | 0 | Normal
2025-10-03 01:00 | 276 | 10 | Spring | 1 | 13.9 | -15.9 | 2.75 | 55.5 | 0 | 0 | 0 | 0 | 15.9 | 56.42 | 72.43 | -56.42 | 0 | 0 | 0 | Battery-supported
2025-10-03 02:00 | 276 | 10 | Spring | 2 | 13.9 | -14.2 | 12.38 | 43.1 | 0 | 0 | 98.01 | 98.01 | 14.2 | 49.14 | 90.42 | 48.87 | 0 | 0 | 0 | Normal
2025-10-03 03:00 | 276 | 10 | Spring | 3 | 13.9 | -15.5 | 14.61 | 83.9 | 0 | 0 | 120 | 120 | 15.5 | 46.92 | 95 | 12.46 | 0 | 0 | 0 | Normal
2025-10-03 04:00 | 276 | 10 | Spring | 4 | 13.9 | -14.8 | 8.31 | 21.7 | 0 | 0 | 15.58 | 15.58 | 14.8 | 54.16 | 79.57 | -38.58 | 0 | 0 | 0 | Battery-supported
2025-10-03 05:00 | 276 | 10 | Spring | 5 | 13.9 | -19.6 | 11.69 | 25.2 | 0 | 0 | 76.89 | 76.89 | 19.6 | 54 | 87.99 | 22.89 | 0 | 0 | 0 | Normal
2025-10-03 06:00 | 276 | 10 | Spring | 6 | 13.9 | -17.2 | 1.89 | 51.2 | 86 | 5.16 | 0 | 5.16 | 17.2 | 56.06 | 67.63 | -50.9 | 0 | 0 | 0 | Battery-supported
2025-10-03 07:00 | 276 | 10 | Spring | 7 | 13.9 | -17.2 | 12 | 27.9 | 221.2 | 13.27 | 85.95 | 99.22 | 17.2 | 51.73 | 85.11 | 47.49 | 0 | 0 | 0 | Normal
2025-10-03 08:00 | 276 | 10 | Spring | 8 | 13.9 | -15.7 | 7.03 | 42 | 277.7 | 16.66 | 6.16 | 22.82 | 15.7 | 67.38 | 67.28 | -44.56 | 0 | 0 | 0 | Battery-supported
2025-10-03 09:00 | 276 | 10 | Spring | 9 | 13.9 | -18.4 | 11.73 | 57.1 | 292.2 | 14.9 | 78.02 | 92.92 | 18.4 | 61.18 | 78.96 | 31.74 | 0 | 0 | 0 | Normal
2025-10-03 10:00 | 276 | 10 | Spring | 10 | 13.9 | -22.4 | 8.54 | 48.9 | 373.5 | 19.05 | 17.92 | 36.97 | 22.4 | 62.84 | 68.62 | -25.87 | 0 | 0 | 0 | Battery-supported
2025-10-03 11:00 | 276 | 10 | Spring | 11 | 13.9 | -19.1 | 8.47 | 5 | 615.1 | 31.37 | 17.18 | 48.55 | 19.1 | 63.4 | 62.68 | -14.85 | 0 | 0 | 0 | Battery-supported
2025-10-03 12:00 | 276 | 10 | Spring | 12 | 13.9 | -16.5 | 11.94 | 81.5 | 254.9 | 15.29 | 84.15 | 99.44 | 16.5 | 57.55 | 78.09 | 41.89 | 0 | 0 | 0 | Normal
2025-10-03 13:00 | 276 | 10 | Spring | 13 | 13.9 | -15.9 | 7.25 | 15.2 | 566.6 | 34 | 7.38 | 41.38 | 15.9 | 55.37 | 72.5 | -13.99 | 0 | 0 | 0 | Battery-supported
2025-10-03 14:00 | 276 | 10 | Spring | 14 | 13.9 | -11.9 | 8.28 | 48.7 | 374.5 | 22.47 | 15.29 | 37.76 | 11.9 | 60.23 | 63.51 | -22.47 | 0 | 0 | 0 | Battery-supported
2025-10-03 15:00 | 276 | 10 | Spring | 15 | 13.9 | -13.9 | 23.67 | 29.5 | 397.7 | 23.86 | 120 | 143.86 | 13.9 | 51.74 | 95 | 85.58 | 0 | 0 | 0 | Normal
2025-10-03 16:00 | 276 | 10 | Spring | 16 | 13.9 | -14.7 | 17.32 | 49.4 | 255.5 | 15.33 | 120 | 135.33 | 14.7 | 61.76 | 95 | 0 | 0 | 0 | 0 | Normal
2025-10-03 17:00 | 276 | 10 | Spring | 17 | 13.9 | -14.6 | 7.67 | 67.5 | 138 | 8.28 | 10.15 | 18.43 | 14.6 | 63.95 | 76.79 | -45.52 | 0 | 0 | 0 | Battery-supported
2025-10-03 18:00 | 276 | 10 | Spring | 18 | 13.9 | -11.9 | 8.64 | 33.1 | 104.9 | 6.29 | 19.01 | 25.3 | 11.9 | 53.47 | 65.52 | -28.17 | 0 | 0 | 0 | Battery-supported
2025-10-03 19:00 | 276 | 10 | Spring | 19 | 13.9 | -15.5 | 5.99 | 29.6 | 0 | 0 | 2.16 | 2.16 | 15.5 | 59.51 | 42.58 | -57.35 | 0 | 0 | 0 | Battery-supported
2025-10-03 20:00 | 276 | 10 | Spring | 20 | 13.9 | -14.4 | 7.05 | 76.8 | 0 | 0 | 6.26 | 6.26 | 14.4 | 54 | 23.49 | -47.74 | 0 | 0 | 0 | Battery-supported
2025-10-03 21:00 | 276 | 10 | Spring | 21 | 13.9 | -16.6 | 7.26 | 46.1 | 0 | 0 | 7.44 | 7.44 | 16.6 | 56.11 | 15 | -21.22 | 27.45 | 9.401 | 0 | Diesel-backup
2025-10-03 22:00 | 276 | 10 | Spring | 22 | 13.9 | -11.2 | 9.37 | 39 | 0 | 0 | 28.31 | 28.31 | 11.2 | 45 | 15 | 0 | 16.69 | 5.946 | 0 | Diesel-backup
2025-10-03 23:00 | 276 | 10 | Spring | 23 | 13.9 | -13.7 | 2.09 | 45.8 | 0 | 0 | 0 | 0 | 13.7 | 52.61 | 15 | 0 | 52.61 | 16.835 | 0 | Diesel-backup
2025-10-04 | 277 | 10 | Spring | 0 | 14.05 | -16.2 | 6.9 | 46.7 | 0 | 0 | 5.5 | 5.5 | 16.2 | 51.15 | 15 | 0 | 45.65 | 14.608 | 0 | Diesel-backup
2025-10-04 01:00 | 277 | 10 | Spring | 1 | 14.05 | -15.3 | 6.2 | 68.3 | 0 | 0 | 2.75 | 2.75 | 15.3 | 46.82 | 15 | 0 | 44.07 | 14.155 | 0 | Diesel-backup
2025-10-04 02:00 | 277 | 10 | Spring | 2 | 14.05 | -14.3 | 18.56 | 51.8 | 0 | 0 | 120 | 120 | 14.3 | 46.42 | 42.08 | 73.58 | 0 | 0 | 0 | Normal
2025-10-04 03:00 | 277 | 10 | Spring | 3 | 14.05 | -16.4 | 8.55 | 70.8 | 0 | 0 | 18.03 | 18.03 | 16.4 | 53.27 | 27.98 | -35.24 | 0 | 0 | 0 | Battery-supported
2025-10-04 04:00 | 277 | 10 | Spring | 4 | 14.05 | -17.3 | 10.09 | 12.1 | 0 | 0 | 40.06 | 40.06 | 17.3 | 47.44 | 25.03 | -7.38 | 0 | 0 | 0 | Battery-supported
2025-10-04 05:00 | 277 | 10 | Spring | 5 | 14.05 | -17.9 | 6.78 | 33.1 | 3 | 0.18 | 4.94 | 5.12 | 17.9 | 55 | 15 | -25.07 | 24.81 | 8.579 | 0 | Diesel-backup
2025-10-04 06:00 | 277 | 10 | Spring | 6 | 14.05 | -16 | 8.59 | 93.1 | 45 | 2.7 | 18.46 | 21.16 | 16 | 51.59 | 15 | 0 | 30.43 | 10.305 | 0 | Diesel-backup
2025-10-04 07:00 | 277 | 10 | Spring | 7 | 14.05 | -17.6 | 7.02 | 96.3 | 79.7 | 4.78 | 6.1 | 10.88 | 17.6 | 50.92 | 15 | 0 | 40.04 | 13.067 | 0 | Diesel-backup
2025-10-04 08:00 | 277 | 10 | Spring | 8 | 14.05 | -17.9 | 9.42 | 43 | 278.2 | 16.69 | 29.04 | 45.73 | 17.9 | 62.75 | 15 | 0 | 17.02 | 6.056 | 0 | Diesel-backup
2025-10-04 09:00 | 277 | 10 | Spring | 9 | 14.05 | -19.8 | 11.64 | 0 | 513.9 | 26.21 | 75.49 | 101.7 | 19.8 | 59.5 | 30.53 | 42.2 | 0 | 0 | 0 | Normal
2025-10-04 10:00 | 277 | 10 | Spring | 10 | 14.05 | -16.5 | 3.64 | 17 | 515.9 | 30.95 | 0 | 30.95 | 16.5 | 58.29 | 19.59 | -27.34 | 0 | 0 | 0 | Battery-supported
2025-10-04 11:00 | 277 | 10 | Spring | 11 | 14.05 | -16.9 | 12.59 | 33.5 | 479.1 | 28.75 | 105.12 | 133.87 | 16.9 | 58.25 | 47.42 | 75.62 | 0 | 0 | 0 | Normal
2025-10-04 12:00 | 277 | 10 | Spring | 12 | 14.05 | -16.9 | 4.78 | 7.2 | 620.7 | 37.24 | 0.29 | 37.53 | 16.9 | 54.72 | 40.55 | -17.19 | 0 | 0 | 0 | Battery-supported
2025-10-04 13:00 | 277 | 10 | Spring | 13 | 14.05 | -15.4 | 24.06 | 90.6 | 204.9 | 12.29 | 120 | 132.29 | 15.4 | 56.96 | 68.27 | 75.33 | 0 | 0 | 0 | Normal
2025-10-04 14:00 | 277 | 10 | Spring | 14 | 14.05 | -13.8 | 9.3 | 53 | 356.4 | 21.38 | 27.31 | 48.69 | 13.8 | 50.43 | 67.57 | -1.74 | 0 | 0 | 0 | Battery-supported
2025-10-04 15:00 | 277 | 10 | Spring | 15 | 14.05 | -13.5 | 10.01 | 21.5 | 430.9 | 25.85 | 38.61 | 64.46 | 13.5 | 54.16 | 71.36 | 10.3 | 0 | 0 | 0 | Normal
2025-10-04 16:00 | 277 | 10 | Spring | 16 | 14.05 | -13.4 | 10.24 | 49.6 | 257.9 | 15.47 | 42.85 | 58.32 | 13.4 | 49.38 | 74.65 | 8.94 | 0 | 0 | 0 | Normal
2025-10-04 17:00 | 277 | 10 | Spring | 17 | 14.05 | -14.9 | 8.96 | 41.5 | 197.8 | 11.87 | 22.78 | 34.65 | 14.9 | 53.71 | 67.03 | -19.06 | 0 | 0 | 0 | Battery-supported
2025-10-04 18:00 | 277 | 10 | Spring | 18 | 14.05 | -15.4 | 5.61 | 39.3 | 105.3 | 6.32 | 1.31 | 7.63 | 15.4 | 54.6 | 48.24 | -46.97 | 0 | 0 | 0 | Battery-supported
2025-10-04 19:00 | 277 | 10 | Spring | 19 | 14.05 | -16.3 | 10.03 | 77.8 | 1.7 | 0.1 | 38.97 | 39.07 | 16.3 | 60.86 | 39.52 | -21.79 | 0 | 0 | 0 | Battery-supported
2025-10-04 20:00 | 277 | 10 | Spring | 20 | 14.05 | -15.2 | 9.7 | 52.3 | 0 | 0 | 33.36 | 33.36 | 15.2 | 54.26 | 31.16 | -20.9 | 0 | 0 | 0 | Battery-supported
2025-10-04 21:00 | 277 | 10 | Spring | 21 | 14.05 | -13.9 | 5.19 | 66 | 0 | 0 | 0.68 | 0.68 | 13.9 | 45 | 15 | -40.41 | 3.91 | 1.457 | 0 | Diesel-backup
2025-10-04 22:00 | 277 | 10 | Spring | 22 | 14.05 | -15.8 | 3.67 | 20.7 | 0 | 0 | 0 | 0 | 15.8 | 49.16 | 15 | 0 | 49.16 | 15.731 | 0 | Diesel-backup
2025-10-04 23:00 | 277 | 10 | Spring | 23 | 14.05 | -14.1 | 14.6 | 22 | 0 | 0 | 120 | 120 | 14.1 | 56.59 | 38.33 | 63.41 | 0 | 0 | 0 | Normal
2025-10-05 | 278 | 10 | Spring | 0 | 14.21 | -16.6 | 6.87 | 43.7 | 0 | 0 | 5.36 | 5.36 | 16.6 | 45 | 22.48 | -39.64 | 0 | 0 | 0 | Battery-supported
2025-10-05 01:00 | 278 | 10 | Spring | 1 | 14.21 | -18.5 | 7.89 | 36.9 | 0 | 0 | 11.84 | 11.84 | 18.5 | 56.19 | 15 | -18.7 | 25.65 | 8.844 | 0 | Diesel-backup
2025-10-05 02:00 | 278 | 10 | Spring | 2 | 14.21 | -13.4 | 9.69 | 32.8 | 0 | 0 | 33.2 | 33.2 | 13.4 | 49.71 | 15 | 0 | 16.51 | 5.885 | 0 | Diesel-backup
2025-10-05 03:00 | 278 | 10 | Spring | 3 | 14.21 | -16.6 | 5.5 | 59.7 | 0 | 0 | 1.12 | 1.12 | 16.6 | 59.86 | 15 | 0 | 58.74 | 18.797 | 0 | Diesel-backup
2025-10-05 04:00 | 278 | 10 | Spring | 4 | 14.21 | -17.8 | 10.5 | 49.4 | 0 | 0 | 48.01 | 48.01 | 17.8 | 53.88 | 15 | 0 | 5.87 | 2.172 | 0 | Diesel-backup
2025-10-05 05:00 | 278 | 10 | Spring | 5 | 14.21 | -18.7 | 8.12 | 66.5 | 7.7 | 0.39 | 13.8 | 14.19 | 18.7 | 53.79 | 15 | 0 | 39.6 | 12.946 | 0 | Diesel-backup
2025-10-05 06:00 | 278 | 10 | Spring | 6 | 14.21 | -15.6 | 8.58 | 66.5 | 79.6 | 4.78 | 18.35 | 23.13 | 15.6 | 50.67 | 15 | 0 | 27.54 | 9.428 | 0 | Diesel-backup
2025-10-05 07:00 | 278 | 10 | Spring | 7 | 14.21 | -13.6 | 16.16 | 71.2 | 137.2 | 8.23 | 120 | 128.23 | 13.6 | 48.37 | 44.39 | 79.86 | 0 | 0 | 0 | Normal
2025-10-05 08:00 | 278 | 10 | Spring | 8 | 14.21 | -17.6 | 9.48 | 85 | 150.8 | 9.05 | 29.93 | 38.98 | 17.6 | 63.33 | 34.65 | -24.35 | 0 | 0 | 0 | Battery-supported
2025-10-05 09:00 | 278 | 10 | Spring | 9 | 14.21 | -17.1 | 7.67 | 42.3 | 352.9 | 21.17 | 10.15 | 31.32 | 17.1 | 57.88 | 24.02 | -26.56 | 0 | 0 | 0 | Battery-supported
2025-10-05 10:00 | 278 | 10 | Spring | 10 | 14.21 | -14.1 | 4.49 | 52.2 | 361 | 21.66 | 0.14 | 21.8 | 14.1 | 69.17 | 15 | -22.56 | 24.81 | 8.58 | 0 | Diesel-backup
2025-10-05 11:00 | 278 | 10 | Spring | 11 | 14.21 | -20.3 | 10.18 | 59.1 | 356.1 | 18.16 | 41.72 | 59.88 | 20.3 | 66.66 | 15 | 0 | 6.78 | 2.501 | 0 | Diesel-backup
2025-10-05 12:00 | 278 | 10 | Spring | 12 | 14.21 | -11.6 | 14.21 | 56.9 | 376 | 22.56 | 120 | 142.56 | 11.6 | 53.76 | 47.68 | 88.8 | 0 | 0 | 0 | Normal
2025-10-05 13:00 | 278 | 10 | Spring | 13 | 14.21 | -10.2 | 7.75 | 57.5 | 363.8 | 21.83 | 10.74 | 32.57 | 10.2 | 52.12 | 39.86 | -19.55 | 0 | 0 | 0 | Battery-supported
2025-10-05 14:00 | 278 | 10 | Spring | 14 | 14.21 | -21.2 | 14.15 | 79.6 | 238.9 | 12.18 | 120 | 132.18 | 21.2 | 64.06 | 64.93 | 68.12 | 0 | 0 | 0 | Normal
2025-10-05 15:00 | 278 | 10 | Spring | 15 | 14.21 | -15 | 10.26 | 15.1 | 458.2 | 27.49 | 43.24 | 70.73 | 15 | 57.74 | 69.71 | 12.99 | 0 | 0 | 0 | Normal
2025-10-05 16:00 | 278 | 10 | Spring | 16 | 14.21 | -16 | 9.06 | 12.7 | 376.3 | 22.58 | 24.06 | 46.64 | 16 | 61.5 | 63.76 | -14.86 | 0 | 0 | 0 | Battery-supported
2025-10-05 17:00 | 278 | 10 | Spring | 17 | 14.21 | -14.7 | 10.98 | 2.9 | 287.9 | 17.27 | 58.58 | 75.85 | 14.7 | 58.82 | 70.03 | 17.03 | 0 | 0 | 0 | Normal
2025-10-05 18:00 | 278 | 10 | Spring | 18 | 14.21 | -14.8 | 3.76 | 15.1 | 140.8 | 8.45 | 0 | 8.45 | 14.8 | 63.59 | 47.97 | -55.14 | 0 | 0 | 0 | Battery-supported
2025-10-05 19:00 | 278 | 10 | Spring | 19 | 14.21 | -12 | 6.94 | 75.4 | 6.7 | 0.4 | 5.7 | 6.1 | 12 | 51.1 | 29.97 | -45 | 0 | 0 | 0 | Battery-supported
2025-10-05 20:00 | 278 | 10 | Spring | 20 | 14.21 | -14 | 7.1 | 24.9 | 0 | 0 | 6.53 | 6.53 | 14 | 56.81 | 15 | -37.43 | 12.85 | 4.639 | 0 | Diesel-backup
2025-10-05 21:00 | 278 | 10 | Spring | 21 | 14.21 | -15.8 | 7.95 | 19.6 | 0 | 0 | 12.33 | 12.33 | 15.8 | 46.86 | 15 | 0 | 34.53 | 11.512 | 0 | Diesel-backup
2025-10-05 22:00 | 278 | 10 | Spring | 22 | 14.21 | -14.3 | 21.82 | 42.2 | 0 | 0 | 120 | 120 | 14.3 | 47.36 | 41.73 | 72.64 | 0 | 0 | 0 | Normal
2025-10-05 23:00 | 278 | 10 | Spring | 23 | 14.21 | -13 | 9.23 | 54.8 | 0 | 0 | 26.33 | 26.33 | 13 | 45.9 | 33.9 | -19.57 | 0 | 0 | 0 | Battery-supported
2025-10-06 | 279 | 10 | Spring | 0 | 14.37 | -16.9 | 3.36 | 34.4 | 0 | 0 | 0 | 0 | 16.9 | 54.99 | 15 | -47.26 | 7.73 | 2.843 | 0 | Diesel-backup
2025-10-06 01:00 | 279 | 10 | Spring | 1 | 14.37 | -18.2 | 5.93 | 64.5 | 0 | 0 | 2.01 | 2.01 | 18.2 | 50.61 | 15 | 0 | 48.6 | 15.552 | 0 | Diesel-backup
2025-10-06 02:00 | 279 | 10 | Spring | 2 | 14.37 | -10.6 | 8.55 | 18.6 | 0 | 0 | 18.03 | 18.03 | 10.6 | 51.17 | 15 | 0 | 33.14 | 11.108 | 0 | Diesel-backup
2025-10-06 03:00 | 279 | 10 | Spring | 3 | 14.37 | -16.8 | 9.43 | 40.6 | 0 | 0 | 29.19 | 29.19 | 16.8 | 57.59 | 15 | 0 | 28.4 | 9.691 | 0 | Diesel-backup
2025-10-06 04:00 | 279 | 10 | Spring | 4 | 14.37 | -16.1 | 1.05 | 80.7 | 0 | 0 | 0 | 0 | 16.1 | 53.94 | 15 | 0 | 53.94 | 17.261 | 0 | Diesel-backup
2025-10-06 05:00 | 279 | 10 | Spring | 5 | 14.37 | -16.9 | 11.5 | 32.1 | 20.1 | 1.21 | 71.66 | 72.87 | 16.9 | 47.32 | 24.4 | 25.55 | 0 | 0 | 0 | Normal
2025-10-06 06:00 | 279 | 10 | Spring | 6 | 14.37 | -15.1 | 11.78 | 24.6 | 136.9 | 8.21 | 79.45 | 87.66 | 15.1 | 55.83 | 36.12 | 31.83 | 0 | 0 | 0 | Normal
2025-10-06 07:00 | 279 | 10 | Spring | 7 | 14.37 | -12.6 | 4.35 | 60.7 | 164.2 | 9.85 | 0.09 | 9.94 | 12.6 | 45.87 | 21.74 | -35.93 | 0 | 0 | 0 | Battery-supported
2025-10-06 08:00 | 279 | 10 | Spring | 8 | 14.37 | -15.2 | 13.94 | 9.5 | 390.8 | 23.45 | 120 | 143.45 | 15.2 | 56.85 | 53.61 | 86.6 | 0 | 0 | 0 | Normal
2025-10-06 09:00 | 279 | 10 | Spring | 9 | 14.37 | -19.8 | 7.69 | 70.2 | 246 | 12.55 | 10.3 | 22.85 | 19.8 | 64.86 | 36.81 | -42.01 | 0 | 0 | 0 | Battery-supported
2025-10-06 10:00 | 279 | 10 | Spring | 10 | 14.37 | -19.3 | 4.91 | 33.9 | 443.3 | 22.61 | 0.39 | 23 | 19.3 | 58.86 | 22.46 | -35.86 | 0 | 0 | 0 | Battery-supported
2025-10-06 11:00 | 279 | 10 | Spring | 11 | 14.37 | -16.9 | 4.14 | 35.7 | 469.1 | 28.15 | 0.04 | 28.19 | 16.9 | 64.88 | 15 | -18.66 | 18.03 | 6.391 | 0 | Diesel-backup
2025-10-06 12:00 | 279 | 10 | Spring | 12 | 14.37 | -16.3 | 11.36 | 28.5 | 515.9 | 30.95 | 67.96 | 98.91 | 16.3 | 62.48 | 28.41 | 36.43 | 0 | 0 | 0 | Normal
2025-10-06 13:00 | 279 | 10 | Spring | 13 | 14.37 | -19.2 | 6.18 | 64.7 | 329.7 | 16.81 | 2.69 | 19.5 | 19.2 | 74.08 | 15 | -33.52 | 21.06 | 7.386 | 0 | Diesel-backup
2025-10-06 14:00 | 279 | 10 | Spring | 14 | 14.37 | -13.2 | 10.01 | 35.6 | 435.6 | 26.14 | 38.61 | 64.75 | 13.2 | 57.4 | 17.7 | 7.35 | 0 | 0 | 0 | Normal
2025-10-06 15:00 | 279 | 10 | Spring | 15 | 14.37 | -17 | 4.06 | 19.5 | 443.7 | 26.62 | 0.02 | 26.64 | 17 | 59.47 | 15 | -6.76 | 26.07 | 8.973 | 0 | Diesel-backup
2025-10-06 16:00 | 279 | 10 | Spring | 16 | 14.37 | -11 | 7.13 | 82.9 | 159.1 | 9.55 | 6.69 | 16.24 | 11 | 62.02 | 15 | 0 | 45.78 | 14.65 | 0 | Diesel-backup
2025-10-06 17:00 | 279 | 10 | Spring | 17 | 14.37 | -9.9 | 10.94 | 43.7 | 202.6 | 12.16 | 57.64 | 69.8 | 9.9 | 45.44 | 23.96 | 24.36 | 0 | 0 | 0 | Normal
2025-10-06 18:00 | 279 | 10 | Spring | 18 | 14.37 | -14.3 | 15.83 | 68.2 | 82 | 4.92 | 120 | 124.92 | 14.3 | 58.21 | 48.51 | 66.71 | 0 | 0 | 0 | Normal
2025-10-06 19:00 | 279 | 10 | Spring | 19 | 14.37 | -12.6 | 16.79 | 31.2 | 20.3 | 1.22 | 120 | 121.22 | 12.6 | 55.05 | 72.86 | 66.17 | 0 | 0 | 0 | Normal
2025-10-06 20:00 | 279 | 10 | Spring | 20 | 14.37 | -16.2 | 15.65 | 62.1 | 0 | 0 | 120 | 120 | 16.2 | 64.12 | 93.43 | 55.88 | 0 | 0 | 0 | Normal
2025-10-06 21:00 | 279 | 10 | Spring | 21 | 14.37 | -12.2 | 30.69 | 32.3 | 0 | 0 | 0 | 0 | 12.2 | 59.63 | 69.58 | -59.63 | 0 | 0 | 0 | Battery-supported
2025-10-06 22:00 | 279 | 10 | Spring | 22 | 14.37 | -14.8 | 10.1 | 66.4 | 0 | 0 | 40.24 | 40.24 | 14.8 | 47.1 | 66.83 | -6.86 | 0 | 0 | 0 | Battery-supported
2025-10-06 23:00 | 279 | 10 | Spring | 23 | 14.37 | -16.3 | 3.98 | 46 | 0 | 0 | 0.02 | 0.02 | 16.3 | 55.93 | 44.47 | -55.91 | 0 | 0 | 0 | Battery-supported
2025-10-07 | 280 | 10 | Spring | 0 | 14.53 | -14.7 | 6 | 74.6 | 0 | 0 | 2.19 | 2.19 | 14.7 | 55.27 | 23.24 | -53.08 | 0 | 0 | 0 | Battery-supported
2025-10-07 01:00 | 280 | 10 | Spring | 1 | 14.53 | -15.4 | 16.48 | 55 | 0 | 0 | 120 | 120 | 15.4 | 55.66 | 46.91 | 64.34 | 0 | 0 | 0 | Normal
2025-10-07 02:00 | 280 | 10 | Spring | 2 | 14.53 | -15.5 | 5.52 | 56.2 | 0 | 0 | 1.15 | 1.15 | 15.5 | 51.48 | 26.78 | -50.33 | 0 | 0 | 0 | Battery-supported
2025-10-07 03:00 | 280 | 10 | Spring | 3 | 14.53 | -13.1 | 0.81 | 44 | 0 | 0 | 0 | 0 | 13.1 | 50.96 | 15 | -29.45 | 21.51 | 7.529 | 0 | Diesel-backup
2025-10-07 04:00 | 280 | 10 | Spring | 4 | 14.53 | -17.3 | 7.26 | 54.1 | 0 | 0 | 7.44 | 7.44 | 17.3 | 48.49 | 15 | 0 | 41.05 | 13.344 | 0 | Diesel-backup
2025-10-07 05:00 | 280 | 10 | Spring | 5 | 14.53 | -12 | 13.73 | 42.5 | 25.5 | 1.53 | 120 | 121.53 | 12 | 54.1 | 39.81 | 67.43 | 0 | 0 | 0 | Normal
2025-10-07 06:00 | 280 | 10 | Spring | 6 | 14.53 | -19 | 5.93 | 64.8 | 91 | 4.64 | 2.01 | 6.65 | 19 | 49.68 | 22.6 | -43.03 | 0 | 0 | 0 | Battery-supported
2025-10-07 07:00 | 280 | 10 | Spring | 7 | 14.53 | -12.7 | 16.94 | 61.1 | 167.2 | 10.03 | 120 | 130.03 | 12.7 | 45 | 53.89 | 85.03 | 0 | 0 | 0 | Normal
2025-10-07 08:00 | 280 | 10 | Spring | 8 | 14.53 | -18.5 | 22.86 | 23.1 | 351.8 | 17.94 | 120 | 137.94 | 18.5 | 60.37 | 82.44 | 77.57 | 0 | 0 | 0 | Normal
2025-10-07 09:00 | 280 | 10 | Spring | 9 | 14.53 | -16.3 | 9.92 | 47.6 | 336.1 | 20.17 | 37.04 | 57.21 | 16.3 | 57.02 | 82.51 | 0.19 | 0 | 0 | 0 | Normal
2025-10-07 10:00 | 280 | 10 | Spring | 10 | 14.53 | -17.2 | 25.13 | 42.3 | 406.7 | 24.4 | 120 | 144.4 | 17.2 | 61.94 | 95 | 33.94 | 0 | 0 | 0 | Normal
2025-10-07 11:00 | 280 | 10 | Spring | 11 | 14.53 | -16.6 | 19.67 | 35.5 | 470.3 | 28.22 | 120 | 148.22 | 16.6 | 58.34 | 95 | 0 | 0 | 0 | 0 | Normal
2025-10-07 12:00 | 280 | 10 | Spring | 12 | 14.53 | -13.8 | 13.98 | 62.8 | 346.8 | 20.81 | 120 | 140.81 | 13.8 | 53.32 | 95 | 0 | 0 | 0 | 0 | Normal
2025-10-07 13:00 | 280 | 10 | Spring | 13 | 14.53 | -11.9 | 10.71 | 55.9 | 372.1 | 22.33 | 52.46 | 74.79 | 11.9 | 50.42 | 95 | 0 | 0 | 0 | 0 | Normal
2025-10-07 14:00 | 280 | 10 | Spring | 14 | 14.53 | -12.2 | 10.16 | 60.1 | 327.2 | 19.63 | 41.35 | 60.98 | 12.2 | 59.95 | 95 | 0 | 0 | 0 | 0 | Normal
2025-10-07 15:00 | 280 | 10 | Spring | 15 | 14.53 | -15.3 | 8.22 | 46.2 | 341.6 | 20.5 | 14.72 | 35.22 | 15.3 | 60.41 | 84.92 | -25.19 | 0 | 0 | 0 | Battery-supported
2025-10-07 16:00 | 280 | 10 | Spring | 16 | 14.53 | -13.6 | 11.97 | 37.1 | 307.2 | 18.43 | 85.05 | 103.48 | 13.6 | 51.4 | 95 | 27.38 | 0 | 0 | 0 | Normal
2025-10-07 17:00 | 280 | 10 | Spring | 17 | 14.53 | -15.5 | 2 | 7.6 | 290.9 | 17.45 | 0 | 17.45 | 15.5 | 61.05 | 77.56 | -43.6 | 0 | 0 | 0 | Battery-supported
2025-10-07 18:00 | 280 | 10 | Spring | 18 | 14.53 | -15.7 | 20.16 | 29.6 | 137.8 | 8.27 | 120 | 128.27 | 15.7 | 57.42 | 95 | 47.39 | 0 | 0 | 0 | Normal
2025-10-07 19:00 | 280 | 10 | Spring | 19 | 14.53 | -15.9 | 25.37 | 31.4 | 28.6 | 1.72 | 120 | 121.72 | 15.9 | 52.59 | 95 | 0 | 0 | 0 | 0 | Normal
2025-10-07 20:00 | 280 | 10 | Spring | 20 | 14.53 | -14.3 | 1.88 | 30.1 | 0 | 0 | 0 | 0 | 14.3 | 52.34 | 74.06 | -52.34 | 0 | 0 | 0 | Battery-supported
2025-10-07 21:00 | 280 | 10 | Spring | 21 | 14.53 | -12.8 | 13.5 | 62.8 | 0 | 0 | 120 | 120 | 12.8 | 51.87 | 95 | 56.89 | 0 | 0 | 0 | Normal
2025-10-07 22:00 | 280 | 10 | Spring | 22 | 14.53 | -17.7 | 19.25 | 29.4 | 0 | 0 | 120 | 120 | 17.7 | 58.1 | 95 | 0 | 0 | 0 | 0 | Normal
2025-10-07 23:00 | 280 | 10 | Spring | 23 | 14.53 | -13.8 | 9.36 | 24.3 | 0 | 0 | 28.16 | 28.16 | 13.8 | 51.61 | 85.62 | -23.45 | 0 | 0 | 0 | Battery-supported
2025-10-08 | 281 | 10 | Spring | 0 | 14.69 | -10.5 | 7.94 | 40.5 | 0 | 0 | 12.25 | 12.25 | 10.5 | 45 | 72.52 | -32.75 | 0 | 0 | 0 | Battery-supported
2025-10-08 01:00 | 281 | 10 | Spring | 1 | 14.69 | -11.7 | 6.89 | 23.6 | 0 | 0 | 5.45 | 5.45 | 11.7 | 48.76 | 55.2 | -43.31 | 0 | 0 | 0 | Battery-supported
2025-10-08 02:00 | 281 | 10 | Spring | 2 | 14.69 | -15.9 | 6.09 | 88.1 | 0 | 0 | 2.43 | 2.43 | 15.9 | 52.87 | 35.02 | -50.44 | 0 | 0 | 0 | Battery-supported
2025-10-08 03:00 | 281 | 10 | Spring | 3 | 14.69 | -18.1 | 10.39 | 4.5 | 0 | 0 | 45.78 | 45.78 | 18.1 | 45 | 35.31 | 0.78 | 0 | 0 | 0 | Normal
2025-10-08 04:00 | 281 | 10 | Spring | 4 | 14.69 | -14.3 | 16.8 | 62.6 | 0 | 0 | 120 | 120 | 14.3 | 51.63 | 60.47 | 68.37 | 0 | 0 | 0 | Normal
2025-10-08 05:00 | 281 | 10 | Spring | 5 | 14.69 | -20.8 | 2.17 | 91.4 | 15.1 | 0.77 | 0 | 0.77 | 20.8 | 56.57 | 38.15 | -55.8 | 0 | 0 | 0 | Battery-supported
2025-10-08 06:00 | 281 | 10 | Spring | 6 | 14.69 | -13.5 | 4.57 | 71.9 | 85.6 | 5.14 | 0.17 | 5.31 | 13.5 | 57.88 | 17.12 | -52.57 | 0 | 0 | 0 | Battery-supported
2025-10-08 07:00 | 281 | 10 | Spring | 7 | 14.69 | -16.5 | 5.82 | 35 | 232.5 | 13.95 | 1.75 | 15.7 | 16.5 | 59.46 | 15 | -5.3 | 38.46 | 12.63 | 0 | Diesel-backup
2025-10-08 08:00 | 281 | 10 | Spring | 8 | 14.69 | -12.1 | 3.01 | 33.8 | 321.2 | 19.27 | 0 | 19.27 | 12.1 | 54.79 | 15 | 0 | 35.52 | 11.797 | 0 | Diesel-backup
2025-10-08 09:00 | 281 | 10 | Spring | 9 | 14.69 | -19.8 | 12.61 | 6.9 | 498.2 | 25.41 | 105.82 | 131.23 | 19.8 | 64.58 | 39.53 | 66.65 | 0 | 0 | 0 | Normal
2025-10-08 10:00 | 281 | 10 | Spring | 10 | 14.69 | -13.9 | 11.65 | 28.3 | 470.2 | 28.21 | 75.77 | 103.98 | 13.9 | 57.4 | 56.67 | 46.58 | 0 | 0 | 0 | Normal
2025-10-08 11:00 | 281 | 10 | Spring | 11 | 14.69 | -15.9 | 14.42 | 26.7 | 512.6 | 30.76 | 120 | 150.76 | 15.9 | 57.03 | 91.16 | 93.73 | 0 | 0 | 0 | Normal
2025-10-08 12:00 | 281 | 10 | Spring | 12 | 14.69 | -16.1 | 1.6 | 68.5 | 318.8 | 19.13 | 0 | 19.13 | 16.1 | 53.65 | 77.35 | -34.52 | 0 | 0 | 0 | Battery-supported
2025-10-08 13:00 | 281 | 10 | Spring | 13 | 14.69 | -18 | 13.43 | 45.5 | 422.4 | 25.34 | 120 | 145.34 | 18 | 58.33 | 95 | 47.95 | 0 | 0 | 0 | Normal
2025-10-08 14:00 | 281 | 10 | Spring | 14 | 14.69 | -13.3 | 16.74 | 48.2 | 381.1 | 22.87 | 120 | 142.87 | 13.3 | 54.48 | 95 | 0 | 0 | 0 | 0 | Normal
2025-10-08 15:00 | 281 | 10 | Spring | 15 | 14.69 | -12.7 | 12.76 | 48.8 | 333.1 | 19.99 | 111.13 | 131.12 | 12.7 | 60.48 | 95 | 0 | 0 | 0 | 0 | Normal
2025-10-08 16:00 | 281 | 10 | Spring | 16 | 14.69 | -9.9 | 8.88 | 60.5 | 235 | 14.1 | 21.8 | 35.9 | 9.9 | 53.75 | 87.86 | -17.85 | 0 | 0 | 0 | Battery-supported
2025-10-08 17:00 | 281 | 10 | Spring | 17 | 14.69 | -11.3 | 8.13 | 47.5 | 203 | 12.18 | 13.89 | 26.07 | 11.3 | 52.04 | 77.47 | -25.97 | 0 | 0 | 0 | Battery-supported
2025-10-08 18:00 | 281 | 10 | Spring | 18 | 14.69 | -14.6 | 11 | 55.3 | 108.8 | 6.53 | 59.05 | 65.58 | 14.6 | 54.65 | 81.49 | 10.93 | 0 | 0 | 0 | Normal
2025-10-08 19:00 | 281 | 10 | Spring | 19 | 14.69 | -15.4 | 10.25 | 30.9 | 36.9 | 2.21 | 43.04 | 45.25 | 15.4 | 60.16 | 75.53 | -14.91 | 0 | 0 | 0 | Battery-supported
2025-10-08 20:00 | 281 | 10 | Spring | 20 | 14.69 | -16.1 | 5.93 | 82 | 0 | 0 | 2.01 | 2.01 | 16.1 | 57.85 | 53.19 | -55.84 | 0 | 0 | 0 | Battery-supported
2025-10-08 21:00 | 281 | 10 | Spring | 21 | 14.69 | -9.9 | 1.72 | 27.7 | 0 | 0 | 0 | 0 | 9.9 | 45 | 35.19 | -45 | 0 | 0 | 0 | Battery-supported
2025-10-08 22:00 | 281 | 10 | Spring | 22 | 14.69 | -15 | 6.49 | 17.6 | 0 | 0 | 3.74 | 3.74 | 15 | 46.28 | 18.18 | -42.54 | 0 | 0 | 0 | Battery-supported
2025-10-08 23:00 | 281 | 10 | Spring | 23 | 14.69 | -10.3 | 23.64 | 94 | 0 | 0 | 120 | 120 | 10.3 | 52.35 | 43.07 | 67.65 | 0 | 0 | 0 | Normal
2025-10-09 | 282 | 10 | Spring | 0 | 14.85 | -12.5 | 1.94 | 93.4 | 0 | 0 | 0 | 0 | 12.5 | 46.99 | 24.28 | -46.99 | 0 | 0 | 0 | Battery-supported
2025-10-09 01:00 | 282 | 10 | Spring | 1 | 14.85 | -13.3 | 10.12 | 43.7 | 0 | 0 | 40.61 | 40.61 | 13.3 | 52.7 | 19.44 | -12.09 | 0 | 0 | 0 | Battery-supported
2025-10-09 02:00 | 282 | 10 | Spring | 2 | 14.85 | -15.1 | 20.42 | 6.9 | 0 | 0 | 120 | 120 | 15.1 | 45 | 47.04 | 75 | 0 | 0 | 0 | Normal
2025-10-09 03:00 | 282 | 10 | Spring | 3 | 14.85 | -13.3 | 14.57 | 63.4 | 0 | 0 | 120 | 120 | 13.3 | 53.03 | 71.69 | 66.97 | 0 | 0 | 0 | Normal
2025-10-09 04:00 | 282 | 10 | Spring | 4 | 14.85 | -15.2 | 15.88 | 60.1 | 0 | 0 | 120 | 120 | 15.2 | 53.31 | 95 | 63.35 | 0 | 0 | 0 | Normal
2025-10-09 05:00 | 282 | 10 | Spring | 5 | 14.85 | -16.3 | 14.86 | 33.9 | 43.7 | 2.62 | 120 | 122.62 | 16.3 | 54.86 | 95 | 0 | 0 | 0 | 0 | Normal
2025-10-09 06:00 | 282 | 10 | Spring | 6 | 14.85 | -14.2 | 3.02 | 23.7 | 159.9 | 9.59 | 0 | 9.59 | 14.2 | 45 | 80.84 | -35.41 | 0 | 0 | 0 | Battery-supported
2025-10-09 07:00 | 282 | 10 | Spring | 7 | 14.85 | -16.2 | 18.37 | 39 | 227.6 | 13.66 | 120 | 133.66 | 16.2 | 51.33 | 95 | 38.49 | 0 | 0 | 0 | Normal
2025-10-09 08:00 | 282 | 10 | Spring | 8 | 14.85 | -17.6 | 19.85 | 71.7 | 200.8 | 12.05 | 120 | 132.05 | 17.6 | 57.33 | 95 | 0 | 0 | 0 | 0 | Normal
2025-10-09 09:00 | 282 | 10 | Spring | 9 | 14.85 | -14.5 | 3.73 | 74.4 | 233.4 | 14 | 0 | 14 | 14.5 | 52.82 | 79.47 | -38.82 | 0 | 0 | 0 | Battery-supported
2025-10-09 10:00 | 282 | 10 | Spring | 10 | 14.85 | -15.8 | 6.83 | 96.5 | 165.4 | 9.92 | 5.17 | 15.09 | 15.8 | 51.28 | 65 | -36.19 | 0 | 0 | 0 | Battery-supported
2025-10-09 11:00 | 282 | 10 | Spring | 11 | 14.85 | -14.4 | 9.38 | 44.5 | 427.2 | 25.63 | 28.45 | 54.08 | 14.4 | 53.09 | 65.36 | 0.99 | 0 | 0 | 0 | Normal
2025-10-09 12:00 | 282 | 10 | Spring | 12 | 14.85 | -16.1 | 6.88 | 46.9 | 425.3 | 25.52 | 5.4 | 30.92 | 16.1 | 54.5 | 55.93 | -23.58 | 0 | 0 | 0 | Battery-supported
2025-10-09 13:00 | 282 | 10 | Spring | 13 | 14.85 | -17.4 | 5.57 | 55.5 | 374.4 | 22.46 | 1.24 | 23.7 | 17.4 | 63.54 | 39.99 | -39.84 | 0 | 0 | 0 | Battery-supported
2025-10-09 14:00 | 282 | 10 | Spring | 14 | 14.85 | -10.6 | 5.66 | 43.5 | 402.8 | 24.17 | 1.41 | 25.58 | 10.6 | 51.17 | 29.76 | -25.59 | 0 | 0 | 0 | Battery-supported
2025-10-09 15:00 | 282 | 10 | Spring | 15 | 14.85 | -10.6 | 13.36 | 23.5 | 434.9 | 26.09 | 120 | 146.09 | 10.6 | 52.98 | 64.02 | 93.11 | 0 | 0 | 0 | Normal
2025-10-09 16:00 | 282 | 10 | Spring | 16 | 14.85 | -11.7 | 15.6 | 21.9 | 363.4 | 21.8 | 120 | 141.8 | 11.7 | 59.5 | 94.31 | 82.3 | 0 | 0 | 0 | Normal
2025-10-09 17:00 | 282 | 10 | Spring | 17 | 14.85 | -14.2 | 5.68 | 64.2 | 166.9 | 10.01 | 1.45 | 11.46 | 14.2 | 57.49 | 75.9 | -46.03 | 0 | 0 | 0 | Battery-supported
2025-10-09 18:00 | 282 | 10 | Spring | 18 | 14.85 | -13.8 | 15.55 | 41 | 134.6 | 8.08 | 120 | 128.08 | 13.8 | 53.94 | 95 | 51.92 | 0 | 0 | 0 | Normal
2025-10-09 19:00 | 282 | 10 | Spring | 19 | 14.85 | -9.9 | 6.87 | 53.8 | 35 | 2.1 | 5.36 | 7.46 | 9.9 | 53.72 | 76.5 | -46.26 | 0 | 0 | 0 | Battery-supported
2025-10-09 20:00 | 282 | 10 | Spring | 20 | 14.85 | -13.7 | 3.91 | 71 | 0 | 0 | 0.01 | 0.01 | 13.7 | 53.57 | 55.07 | -53.56 | 0 | 0 | 0 | Battery-supported
2025-10-09 21:00 | 282 | 10 | Spring | 21 | 14.85 | -14.3 | 10.81 | 56.6 | 0 | 0 | 54.67 | 54.67 | 14.3 | 45 | 58.63 | 9.67 | 0 | 0 | 0 | Normal
2025-10-09 22:00 | 282 | 10 | Spring | 22 | 14.85 | -9 | 9.12 | 43 | 0 | 0 | 24.84 | 24.84 | 9 | 45.5 | 50.37 | -20.66 | 0 | 0 | 0 | Battery-supported
2025-10-09 23:00 | 282 | 10 | Spring | 23 | 14.85 | -13.4 | 11.05 | 66.8 | 0 | 0 | 60.24 | 60.24 | 13.4 | 50.99 | 53.77 | 9.25 | 0 | 0 | 0 | Normal
2025-10-10 | 283 | 10 | Spring | 0 | 15.01 | -9.5 | 10.9 | 58.1 | 0 | 0 | 56.72 | 56.72 | 9.5 | 45 | 58.08 | 11.72 | 0 | 0 | 0 | Normal
2025-10-10 01:00 | 283 | 10 | Spring | 1 | 15.01 | -16.9 | 10.24 | 45.8 | 0 | 0 | 42.85 | 42.85 | 16.9 | 51.38 | 54.67 | -8.53 | 0 | 0 | 0 | Battery-supported
2025-10-10 02:00 | 283 | 10 | Spring | 2 | 15.01 | -13 | 8.46 | 62.3 | 0 | 0 | 17.08 | 17.08 | 13 | 46.31 | 42.98 | -29.23 | 0 | 0 | 0 | Battery-supported
2025-10-10 03:00 | 283 | 10 | Spring | 3 | 15.01 | -10 | 15.29 | 68 | 0 | 0 | 120 | 120 | 10 | 51.19 | 68.3 | 68.81 | 0 | 0 | 0 | Normal
2025-10-10 04:00 | 283 | 10 | Spring | 4 | 15.01 | -14.9 | 12.73 | 54.9 | 0 | 0 | 110.06 | 110.06 | 14.9 | 51.1 | 90 | 58.96 | 0 | 0 | 0 | Normal
2025-10-10 05:00 | 283 | 10 | Spring | 5 | 15.01 | -15.8 | 6.99 | 62.4 | 36.7 | 2.2 | 5.95 | 8.15 | 15.8 | 50.29 | 73.14 | -42.14 | 0 | 0 | 0 | Battery-supported
2025-10-10 06:00 | 283 | 10 | Spring | 6 | 15.01 | -18.1 | 6.89 | 45.7 | 133.4 | 6.8 | 5.45 | 12.25 | 18.1 | 56.97 | 55.25 | -44.72 | 0 | 0 | 0 | Battery-supported
2025-10-10 07:00 | 283 | 10 | Spring | 7 | 15.01 | -13.3 | 2.82 | 39.1 | 232.1 | 13.93 | 0 | 13.93 | 13.3 | 52.53 | 39.81 | -38.6 | 0 | 0 | 0 | Battery-supported
2025-10-10 08:00 | 283 | 10 | Spring | 8 | 15.01 | -17.4 | 3.15 | 56.1 | 254.3 | 15.26 | 0 | 15.26 | 17.4 | 62.18 | 21.05 | -46.92 | 0 | 0 | 0 | Battery-supported
2025-10-10 09:00 | 283 | 10 | Spring | 9 | 15.01 | -15.8 | 8.09 | 25.8 | 428 | 25.68 | 13.53 | 39.21 | 15.8 | 62.67 | 15 | -15.12 | 8.34 | 3.061 | 0 | Diesel-backup
2025-10-10 10:00 | 283 | 10 | Spring | 10 | 15.01 | -18.2 | 14.19 | 65.1 | 306.6 | 15.64 | 120 | 135.64 | 18.2 | 63.42 | 41.58 | 72.22 | 0 | 0 | 0 | Normal
2025-10-10 11:00 | 283 | 10 | Spring | 11 | 15.01 | -11.8 | 5.05 | 50.9 | 396.6 | 23.8 | 0.52 | 24.32 | 11.8 | 55 | 29.3 | -30.68 | 0 | 0 | 0 | Battery-supported
2025-10-10 12:00 | 283 | 10 | Spring | 12 | 15.01 | -12.4 | 13.07 | 18.2 | 566.4 | 33.98 | 120 | 153.98 | 12.4 | 59.37 | 64.12 | 94.61 | 0 | 0 | 0 | Normal
2025-10-10 13:00 | 283 | 10 | Spring | 13 | 15.01 | -14.6 | 10.02 | 23.8 | 527.3 | 31.64 | 38.79 | 70.43 | 14.6 | 53.86 | 70.22 | 16.57 | 0 | 0 | 0 | Normal
2025-10-10 14:00 | 283 | 10 | Spring | 14 | 15.01 | -16.7 | 5.27 | 59 | 334.3 | 20.06 | 0.78 | 20.84 | 16.7 | 55.88 | 56.2 | -35.04 | 0 | 0 | 0 | Battery-supported
2025-10-10 15:00 | 283 | 10 | Spring | 15 | 15.01 | -10.4 | 9.29 | 8.3 | 497.7 | 29.86 | 27.17 | 57.03 | 10.4 | 55.38 | 56.81 | 1.65 | 0 | 0 | 0 | Normal
2025-10-10 16:00 | 283 | 10 | Spring | 16 | 15.01 | -14.2 | 9.08 | 34.7 | 324.7 | 19.48 | 24.32 | 43.8 | 14.2 | 54.49 | 52.53 | -10.69 | 0 | 0 | 0 | Battery-supported
2025-10-10 17:00 | 283 | 10 | Spring | 17 | 15.01 | -15.6 | 5.42 | 29.5 | 255.7 | 15.34 | 0.99 | 16.33 | 15.6 | 61.89 | 34.31 | -45.56 | 0 | 0 | 0 | Battery-supported
2025-10-10 18:00 | 283 | 10 | Spring | 18 | 15.01 | -16.8 | 12.57 | 73 | 91.9 | 5.51 | 104.43 | 109.94 | 16.8 | 60.8 | 52.39 | 49.14 | 0 | 0 | 0 | Normal
2025-10-10 19:00 | 283 | 10 | Spring | 19 | 15.01 | -14.2 | 14.98 | 82.3 | 26.4 | 1.58 | 120 | 121.58 | 14.2 | 65.48 | 73.04 | 56.1 | 0 | 0 | 0 | Normal
2025-10-10 20:00 | 283 | 10 | Spring | 20 | 15.01 | -15.9 | 7.39 | 56.7 | 0 | 0 | 8.24 | 8.24 | 15.9 | 54.95 | 54.35 | -46.71 | 0 | 0 | 0 | Battery-supported
2025-10-10 21:00 | 283 | 10 | Spring | 21 | 15.01 | -14.1 | 4.16 | 56.1 | 0 | 0 | 0.04 | 0.04 | 14.1 | 52.83 | 33.24 | -52.79 | 0 | 0 | 0 | Battery-supported
2025-10-10 22:00 | 283 | 10 | Spring | 22 | 15.01 | -11.2 | 15.39 | 37.1 | 0 | 0 | 120 | 120 | 11.2 | 45 | 60.84 | 75 | 0 | 0 | 0 | Normal
2025-10-10 23:00 | 283 | 10 | Spring | 23 | 15.01 | -14 | 3.01 | 82.2 | 0 | 0 | 0 | 0 | 14 | 50.17 | 40.77 | -50.17 | 0 | 0 | 0 | Battery-supported
2025-10-11 | 284 | 10 | Spring | 0 | 15.17 | -12.4 | 10.5 | 7.4 | 0 | 0 | 48.01 | 48.01 | 12.4 | 50.31 | 39.85 | -2.3 | 0 | 0 | 0 | Battery-supported
2025-10-11 01:00 | 284 | 10 | Spring | 1 | 15.17 | -15.2 | 5.03 | 76.2 | 0 | 0 | 0.5 | 0.5 | 15.2 | 51.78 | 19.34 | -51.28 | 0 | 0 | 0 | Battery-supported
2025-10-11 02:00 | 284 | 10 | Spring | 2 | 15.17 | -13.8 | 3.91 | 57.3 | 0 | 0 | 0.01 | 0.01 | 13.8 | 50.83 | 15 | -10.85 | 39.97 | 13.049 | 0 | Diesel-backup
2025-10-11 03:00 | 284 | 10 | Spring | 3 | 15.17 | -10.1 | 6.33 | 75.7 | 0 | 0 | 3.17 | 3.17 | 10.1 | 46.79 | 15 | 0 | 43.62 | 14.035 | 0 | Diesel-backup
2025-10-11 04:00 | 284 | 10 | Spring | 4 | 15.17 | -15.5 | 9.04 | 34.9 | 0 | 0 | 23.8 | 23.8 | 15.5 | 49.54 | 15 | 0 | 25.74 | 8.871 | 0 | Diesel-backup
2025-10-11 05:00 | 284 | 10 | Spring | 5 | 15.17 | -14.2 | 4.49 | 30 | 61.3 | 3.68 | 0.14 | 3.82 | 14.2 | 52.63 | 15 | 0 | 48.81 | 15.619 | 0 | Diesel-backup
2025-10-11 06:00 | 284 | 10 | Spring | 6 | 15.17 | -18.7 | 3.47 | 87.7 | 72.4 | 3.69 | 0 | 3.69 | 18.7 | 57.34 | 15 | 0 | 53.65 | 17.168 | 0 | Diesel-backup
2025-10-11 07:00 | 284 | 10 | Spring | 7 | 15.17 | -12.1 | 2.36 | 25.1 | 271.6 | 16.3 | 0 | 16.3 | 12.1 | 45.77 | 15 | 0 | 29.47 | 10.016 | 0 | Diesel-backup
2025-10-11 08:00 | 284 | 10 | Spring | 8 | 15.17 | -16.5 | 20.29 | 77.1 | 187 | 11.22 | 120 | 131.22 | 16.5 | 56.37 | 42.54 | 74.85 | 0 | 0 | 0 | Normal
2025-10-11 09:00 | 284 | 10 | Spring | 9 | 15.17 | -13.1 | 11 | 51.4 | 327.7 | 19.66 | 59.05 | 78.71 | 13.1 | 57.2 | 50.46 | 21.51 | 0 | 0 | 0 | Normal
2025-10-11 10:00 | 284 | 10 | Spring | 10 | 15.17 | -15.6 | 5.28 | 42.8 | 407.8 | 24.47 | 0.79 | 25.26 | 15.6 | 59.45 | 36.78 | -34.19 | 0 | 0 | 0 | Battery-supported
2025-10-11 11:00 | 284 | 10 | Spring | 11 | 15.17 | -13.7 | 11.32 | 45.2 | 424.5 | 25.47 | 66.93 | 92.4 | 13.7 | 50.29 | 52.28 | 42.11 | 0 | 0 | 0 | Normal
2025-10-11 12:00 | 284 | 10 | Spring | 12 | 15.17 | -13.3 | 8.98 | 22.8 | 544 | 32.64 | 23.03 | 55.67 | 13.3 | 57.22 | 51.66 | -1.55 | 0 | 0 | 0 | Battery-supported
2025-10-11 13:00 | 284 | 10 | Spring | 13 | 15.17 | -15.4 | 13.29 | 73.4 | 288.7 | 17.32 | 120 | 137.32 | 15.4 | 55.2 | 81.88 | 82.12 | 0 | 0 | 0 | Normal
2025-10-11 14:00 | 284 | 10 | Spring | 14 | 15.17 | -11.6 | 7.73 | 80.1 | 239.9 | 14.39 | 10.59 | 24.98 | 11.6 | 46.94 | 73.1 | -21.96 | 0 | 0 | 0 | Battery-supported
2025-10-11 15:00 | 284 | 10 | Spring | 15 | 15.17 | -15.3 | 14.65 | 49.1 | 337 | 20.22 | 120 | 140.22 | 15.3 | 59.88 | 95 | 59.52 | 0 | 0 | 0 | Normal
2025-10-11 16:00 | 284 | 10 | Spring | 16 | 15.17 | -11.5 | 5.78 | 75.6 | 192.1 | 11.53 | 1.66 | 13.19 | 11.5 | 49.67 | 80.41 | -36.48 | 0 | 0 | 0 | Battery-supported
2025-10-11 17:00 | 284 | 10 | Spring | 17 | 15.17 | -13.8 | 9.94 | 19 | 286.8 | 17.21 | 37.38 | 54.59 | 13.8 | 61.96 | 77.46 | -7.37 | 0 | 0 | 0 | Battery-supported
2025-10-11 18:00 | 284 | 10 | Spring | 18 | 15.17 | -11.9 | 14.13 | 20.3 | 179.1 | 10.75 | 120 | 130.75 | 11.9 | 58.04 | 95 | 47.66 | 0 | 0 | 0 | Normal
2025-10-11 19:00 | 284 | 10 | Spring | 19 | 15.17 | -13.5 | 10.23 | 91.3 | 24.9 | 1.49 | 42.66 | 44.15 | 13.5 | 57.49 | 89.66 | -13.34 | 0 | 0 | 0 | Battery-supported
2025-10-11 20:00 | 284 | 10 | Spring | 20 | 15.17 | -12.4 | 23.82 | 30.7 | 0 | 0 | 120 | 120 | 12.4 | 60.97 | 95 | 14.5 | 0 | 0 | 0 | Normal
2025-10-11 21:00 | 284 | 10 | Spring | 21 | 15.17 | -14.9 | 13.14 | 71.8 | 0 | 0 | 120 | 120 | 14.9 | 53.76 | 95 | 0 | 0 | 0 | 0 | Normal
2025-10-11 22:00 | 284 | 10 | Spring | 22 | 15.17 | -12.1 | 11.21 | 42.1 | 0 | 0 | 64.15 | 64.15 | 12.1 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-10-11 23:00 | 284 | 10 | Spring | 23 | 15.17 | -12.8 | 7.05 | 36.2 | 0 | 0 | 6.26 | 6.26 | 12.8 | 51.85 | 76.76 | -45.59 | 0 | 0 | 0 | Battery-supported
2025-10-12 | 285 | 10 | Spring | 0 | 15.33 | -14.2 | 10.03 | 53.8 | 0 | 0 | 38.97 | 38.97 | 14.2 | 46.46 | 73.77 | -7.49 | 0 | 0 | 0 | Battery-supported
2025-10-12 01:00 | 285 | 10 | Spring | 1 | 15.33 | -13.5 | 16.99 | 21.8 | 0 | 0 | 120 | 120 | 13.5 | 52.18 | 95 | 57.7 | 0 | 0 | 0 | Normal
2025-10-12 02:00 | 285 | 10 | Spring | 2 | 15.33 | -13.5 | 6.48 | 86.5 | 0 | 0 | 3.7 | 3.7 | 13.5 | 46.82 | 77.75 | -43.12 | 0 | 0 | 0 | Battery-supported
2025-10-12 03:00 | 285 | 10 | Spring | 3 | 15.33 | -15.5 | 4.9 | 90.1 | 0 | 0 | 0.38 | 0.38 | 15.5 | 45.46 | 59.72 | -45.08 | 0 | 0 | 0 | Battery-supported
2025-10-12 04:00 | 285 | 10 | Spring | 4 | 15.33 | -14.8 | 6.5 | 64 | 0 | 0 | 3.78 | 3.78 | 14.8 | 51.51 | 40.63 | -47.73 | 0 | 0 | 0 | Battery-supported
2025-10-12 05:00 | 285 | 10 | Spring | 5 | 15.33 | -17 | 6.28 | 51.8 | 54.4 | 3.26 | 3.01 | 6.27 | 17 | 50.07 | 23.11 | -43.8 | 0 | 0 | 0 | Battery-supported
2025-10-12 06:00 | 285 | 10 | Spring | 6 | 15.33 | -9.9 | 12.07 | 26.7 | 175.4 | 10.52 | 88.1 | 98.62 | 9.9 | 49.22 | 41.29 | 49.4 | 0 | 0 | 0 | Normal
2025-10-12 07:00 | 285 | 10 | Spring | 7 | 15.33 | -12.9 | 22.18 | 20.4 | 288.4 | 17.3 | 120 | 137.3 | 12.9 | 53.13 | 72.26 | 84.17 | 0 | 0 | 0 | Normal
2025-10-12 08:00 | 285 | 10 | Spring | 8 | 15.33 | -14.7 | 3.09 | 31.7 | 341.2 | 20.47 | 0 | 20.47 | 14.7 | 50.79 | 60.13 | -30.32 | 0 | 0 | 0 | Battery-supported
2025-10-12 09:00 | 285 | 10 | Spring | 9 | 15.33 | -12.6 | 1.51 | 41.5 | 368.9 | 22.13 | 0 | 22.13 | 12.6 | 55.6 | 46.75 | -33.47 | 0 | 0 | 0 | Battery-supported
2025-10-12 10:00 | 285 | 10 | Spring | 10 | 15.33 | -19.4 | 9.1 | 28.3 | 474 | 24.17 | 24.58 | 48.75 | 19.4 | 65 | 40.25 | -16.25 | 0 | 0 | 0 | Battery-supported
2025-10-12 11:00 | 285 | 10 | Spring | 11 | 15.33 | -20.5 | 4.49 | 58.8 | 359.1 | 18.31 | 0.14 | 18.45 | 20.5 | 64 | 22.03 | -45.55 | 0 | 0 | 0 | Battery-supported
2025-10-12 12:00 | 285 | 10 | Spring | 12 | 15.33 | -15.4 | 10.73 | 74.1 | 291.5 | 17.49 | 52.9 | 70.39 | 15.4 | 58.98 | 26.22 | 11.41 | 0 | 0 | 0 | Normal
2025-10-12 13:00 | 285 | 10 | Spring | 13 | 15.33 | -17.2 | 11.47 | 18.1 | 555.2 | 33.31 | 70.86 | 104.17 | 17.2 | 61.28 | 42.01 | 42.89 | 0 | 0 | 0 | Normal
2025-10-12 14:00 | 285 | 10 | Spring | 14 | 15.33 | -14.3 | 6.3 | 48.7 | 381.8 | 22.91 | 3.07 | 25.98 | 14.3 | 50.89 | 32.04 | -24.91 | 0 | 0 | 0 | Battery-supported
2025-10-12 15:00 | 285 | 10 | Spring | 15 | 15.33 | -12.9 | 12.26 | 53.9 | 319.3 | 19.16 | 94.09 | 113.25 | 12.9 | 62.29 | 50.8 | 50.96 | 0 | 0 | 0 | Normal
2025-10-12 16:00 | 285 | 10 | Spring | 16 | 15.33 | -11 | 5.65 | 65 | 229.5 | 13.77 | 1.39 | 15.16 | 11 | 56.64 | 34.21 | -41.48 | 0 | 0 | 0 | Battery-supported
2025-10-12 17:00 | 285 | 10 | Spring | 17 | 15.33 | -15.2 | 5.64 | 68.4 | 165.8 | 9.95 | 1.37 | 11.32 | 15.2 | 55.6 | 16.49 | -44.28 | 0 | 0 | 0 | Battery-supported
2025-10-12 18:00 | 285 | 10 | Spring | 18 | 15.33 | -11.6 | 5.09 | 14.5 | 195.5 | 11.73 | 0.56 | 12.29 | 11.6 | 51.6 | 15 | -3.73 | 35.58 | 11.814 | 0 | Diesel-backup
2025-10-12 19:00 | 285 | 10 | Spring | 19 | 15.33 | -12.3 | 6.55 | 51.2 | 54.9 | 3.29 | 3.97 | 7.26 | 12.3 | 58.77 | 15 | 0 | 51.51 | 16.483 | 0 | Diesel-backup
2025-10-12 20:00 | 285 | 10 | Spring | 20 | 15.33 | -11.5 | 8.57 | 73.7 | 0 | 0 | 18.24 | 18.24 | 11.5 | 55.55 | 15 | 0 | 37.31 | 12.306 | 0 | Diesel-backup
2025-10-12 21:00 | 285 | 10 | Spring | 21 | 15.33 | -13.5 | 8.01 | 66.7 | 0 | 0 | 12.84 | 12.84 | 13.5 | 49.96 | 15 | 0 | 37.12 | 12.253 | 0 | Diesel-backup
2025-10-12 22:00 | 285 | 10 | Spring | 22 | 15.33 | -9.4 | 9.6 | 21.8 | 0 | 0 | 31.77 | 31.77 | 9.4 | 46.62 | 15 | 0 | 14.85 | 5.325 | 0 | Diesel-backup
2025-10-12 23:00 | 285 | 10 | Spring | 23 | 15.33 | -12.9 | 11.9 | 24.8 | 0 | 0 | 82.96 | 82.96 | 12.9 | 48.81 | 27.57 | 34.15 | 0 | 0 | 0 | Normal
2025-10-13 | 286 | 10 | Spring | 0 | 15.49 | -8.9 | 9.64 | 94.4 | 0 | 0 | 32.4 | 32.4 | 8.9 | 45 | 22.53 | -12.6 | 0 | 0 | 0 | Battery-supported
2025-10-13 01:00 | 286 | 10 | Spring | 1 | 15.49 | -14.9 | 19.93 | 65.4 | 0 | 0 | 120 | 120 | 14.9 | 48.26 | 48.93 | 71.74 | 0 | 0 | 0 | Normal
2025-10-13 02:00 | 286 | 10 | Spring | 2 | 15.49 | -11.9 | 8.92 | 34 | 0 | 0 | 22.28 | 22.28 | 11.9 | 49.14 | 38.18 | -26.86 | 0 | 0 | 0 | Battery-supported
2025-10-13 03:00 | 286 | 10 | Spring | 3 | 15.49 | -14.1 | 13.44 | 46.3 | 0 | 0 | 120 | 120 | 14.1 | 51.68 | 63.33 | 68.32 | 0 | 0 | 0 | Normal
2025-10-13 04:00 | 286 | 10 | Spring | 4 | 15.49 | -15 | 2.78 | 14.6 | 0 | 0 | 0 | 0 | 15 | 48.1 | 44.09 | -48.1 | 0 | 0 | 0 | Battery-supported
2025-10-13 05:00 | 286 | 10 | Spring | 5 | 15.49 | -13.2 | 9.57 | 48.3 | 63 | 3.78 | 31.3 | 35.08 | 13.2 | 48.06 | 38.89 | -12.98 | 0 | 0 | 0 | Battery-supported
2025-10-13 06:00 | 286 | 10 | Spring | 6 | 15.49 | -15.5 | 7.93 | 58.1 | 128.4 | 7.7 | 12.17 | 19.87 | 15.5 | 55.15 | 24.78 | -35.28 | 0 | 0 | 0 | Battery-supported
2025-10-13 07:00 | 286 | 10 | Spring | 7 | 15.49 | -20.9 | 7.49 | 40.9 | 240.3 | 12.26 | 8.89 | 21.15 | 20.9 | 61.52 | 15 | -24.45 | 15.92 | 5.686 | 0 | Diesel-backup
2025-10-13 08:00 | 286 | 10 | Spring | 8 | 15.49 | -21.8 | 16.74 | 60.2 | 247.7 | 12.63 | 120 | 132.63 | 21.8 | 66.12 | 39.48 | 66.51 | 0 | 0 | 0 | Normal
2025-10-13 09:00 | 286 | 10 | Spring | 9 | 15.49 | -12.2 | 24.17 | 46.4 | 351.1 | 21.07 | 120 | 141.07 | 12.2 | 58.75 | 69.77 | 82.32 | 0 | 0 | 0 | Normal
2025-10-13 10:00 | 286 | 10 | Spring | 10 | 15.49 | -12.2 | 11.93 | 29.6 | 468.9 | 28.13 | 83.85 | 111.98 | 12.2 | 56.62 | 90.14 | 55.36 | 0 | 0 | 0 | Normal
2025-10-13 11:00 | 286 | 10 | Spring | 11 | 15.49 | -10.5 | 2.32 | 41.6 | 442.2 | 26.53 | 0 | 26.53 | 10.5 | 56.32 | 78.23 | -29.79 | 0 | 0 | 0 | Battery-supported
2025-10-13 12:00 | 286 | 10 | Spring | 12 | 15.49 | -14.4 | 6.07 | 73.1 | 296.6 | 17.8 | 2.38 | 20.18 | 14.4 | 57.36 | 63.35 | -37.18 | 0 | 0 | 0 | Battery-supported
2025-10-13 13:00 | 286 | 10 | Spring | 13 | 15.49 | -16.8 | 3.15 | 10.9 | 590.1 | 35.41 | 0 | 35.41 | 16.8 | 57.39 | 54.56 | -21.98 | 0 | 0 | 0 | Battery-supported
2025-10-13 14:00 | 286 | 10 | Spring | 14 | 15.49 | -14.5 | 9.42 | 29.6 | 468.9 | 28.13 | 29.04 | 57.17 | 14.5 | 64.9 | 51.47 | -7.73 | 0 | 0 | 0 | Battery-supported
2025-10-13 15:00 | 286 | 10 | Spring | 15 | 15.49 | -13.2 | 11.06 | 38.8 | 381.7 | 22.9 | 60.47 | 83.37 | 13.2 | 63.4 | 58.82 | 19.97 | 0 | 0 | 0 | Normal
2025-10-13 16:00 | 286 | 10 | Spring | 16 | 15.49 | -15 | 2.61 | 38.5 | 321.3 | 19.28 | 0 | 19.28 | 15 | 58.11 | 43.29 | -38.83 | 0 | 0 | 0 | Battery-supported
2025-10-13 17:00 | 286 | 10 | Spring | 17 | 15.49 | -8.9 | 18.42 | 75.8 | 149.6 | 8.98 | 120 | 128.98 | 8.9 | 53.49 | 71.07 | 75.49 | 0 | 0 | 0 | Normal
2025-10-13 18:00 | 286 | 10 | Spring | 18 | 15.49 | -7.3 | 3.84 | 72.7 | 103.3 | 6.2 | 0.01 | 6.21 | 7.3 | 50.99 | 53.16 | -44.78 | 0 | 0 | 0 | Battery-supported
2025-10-13 19:00 | 286 | 10 | Spring | 19 | 15.49 | -11.1 | 10.76 | 59.3 | 54.9 | 3.29 | 53.56 | 56.85 | 11.1 | 54.31 | 54.09 | 2.54 | 0 | 0 | 0 | Normal
2025-10-13 20:00 | 286 | 10 | Spring | 20 | 15.49 | -12.1 | 18.19 | 75.9 | 0 | 0 | 120 | 120 | 12.1 | 55.49 | 77.83 | 64.51 | 0 | 0 | 0 | Normal
2025-10-13 21:00 | 286 | 10 | Spring | 21 | 15.49 | -15 | 9.53 | 28.9 | 0 | 0 | 30.69 | 30.69 | 15 | 54.7 | 68.23 | -24.01 | 0 | 0 | 0 | Battery-supported
2025-10-13 22:00 | 286 | 10 | Spring | 22 | 15.49 | -8.9 | 5.4 | 57.6 | 0 | 0 | 0.96 | 0.96 | 8.9 | 45 | 50.61 | -44.04 | 0 | 0 | 0 | Battery-supported
2025-10-13 23:00 | 286 | 10 | Spring | 23 | 15.49 | -12.3 | 5.19 | 44.2 | 0 | 0 | 0.68 | 0.68 | 12.3 | 45 | 32.88 | -44.32 | 0 | 0 | 0 | Battery-supported
2025-10-14 | 287 | 10 | Spring | 0 | 15.65 | -13.2 | 9.65 | 83.5 | 0 | 0 | 32.56 | 32.56 | 13.2 | 51.94 | 25.13 | -19.38 | 0 | 0 | 0 | Battery-supported
2025-10-14 01:00 | 287 | 10 | Spring | 1 | 15.65 | -11.9 | 13.41 | 47.9 | 0 | 0 | 120 | 120 | 11.9 | 47.65 | 51.75 | 72.35 | 0 | 0 | 0 | Normal
2025-10-14 02:00 | 287 | 10 | Spring | 2 | 15.65 | -14.7 | 10.5 | 72 | 0 | 0 | 48.01 | 48.01 | 14.7 | 54.88 | 49.01 | -6.87 | 0 | 0 | 0 | Battery-supported
2025-10-14 03:00 | 287 | 10 | Spring | 3 | 15.65 | -13.4 | 5.1 | 79.9 | 0 | 0 | 0.57 | 0.57 | 13.4 | 48.84 | 29.7 | -48.27 | 0 | 0 | 0 | Battery-supported
2025-10-14 04:00 | 287 | 10 | Spring | 4 | 15.65 | -17.3 | 7.78 | 52.2 | 0 | 0 | 10.97 | 10.97 | 17.3 | 53.88 | 15 | -36.75 | 6.16 | 2.279 | 0 | Diesel-backup
2025-10-14 05:00 | 287 | 10 | Spring | 5 | 15.65 | -12 | 4.64 | 35.8 | 79.3 | 4.76 | 0.21 | 4.97 | 12 | 46.34 | 15 | 0 | 41.37 | 13.431 | 0 | Diesel-backup
2025-10-14 06:00 | 287 | 10 | Spring | 6 | 15.65 | -14.9 | 4.61 | 80.8 | 92.7 | 5.56 | 0.19 | 5.75 | 14.9 | 55.47 | 15 | 0 | 49.72 | 15.91 | 0 | Diesel-backup
2025-10-14 07:00 | 287 | 10 | Spring | 7 | 15.65 | -12.3 | 4.44 | 56.2 | 203.9 | 12.23 | 0.12 | 12.35 | 12.3 | 50.95 | 15 | 0 | 38.6 | 12.668 | 0 | Diesel-backup
2025-10-14 08:00 | 287 | 10 | Spring | 8 | 15.65 | -15.3 | 6.75 | 18.4 | 392.8 | 23.57 | 4.8 | 28.37 | 15.3 | 53.95 | 15 | 0 | 25.58 | 8.821 | 0 | Diesel-backup
2025-10-14 09:00 | 287 | 10 | Spring | 9 | 15.65 | -15.1 | 8.29 | 66.2 | 272.2 | 16.33 | 15.38 | 31.71 | 15.1 | 60.75 | 15 | 0 | 29.04 | 9.886 | 0 | Diesel-backup
2025-10-14 10:00 | 287 | 10 | Spring | 10 | 15.65 | -17.3 | 8.88 | 25.4 | 488.6 | 29.32 | 21.8 | 51.12 | 17.3 | 64.61 | 15 | 0 | 13.49 | 4.861 | 0 | Diesel-backup
2025-10-14 11:00 | 287 | 10 | Spring | 11 | 15.65 | -12.8 | 10.17 | 35.6 | 470.9 | 28.25 | 41.53 | 69.78 | 12.8 | 55.83 | 20.13 | 13.95 | 0 | 0 | 0 | Normal
2025-10-14 12:00 | 287 | 10 | Spring | 12 | 15.65 | -16 | 5.29 | 29 | 513.2 | 30.79 | 0.8 | 31.59 | 16 | 61.96 | 15 | -12.83 | 17.54 | 6.228 | 0 | Diesel-backup
2025-10-14 13:00 | 287 | 10 | Spring | 13 | 15.65 | -14.8 | 8.4 | 72.5 | 293.4 | 17.6 | 16.47 | 34.07 | 14.8 | 63.18 | 15 | 0 | 29.11 | 9.907 | 0 | Diesel-backup
2025-10-14 14:00 | 287 | 10 | Spring | 14 | 15.65 | -13.4 | 9.03 | 73.9 | 269.1 | 16.15 | 23.67 | 39.82 | 13.4 | 56.18 | 15 | 0 | 16.36 | 5.835 | 0 | Diesel-backup
2025-10-14 15:00 | 287 | 10 | Spring | 15 | 15.65 | -12.7 | 15.85 | 10.9 | 496.5 | 29.79 | 120 | 149.79 | 12.7 | 57.25 | 49.05 | 92.54 | 0 | 0 | 0 | Normal
2025-10-14 16:00 | 287 | 10 | Spring | 16 | 15.65 | -16.4 | 2.67 | 53.5 | 272.9 | 16.37 | 0 | 16.37 | 16.4 | 57.66 | 32.54 | -41.29 | 0 | 0 | 0 | Battery-supported
2025-10-14 17:00 | 287 | 10 | Spring | 17 | 15.65 | -12.8 | 3.24 | 54.9 | 207.3 | 12.44 | 0 | 12.44 | 12.8 | 58.12 | 15 | -43.85 | 1.83 | 0.688 | 0 | Diesel-backup
2025-10-14 18:00 | 287 | 10 | Spring | 18 | 15.65 | -10.3 | 11.54 | 72.9 | 106.6 | 6.4 | 72.74 | 79.14 | 10.3 | 49.71 | 25.83 | 29.43 | 0 | 0 | 0 | Normal
2025-10-14 19:00 | 287 | 10 | Spring | 19 | 15.65 | -12.7 | 12.25 | 43.4 | 73.2 | 4.39 | 93.76 | 98.15 | 12.7 | 58.56 | 40.4 | 39.59 | 0 | 0 | 0 | Normal
2025-10-14 20:00 | 287 | 10 | Spring | 20 | 15.65 | -12.4 | 11.57 | 56.4 | 0 | 0 | 73.56 | 73.56 | 12.4 | 61.74 | 44.75 | 11.82 | 0 | 0 | 0 | Normal
2025-10-14 21:00 | 287 | 10 | Spring | 21 | 15.65 | -11.6 | 11.5 | 39.7 | 0 | 0 | 71.66 | 71.66 | 11.6 | 45 | 54.56 | 26.66 | 0 | 0 | 0 | Normal
2025-10-14 22:00 | 287 | 10 | Spring | 22 | 15.65 | -12.3 | 2.86 | 79.8 | 0 | 0 | 0 | 0 | 12.3 | 52.86 | 33.42 | -52.86 | 0 | 0 | 0 | Battery-supported
2025-10-14 23:00 | 287 | 10 | Spring | 23 | 15.65 | -14.6 | 22.04 | 27.8 | 0 | 0 | 120 | 120 | 14.6 | 49.75 | 59.27 | 70.25 | 0 | 0 | 0 | Normal
2025-10-15 | 288 | 10 | Spring | 0 | 15.82 | -12.5 | 14.79 | 45.7 | 0 | 0 | 120 | 120 | 12.5 | 45.22 | 86.79 | 74.78 | 0 | 0 | 0 | Normal
2025-10-15 01:00 | 288 | 10 | Spring | 1 | 15.82 | -10.6 | 2.89 | 39.3 | 0 | 0 | 0 | 0 | 10.6 | 45.05 | 68.77 | -45.05 | 0 | 0 | 0 | Battery-supported
2025-10-15 02:00 | 288 | 10 | Spring | 2 | 15.82 | -15.5 | 7.14 | 18.4 | 0 | 0 | 6.75 | 6.75 | 15.5 | 50.93 | 51.1 | -44.18 | 0 | 0 | 0 | Battery-supported
2025-10-15 03:00 | 288 | 10 | Spring | 3 | 15.82 | -14.4 | 6.89 | 38.9 | 0 | 0 | 5.45 | 5.45 | 14.4 | 48.13 | 34.02 | -42.68 | 0 | 0 | 0 | Battery-supported
2025-10-15 04:00 | 288 | 10 | Spring | 4 | 15.82 | -16.9 | 7.9 | 13.7 | 0 | 0 | 11.92 | 11.92 | 16.9 | 56.77 | 16.08 | -44.85 | 0 | 0 | 0 | Battery-supported
2025-10-15 05:00 | 288 | 10 | Spring | 5 | 15.82 | -12.1 | 6.36 | 11.9 | 107.3 | 6.44 | 3.27 | 9.71 | 12.1 | 46.31 | 15 | -2.71 | 33.89 | 11.327 | 0 | Diesel-backup
2025-10-15 06:00 | 288 | 10 | Spring | 6 | 15.82 | -14.7 | 4.01 | 15.4 | 214.8 | 12.89 | 0.02 | 12.91 | 14.7 | 51.28 | 15 | 0 | 38.37 | 12.604 | 0 | Diesel-backup
2025-10-15 07:00 | 288 | 10 | Spring | 7 | 15.82 | -16.5 | 9.09 | 33.8 | 267.3 | 16.04 | 24.45 | 40.49 | 16.5 | 60.29 | 15 | 0 | 19.8 | 6.975 | 0 | Diesel-backup
2025-10-15 08:00 | 288 | 10 | Spring | 8 | 15.82 | -14.5 | 16.37 | 21.1 | 387 | 23.22 | 120 | 143.22 | 14.5 | 57.13 | 46.68 | 86.09 | 0 | 0 | 0 | Normal
2025-10-15 09:00 | 288 | 10 | Spring | 9 | 15.82 | -17.3 | 6.24 | 43.4 | 366 | 21.96 | 2.88 | 24.84 | 17.3 | 58.67 | 33.15 | -33.83 | 0 | 0 | 0 | Battery-supported
2025-10-15 10:00 | 288 | 10 | Spring | 10 | 15.82 | -16.7 | 10.09 | 56.2 | 349.8 | 20.99 | 40.06 | 61.05 | 16.7 | 58.49 | 34.09 | 2.56 | 0 | 0 | 0 | Normal
2025-10-15 11:00 | 288 | 10 | Spring | 11 | 15.82 | -17.4 | 8.04 | 60 | 353.6 | 21.22 | 13.1 | 34.32 | 17.4 | 65.17 | 21.75 | -30.85 | 0 | 0 | 0 | Battery-supported
2025-10-15 12:00 | 288 | 10 | Spring | 12 | 15.82 | -16.3 | 11.46 | 1.1 | 650.5 | 39.03 | 70.59 | 109.62 | 16.3 | 59.22 | 40.3 | 50.4 | 0 | 0 | 0 | Normal
2025-10-15 13:00 | 288 | 10 | Spring | 13 | 15.82 | -10.6 | 7.61 | 67.9 | 315.5 | 18.93 | 9.72 | 28.65 | 10.6 | 54.94 | 29.78 | -26.29 | 0 | 0 | 0 | Battery-supported
2025-10-15 14:00 | 288 | 10 | Spring | 14 | 15.82 | -14.8 | 5.67 | 44.2 | 404.5 | 24.27 | 1.43 | 25.7 | 14.8 | 55.28 | 17.95 | -29.58 | 0 | 0 | 0 | Battery-supported
2025-10-15 15:00 | 288 | 10 | Spring | 15 | 15.82 | -11.7 | 6.46 | 3.1 | 530.4 | 31.82 | 3.63 | 35.45 | 11.7 | 53.79 | 15 | -7.38 | 10.96 | 3.986 | 0 | Diesel-backup
2025-10-15 16:00 | 288 | 10 | Spring | 16 | 15.82 | -14.2 | 16.02 | 40.8 | 318.9 | 19.13 | 120 | 139.13 | 14.2 | 61.33 | 43.63 | 77.8 | 0 | 0 | 0 | Normal
2025-10-15 17:00 | 288 | 10 | Spring | 17 | 15.82 | -10.4 | 8.65 | 59.1 | 199.5 | 11.97 | 19.12 | 31.09 | 10.4 | 47.83 | 36.93 | -16.74 | 0 | 0 | 0 | Battery-supported
2025-10-15 18:00 | 288 | 10 | Spring | 18 | 15.82 | -14.1 | 8.48 | 78.8 | 99.3 | 5.96 | 17.29 | 23.25 | 14.1 | 50.25 | 26.13 | -27 | 0 | 0 | 0 | Battery-supported
2025-10-15 19:00 | 288 | 10 | Spring | 19 | 15.82 | -11.6 | 15.73 | 84.4 | 43.2 | 2.59 | 120 | 122.59 | 11.6 | 52.85 | 51.8 | 69.74 | 0 | 0 | 0 | Normal
2025-10-15 20:00 | 288 | 10 | Spring | 20 | 15.82 | -11.5 | 17.38 | 21.6 | 0 | 0 | 120 | 120 | 11.5 | 53.14 | 76.4 | 66.86 | 0 | 0 | 0 | Normal
2025-10-15 21:00 | 288 | 10 | Spring | 21 | 15.82 | -6.6 | 1.54 | 21.4 | 0 | 0 | 0 | 0 | 6.6 | 45 | 58.4 | -45 | 0 | 0 | 0 | Battery-supported
2025-10-15 22:00 | 288 | 10 | Spring | 22 | 15.82 | -10.5 | 3.29 | 23.3 | 0 | 0 | 0 | 0 | 10.5 | 45 | 40.4 | -45 | 0 | 0 | 0 | Battery-supported
2025-10-15 23:00 | 288 | 10 | Spring | 23 | 15.82 | -13.4 | 13.2 | 69.5 | 0 | 0 | 120 | 120 | 13.4 | 48.67 | 66.65 | 71.33 | 0 | 0 | 0 | Normal
2025-10-16 | 289 | 10 | Spring | 0 | 15.98 | -10.7 | 8.86 | 32.6 | 0 | 0 | 21.55 | 21.55 | 10.7 | 45 | 57.27 | -23.45 | 0 | 0 | 0 | Battery-supported
2025-10-16 01:00 | 289 | 10 | Spring | 1 | 15.98 | -7.9 | 17.35 | 21.2 | 0 | 0 | 120 | 120 | 7.9 | 48.56 | 83.56 | 71.44 | 0 | 0 | 0 | Normal
2025-10-16 02:00 | 289 | 10 | Spring | 2 | 15.98 | -16.5 | 2.66 | 39.4 | 0 | 0 | 0 | 0 | 16.5 | 55.01 | 61.56 | -55.01 | 0 | 0 | 0 | Battery-supported
2025-10-16 03:00 | 289 | 10 | Spring | 3 | 15.98 | -15.2 | 9.62 | 33.1 | 0 | 0 | 32.08 | 32.08 | 15.2 | 49.94 | 54.41 | -17.86 | 0 | 0 | 0 | Battery-supported
2025-10-16 04:00 | 289 | 10 | Spring | 4 | 15.98 | -14.2 | 11.75 | 63.6 | 0 | 0 | 78.59 | 78.59 | 14.2 | 53.06 | 63.81 | 25.53 | 0 | 0 | 0 | Normal
2025-10-16 05:00 | 289 | 10 | Spring | 5 | 15.98 | -14.9 | 6.93 | 62 | 68 | 4.08 | 5.65 | 9.73 | 14.9 | 45 | 49.7 | -35.27 | 0 | 0 | 0 | Battery-supported
2025-10-16 06:00 | 289 | 10 | Spring | 6 | 15.98 | -15 | 12.73 | 59.5 | 138.6 | 8.32 | 110.06 | 118.38 | 15 | 51.56 | 74.29 | 66.82 | 0 | 0 | 0 | Normal
2025-10-16 07:00 | 289 | 10 | Spring | 7 | 15.98 | -17.3 | 13.3 | 57.6 | 206.7 | 12.4 | 120 | 132.4 | 17.3 | 55.95 | 95 | 56.27 | 0 | 0 | 0 | Normal
2025-10-16 08:00 | 289 | 10 | Spring | 8 | 15.98 | -11.4 | 8.07 | 53.2 | 278.4 | 16.7 | 13.36 | 30.06 | 11.4 | 52.36 | 86.08 | -22.3 | 0 | 0 | 0 | Battery-supported
2025-10-16 09:00 | 289 | 10 | Spring | 9 | 15.98 | -17.5 | 7.74 | 25 | 443 | 26.58 | 10.67 | 37.25 | 17.5 | 62.84 | 75.84 | -25.59 | 0 | 0 | 0 | Battery-supported
2025-10-16 10:00 | 289 | 10 | Spring | 10 | 15.98 | -14.7 | 14.04 | 31.2 | 464 | 27.84 | 120 | 147.84 | 14.7 | 55.38 | 95 | 52.05 | 0 | 0 | 0 | Normal
2025-10-16 11:00 | 289 | 10 | Spring | 11 | 15.98 | -11.7 | 9.51 | 75.8 | 277.6 | 16.66 | 30.38 | 47.04 | 11.7 | 56.26 | 91.31 | -9.22 | 0 | 0 | 0 | Battery-supported
2025-10-16 12:00 | 289 | 10 | Spring | 12 | 15.98 | -13.8 | 11.29 | 54.9 | 386.1 | 23.17 | 66.16 | 89.33 | 13.8 | 51.79 | 95 | 10.02 | 0 | 0 | 0 | Normal
2025-10-16 13:00 | 289 | 10 | Spring | 13 | 15.98 | -15.5 | 9.49 | 56.2 | 372 | 22.32 | 30.08 | 52.4 | 15.5 | 62.32 | 91.03 | -9.92 | 0 | 0 | 0 | Battery-supported
2025-10-16 14:00 | 289 | 10 | Spring | 14 | 15.98 | -15.9 | 9.21 | 53.1 | 364.7 | 21.88 | 26.06 | 47.94 | 15.9 | 59.13 | 86.56 | -11.19 | 0 | 0 | 0 | Battery-supported
2025-10-16 15:00 | 289 | 10 | Spring | 15 | 15.98 | -13.1 | 7.73 | 18.2 | 470.8 | 28.25 | 10.59 | 38.84 | 13.1 | 57.24 | 79.2 | -18.4 | 0 | 0 | 0 | Battery-supported
2025-10-16 16:00 | 289 | 10 | Spring | 16 | 15.98 | -13.9 | 11.73 | 57.4 | 264.1 | 15.85 | 78.02 | 93.87 | 13.9 | 56.83 | 92.83 | 37.04 | 0 | 0 | 0 | Normal
2025-10-16 17:00 | 289 | 10 | Spring | 17 | 15.98 | -11.4 | 4.96 | 20.3 | 308.5 | 18.51 | 0.44 | 18.95 | 11.4 | 58.95 | 76.83 | -40 | 0 | 0 | 0 | Battery-supported
2025-10-16 18:00 | 289 | 10 | Spring | 18 | 15.98 | -14.7 | 2.75 | 39.1 | 176.9 | 10.61 | 0 | 10.61 | 14.7 | 58.92 | 57.5 | -48.31 | 0 | 0 | 0 | Battery-supported
2025-10-16 19:00 | 289 | 10 | Spring | 19 | 15.98 | -9.7 | 8.44 | 50 | 79.5 | 4.77 | 16.87 | 21.64 | 9.7 | 56.68 | 43.49 | -35.04 | 0 | 0 | 0 | Battery-supported
2025-10-16 20:00 | 289 | 10 | Spring | 20 | 15.98 | -11.2 | 17.5 | 48.5 | 0 | 0 | 120 | 120 | 11.2 | 52.24 | 68.42 | 67.76 | 0 | 0 | 0 | Normal
2025-10-16 21:00 | 289 | 10 | Spring | 21 | 15.98 | -11.1 | 9.52 | 51.3 | 0 | 0 | 30.54 | 30.54 | 11.1 | 48.57 | 61.21 | -18.03 | 0 | 0 | 0 | Battery-supported
2025-10-16 22:00 | 289 | 10 | Spring | 22 | 15.98 | -8.5 | 7.3 | 84.4 | 0 | 0 | 7.68 | 7.68 | 8.5 | 50.01 | 44.28 | -42.33 | 0 | 0 | 0 | Battery-supported
2025-10-16 23:00 | 289 | 10 | Spring | 23 | 15.98 | -12.9 | 6.74 | 83 | 0 | 0 | 4.76 | 4.76 | 12.9 | 54.58 | 24.35 | -49.82 | 0 | 0 | 0 | Battery-supported
2025-10-17 | 290 | 10 | Spring | 0 | 16.15 | -13.6 | 6.44 | 54.7 | 0 | 0 | 3.56 | 3.56 | 13.6 | 45 | 15 | -23.38 | 18.06 | 6.403 | 0 | Diesel-backup
2025-10-17 01:00 | 290 | 10 | Spring | 1 | 16.15 | -13.6 | 0.95 | 57.4 | 0 | 0 | 0 | 0 | 13.6 | 49.46 | 15 | 0 | 49.46 | 15.827 | 0 | Diesel-backup
2025-10-17 02:00 | 290 | 10 | Spring | 2 | 16.15 | -13.2 | 16.09 | 61.2 | 0 | 0 | 120 | 120 | 13.2 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-10-17 03:00 | 290 | 10 | Spring | 3 | 16.15 | -13.3 | 6.04 | 61.7 | 0 | 0 | 2.29 | 2.29 | 13.3 | 46.95 | 24.74 | -44.66 | 0 | 0 | 0 | Battery-supported
2025-10-17 04:00 | 290 | 10 | Spring | 4 | 16.15 | -15.3 | 8.51 | 58.3 | 5.4 | 0.32 | 17.6 | 17.92 | 15.3 | 48.31 | 15 | -24.34 | 6.05 | 2.238 | 0 | Diesel-backup
2025-10-17 05:00 | 290 | 10 | Spring | 5 | 16.15 | -18.3 | 7.01 | 32.2 | 103.3 | 5.27 | 6.05 | 11.32 | 18.3 | 55.92 | 15 | 0 | 44.6 | 14.295 | 0 | Diesel-backup
2025-10-17 06:00 | 290 | 10 | Spring | 6 | 16.15 | -15.3 | 5.41 | 14.5 | 229.6 | 13.78 | 0.98 | 14.76 | 15.3 | 49.95 | 15 | 0 | 35.19 | 11.703 | 0 | Diesel-backup
2025-10-17 07:00 | 290 | 10 | Spring | 7 | 16.15 | -13.4 | 16.56 | 53.4 | 221.5 | 13.29 | 120 | 133.29 | 13.4 | 45.64 | 47.26 | 87.65 | 0 | 0 | 0 | Normal
2025-10-17 08:00 | 290 | 10 | Spring | 8 | 16.15 | -13.9 | 4.11 | 28.3 | 368.1 | 22.09 | 0.03 | 22.12 | 13.9 | 59.22 | 32.42 | -37.1 | 0 | 0 | 0 | Battery-supported
2025-10-17 09:00 | 290 | 10 | Spring | 9 | 16.15 | -11.6 | 11.91 | 100 | 136.8 | 8.21 | 83.25 | 91.46 | 11.6 | 50.65 | 47.43 | 40.81 | 0 | 0 | 0 | Normal
2025-10-17 10:00 | 290 | 10 | Spring | 10 | 16.15 | -9.7 | 3.05 | 27.2 | 483 | 28.98 | 0 | 28.98 | 9.7 | 49.81 | 39.1 | -20.83 | 0 | 0 | 0 | Battery-supported
2025-10-17 11:00 | 290 | 10 | Spring | 11 | 16.15 | -12.1 | 7.74 | 96.3 | 178.6 | 10.72 | 10.67 | 21.39 | 12.1 | 53.77 | 26.15 | -32.38 | 0 | 0 | 0 | Battery-supported
2025-10-17 12:00 | 290 | 10 | Spring | 12 | 16.15 | -10.5 | 15.27 | 74.7 | 288.6 | 17.32 | 120 | 137.32 | 10.5 | 52.89 | 57.22 | 84.43 | 0 | 0 | 0 | Normal
2025-10-17 13:00 | 290 | 10 | Spring | 13 | 16.15 | -11.4 | 6.27 | 26.3 | 516.5 | 30.99 | 2.97 | 33.96 | 11.4 | 55.3 | 48.68 | -21.34 | 0 | 0 | 0 | Battery-supported
2025-10-17 14:00 | 290 | 10 | Spring | 14 | 16.15 | -9 | 11.32 | 72.5 | 277.1 | 16.63 | 66.93 | 83.56 | 9 | 52.95 | 59.95 | 30.61 | 0 | 0 | 0 | Normal
2025-10-17 15:00 | 290 | 10 | Spring | 15 | 16.15 | -8.3 | 6.1 | 36.9 | 396.1 | 23.77 | 2.46 | 26.23 | 8.3 | 49.01 | 50.84 | -22.78 | 0 | 0 | 0 | Battery-supported
2025-10-17 16:00 | 290 | 10 | Spring | 16 | 16.15 | -9.9 | 6.9 | 40.8 | 324.3 | 19.46 | 5.5 | 24.96 | 9.9 | 54.04 | 39.2 | -29.08 | 0 | 0 | 0 | Battery-supported
2025-10-17 17:00 | 290 | 10 | Spring | 17 | 16.15 | -10.1 | 12.83 | 43 | 250.3 | 15.02 | 113.67 | 128.69 | 10.1 | 53.61 | 66.83 | 75.08 | 0 | 0 | 0 | Normal
2025-10-17 18:00 | 290 | 10 | Spring | 18 | 16.15 | -11.9 | 11.46 | 41.3 | 177.9 | 10.67 | 70.59 | 81.26 | 11.9 | 55.1 | 76.46 | 26.16 | 0 | 0 | 0 | Normal
2025-10-17 19:00 | 290 | 10 | Spring | 19 | 16.15 | -11.4 | 17.54 | 23 | 112.7 | 6.76 | 120 | 126.76 | 11.4 | 48.42 | 95 | 50.38 | 0 | 0 | 0 | Normal
2025-10-17 20:00 | 290 | 10 | Spring | 20 | 16.15 | -12 | 6.26 | 66.3 | 4.9 | 0.29 | 2.94 | 3.23 | 12 | 56.96 | 73.51 | -53.73 | 0 | 0 | 0 | Battery-supported
2025-10-17 21:00 | 290 | 10 | Spring | 21 | 16.15 | -9.9 | 10.26 | 62.3 | 0 | 0 | 43.24 | 43.24 | 9.9 | 47.37 | 71.86 | -4.13 | 0 | 0 | 0 | Battery-supported
2025-10-17 22:00 | 290 | 10 | Spring | 22 | 16.15 | -13 | 8.8 | 9.8 | 0 | 0 | 20.84 | 20.84 | 13 | 51.11 | 59.75 | -30.27 | 0 | 0 | 0 | Battery-supported
2025-10-17 23:00 | 290 | 10 | Spring | 23 | 16.15 | -12.1 | 10.42 | 16 | 0 | 0 | 46.38 | 46.38 | 12.1 | 47.79 | 59.18 | -1.41 | 0 | 0 | 0 | Battery-supported
2025-10-18 | 291 | 10 | Spring | 0 | 16.32 | -17 | 14.56 | 55.4 | 0 | 0 | 120 | 120 | 17 | 56.35 | 82.61 | 63.65 | 0 | 0 | 0 | Normal
2025-10-18 01:00 | 291 | 10 | Spring | 1 | 16.32 | -8.4 | 5.56 | 4.2 | 0 | 0 | 1.22 | 1.22 | 8.4 | 45.4 | 64.94 | -44.18 | 0 | 0 | 0 | Battery-supported
2025-10-18 02:00 | 291 | 10 | Spring | 2 | 16.32 | -13 | 9.98 | 79.9 | 0 | 0 | 38.08 | 38.08 | 13 | 46.41 | 61.6 | -8.33 | 0 | 0 | 0 | Battery-supported
2025-10-18 03:00 | 291 | 10 | Spring | 3 | 16.32 | -11.9 | 16.39 | 41.1 | 0 | 0 | 120 | 120 | 11.9 | 46.71 | 88.57 | 73.29 | 0 | 0 | 0 | Normal
2025-10-18 04:00 | 291 | 10 | Spring | 4 | 16.32 | -10.1 | 8.77 | 18.5 | 17.4 | 1.04 | 20.49 | 21.53 | 10.1 | 45 | 79.19 | -23.47 | 0 | 0 | 0 | Battery-supported
2025-10-18 05:00 | 291 | 10 | Spring | 5 | 16.32 | -12.9 | 12.73 | 55.1 | 85.2 | 5.11 | 110.06 | 115.17 | 12.9 | 45 | 95 | 42.97 | 0 | 0 | 0 | Normal
2025-10-18 06:00 | 291 | 10 | Spring | 6 | 16.32 | -10.7 | 2.1 | 6.4 | 252.2 | 15.13 | 0 | 15.13 | 10.7 | 48.55 | 81.63 | -33.42 | 0 | 0 | 0 | Battery-supported
2025-10-18 07:00 | 291 | 10 | Spring | 7 | 16.32 | -16.7 | 9 | 28.3 | 295.3 | 17.72 | 23.29 | 41.01 | 16.7 | 50.73 | 77.74 | -9.72 | 0 | 0 | 0 | Battery-supported
2025-10-18 08:00 | 291 | 10 | Spring | 8 | 16.32 | -8.8 | 6.46 | 67.8 | 231.3 | 13.88 | 3.63 | 17.51 | 8.8 | 54.61 | 62.9 | -37.1 | 0 | 0 | 0 | Battery-supported
2025-10-18 09:00 | 291 | 10 | Spring | 9 | 16.32 | -11.6 | 1.28 | 0.5 | 547.4 | 32.84 | 0 | 32.84 | 11.6 | 62.1 | 51.2 | -29.26 | 0 | 0 | 0 | Battery-supported
2025-10-18 10:00 | 291 | 10 | Spring | 10 | 16.32 | -13.4 | 11.32 | 39.9 | 426 | 25.56 | 66.93 | 92.49 | 13.4 | 60.62 | 62.93 | 31.87 | 0 | 0 | 0 | Normal
2025-10-18 11:00 | 291 | 10 | Spring | 11 | 16.32 | -10.5 | 10.02 | 71.2 | 300.2 | 18.01 | 38.79 | 56.8 | 10.5 | 49.69 | 65.54 | 7.11 | 0 | 0 | 0 | Normal
2025-10-18 12:00 | 291 | 10 | Spring | 12 | 16.32 | -15.9 | 4.96 | 66.5 | 328.8 | 19.73 | 0.44 | 20.17 | 15.9 | 56.69 | 50.94 | -36.52 | 0 | 0 | 0 | Battery-supported
2025-10-18 13:00 | 291 | 10 | Spring | 13 | 16.32 | -13.6 | 3.29 | 19.8 | 548.4 | 32.9 | 0 | 32.9 | 13.6 | 58.93 | 40.52 | -26.03 | 0 | 0 | 0 | Battery-supported
2025-10-18 14:00 | 291 | 10 | Spring | 14 | 16.32 | -9.4 | 22.15 | 63.7 | 317.3 | 19.04 | 120 | 139.04 | 9.4 | 54.12 | 71.78 | 84.92 | 0 | 0 | 0 | Normal
2025-10-18 15:00 | 291 | 10 | Spring | 15 | 16.32 | -16.3 | 10.48 | 55.7 | 319.8 | 19.19 | 47.6 | 66.79 | 16.3 | 64.65 | 72.56 | 2.14 | 0 | 0 | 0 | Normal
2025-10-18 16:00 | 291 | 10 | Spring | 16 | 16.32 | -10.6 | 10.34 | 23.8 | 386.7 | 23.2 | 44.79 | 67.99 | 10.6 | 52.18 | 78.38 | 15.81 | 0 | 0 | 0 | Normal
2025-10-18 17:00 | 291 | 10 | Spring | 17 | 16.32 | -10.3 | 5.46 | 39.9 | 262.5 | 15.75 | 1.05 | 16.8 | 10.3 | 48.29 | 65.78 | -31.49 | 0 | 0 | 0 | Battery-supported
2025-10-18 18:00 | 291 | 10 | Spring | 18 | 16.32 | -6.9 | 7 | 46.9 | 171.8 | 10.31 | 6 | 16.31 | 6.9 | 46.23 | 53.82 | -29.92 | 0 | 0 | 0 | Battery-supported
2025-10-18 19:00 | 291 | 10 | Spring | 19 | 16.32 | -14.6 | 16.49 | 53.7 | 86.7 | 5.2 | 120 | 125.2 | 14.6 | 62.4 | 76.93 | 62.8 | 0 | 0 | 0 | Normal
2025-10-18 20:00 | 291 | 10 | Spring | 20 | 16.32 | -7.5 | 8.88 | 49.3 | 12.7 | 0.76 | 21.8 | 22.56 | 7.5 | 51.18 | 65.48 | -28.62 | 0 | 0 | 0 | Battery-supported
2025-10-18 21:00 | 291 | 10 | Spring | 21 | 16.32 | -12.3 | 16.8 | 65.9 | 0 | 0 | 120 | 120 | 12.3 | 50.68 | 90.99 | 69.32 | 0 | 0 | 0 | Normal
2025-10-18 22:00 | 291 | 10 | Spring | 22 | 16.32 | -12.2 | 10.51 | 75.3 | 0 | 0 | 48.21 | 48.21 | 12.2 | 45.9 | 91.84 | 2.31 | 0 | 0 | 0 | Normal
2025-10-18 23:00 | 291 | 10 | Spring | 23 | 16.32 | -14.2 | 14.79 | 28.8 | 0 | 0 | 120 | 120 | 14.2 | 46.32 | 95 | 8.59 | 0 | 0 | 0 | Normal
2025-10-19 | 292 | 10 | Spring | 0 | 16.49 | -14 | 1.97 | 59.8 | 0 | 0 | 0 | 0 | 14 | 51.68 | 74.33 | -51.68 | 0 | 0 | 0 | Battery-supported
2025-10-19 01:00 | 292 | 10 | Spring | 1 | 16.49 | -11.1 | 5.25 | 88.5 | 0 | 0 | 0.75 | 0.75 | 11.1 | 45 | 56.63 | -44.25 | 0 | 0 | 0 | Battery-supported
2025-10-19 02:00 | 292 | 10 | Spring | 2 | 16.49 | -14.8 | 8.75 | 45.6 | 0 | 0 | 20.25 | 20.25 | 14.8 | 51.8 | 44.01 | -31.55 | 0 | 0 | 0 | Battery-supported
2025-10-19 03:00 | 292 | 10 | Spring | 3 | 16.49 | -11.1 | 7.33 | 62.5 | 0 | 0 | 7.86 | 7.86 | 11.1 | 52.64 | 26.1 | -44.78 | 0 | 0 | 0 | Battery-supported
2025-10-19 04:00 | 292 | 10 | Spring | 4 | 16.49 | -14.5 | 11.32 | 100 | 7.6 | 0.46 | 66.93 | 67.39 | 14.5 | 45 | 34.34 | 22.39 | 0 | 0 | 0 | Normal
2025-10-19 05:00 | 292 | 10 | Spring | 5 | 16.49 | -16.1 | 3.28 | 25.8 | 124.2 | 7.45 | 0 | 7.45 | 16.1 | 47.39 | 18.36 | -39.94 | 0 | 0 | 0 | Battery-supported
2025-10-19 06:00 | 292 | 10 | Spring | 6 | 16.49 | -14.8 | 3.33 | 68.5 | 132.2 | 7.93 | 0 | 7.93 | 14.8 | 49.75 | 15 | -8.4 | 33.42 | 11.19 | 0 | Diesel-backup
2025-10-19 07:00 | 292 | 10 | Spring | 7 | 16.49 | -13 | 11.08 | 44 | 254.6 | 15.28 | 60.96 | 76.24 | 13 | 46.18 | 26.06 | 30.06 | 0 | 0 | 0 | Normal
2025-10-19 08:00 | 292 | 10 | Spring | 8 | 16.49 | -14.4 | 14.39 | 33.7 | 354.5 | 21.27 | 120 | 141.27 | 14.4 | 56.94 | 57.1 | 84.33 | 0 | 0 | 0 | Normal
2025-10-19 09:00 | 292 | 10 | Spring | 9 | 16.49 | -13.7 | 6.95 | 74.4 | 243.8 | 14.63 | 5.75 | 20.38 | 13.7 | 65.59 | 39.01 | -45.21 | 0 | 0 | 0 | Battery-supported
2025-10-19 10:00 | 292 | 10 | Spring | 10 | 16.49 | -12.1 | 17.7 | 27 | 485.7 | 29.14 | 120 | 149.14 | 12.1 | 52.53 | 74.56 | 96.61 | 0 | 0 | 0 | Normal
2025-10-19 11:00 | 292 | 10 | Spring | 11 | 16.49 | -11 | 19.99 | 51.5 | 395.3 | 23.72 | 120 | 143.72 | 11 | 53.19 | 95 | 55.53 | 0 | 0 | 0 | Normal
2025-10-19 12:00 | 292 | 10 | Spring | 12 | 16.49 | -13.8 | 8.23 | 48.4 | 418 | 25.08 | 14.81 | 39.89 | 13.8 | 52.88 | 89.8 | -12.99 | 0 | 0 | 0 | Battery-supported
2025-10-19 13:00 | 292 | 10 | Spring | 13 | 16.49 | -15 | 6.8 | 48.2 | 411.4 | 24.68 | 5.03 | 29.71 | 15 | 52.41 | 80.72 | -22.7 | 0 | 0 | 0 | Battery-supported
2025-10-19 14:00 | 292 | 10 | Spring | 14 | 16.49 | -12.2 | 5.87 | 74.9 | 267 | 16.02 | 1.86 | 17.88 | 12.2 | 56.98 | 65.08 | -39.1 | 0 | 0 | 0 | Battery-supported
2025-10-19 15:00 | 292 | 10 | Spring | 15 | 16.49 | -10.9 | 5.23 | 65.6 | 280.2 | 16.81 | 0.72 | 17.53 | 10.9 | 47.44 | 53.12 | -29.91 | 0 | 0 | 0 | Battery-supported
2025-10-19 16:00 | 292 | 10 | Spring | 16 | 16.49 | -14.8 | 12.32 | 40.9 | 329 | 19.74 | 96.03 | 115.77 | 14.8 | 52.61 | 76.36 | 63.16 | 0 | 0 | 0 | Normal
2025-10-19 17:00 | 292 | 10 | Spring | 17 | 16.49 | -13.2 | 4.81 | 62.2 | 202.8 | 12.17 | 0.31 | 12.48 | 13.2 | 56.38 | 58.8 | -43.9 | 0 | 0 | 0 | Battery-supported
2025-10-19 18:00 | 292 | 10 | Spring | 18 | 16.49 | -12.6 | 4.27 | 43.4 | 183.4 | 11 | 0.06 | 11.06 | 12.6 | 57.95 | 40.05 | -46.89 | 0 | 0 | 0 | Battery-supported
2025-10-19 19:00 | 292 | 10 | Spring | 19 | 16.49 | -11.3 | 5.08 | 45.3 | 101.7 | 6.1 | 0.55 | 6.65 | 11.3 | 50.83 | 22.37 | -44.18 | 0 | 0 | 0 | Battery-supported
2025-10-19 20:00 | 292 | 10 | Spring | 20 | 16.49 | -12.5 | 8.28 | 29.7 | 23.7 | 1.42 | 15.29 | 16.71 | 12.5 | 52.54 | 15 | -18.44 | 17.39 | 6.18 | 0 | Diesel-backup
2025-10-19 21:00 | 292 | 10 | Spring | 21 | 16.49 | -9.3 | 8.63 | 19.6 | 0 | 0 | 18.9 | 18.9 | 9.3 | 45 | 15 | 0 | 26.1 | 8.983 | 0 | Diesel-backup
2025-10-19 22:00 | 292 | 10 | Spring | 22 | 16.49 | -14.6 | 11.94 | 12.5 | 0 | 0 | 84.15 | 84.15 | 14.6 | 51.64 | 26.96 | 32.51 | 0 | 0 | 0 | Normal
2025-10-19 23:00 | 292 | 10 | Spring | 23 | 16.49 | -14.7 | 7.83 | 59.1 | 0 | 0 | 11.36 | 11.36 | 14.7 | 49.84 | 15 | -29.91 | 8.57 | 3.142 | 0 | Diesel-backup
2025-10-20 | 293 | 10 | Spring | 0 | 16.66 | -12.1 | 3.12 | 38.1 | 0 | 0 | 0 | 0 | 12.1 | 47.14 | 15 | 0 | 47.14 | 15.085 | 0 | Diesel-backup
2025-10-20 01:00 | 293 | 10 | Spring | 1 | 16.66 | -12.1 | 6.59 | 86.7 | 0 | 0 | 4.13 | 4.13 | 12.1 | 45 | 15 | 0 | 40.87 | 13.294 | 0 | Diesel-backup
2025-10-20 02:00 | 293 | 10 | Spring | 2 | 16.66 | -15.3 | 8.38 | 72.2 | 0 | 0 | 16.27 | 16.27 | 15.3 | 53.55 | 15 | 0 | 37.28 | 12.298 | 0 | Diesel-backup
2025-10-20 03:00 | 293 | 10 | Spring | 3 | 16.66 | -13.8 | 5.63 | 23.4 | 0 | 0 | 1.35 | 1.35 | 13.8 | 46.8 | 15 | 0 | 45.45 | 14.544 | 0 | Diesel-backup
2025-10-20 04:00 | 293 | 10 | Spring | 4 | 16.66 | -13.8 | 9.93 | 49.6 | 25.6 | 1.54 | 37.21 | 38.75 | 13.8 | 52.36 | 15 | 0 | 13.61 | 4.902 | 0 | Diesel-backup
2025-10-20 05:00 | 293 | 10 | Spring | 5 | 16.66 | -14 | 1.36 | 32.1 | 123.5 | 7.41 | 0 | 7.41 | 14 | 46.38 | 15 | 0 | 38.97 | 12.771 | 0 | Diesel-backup
2025-10-20 06:00 | 293 | 10 | Spring | 6 | 16.66 | -13.1 | 7.76 | 64.5 | 144 | 8.64 | 10.82 | 19.46 | 13.1 | 49.4 | 15 | 0 | 29.94 | 10.158 | 0 | Diesel-backup
2025-10-20 07:00 | 293 | 10 | Spring | 7 | 16.66 | -15 | 15.93 | 75.1 | 168.3 | 10.1 | 120 | 130.1 | 15 | 46.98 | 45.59 | 83.12 | 0 | 0 | 0 | Normal
2025-10-20 08:00 | 293 | 10 | Spring | 8 | 16.66 | -10.4 | 14.11 | 64.6 | 246.4 | 14.78 | 120 | 134.78 | 10.4 | 57.25 | 74.12 | 77.53 | 0 | 0 | 0 | Normal
2025-10-20 09:00 | 293 | 10 | Spring | 9 | 16.66 | -12.5 | 8.98 | 87.8 | 189.1 | 11.35 | 23.03 | 34.38 | 12.5 | 50.66 | 67.61 | -16.28 | 0 | 0 | 0 | Battery-supported
2025-10-20 10:00 | 293 | 10 | Spring | 10 | 16.66 | -15.2 | 8.55 | 77.7 | 254.7 | 15.28 | 18.03 | 33.31 | 15.2 | 59.41 | 57.17 | -26.1 | 0 | 0 | 0 | Battery-supported
2025-10-20 11:00 | 293 | 10 | Spring | 11 | 16.66 | -13 | 10.74 | 54.1 | 382.7 | 22.96 | 53.12 | 76.08 | 13 | 51.12 | 66.35 | 24.96 | 0 | 0 | 0 | Normal
2025-10-20 12:00 | 293 | 10 | Spring | 12 | 16.66 | -12.6 | 4.28 | 57.9 | 371 | 22.26 | 0.07 | 22.33 | 12.6 | 53.89 | 53.73 | -31.56 | 0 | 0 | 0 | Battery-supported
2025-10-20 13:00 | 293 | 10 | Spring | 13 | 16.66 | -9.8 | 13.48 | 32.8 | 486 | 29.16 | 120 | 149.16 | 9.8 | 55.36 | 88.25 | 93.8 | 0 | 0 | 0 | Normal
2025-10-20 14:00 | 293 | 10 | Spring | 14 | 16.66 | -13.4 | 17.34 | 35.3 | 448.6 | 26.92 | 120 | 146.92 | 13.4 | 51.84 | 95 | 18.35 | 0 | 0 | 0 | Normal
2025-10-20 15:00 | 293 | 10 | Spring | 15 | 16.66 | -10 | 7.74 | 70.3 | 261.8 | 15.71 | 10.67 | 26.38 | 10 | 54.88 | 83.6 | -28.5 | 0 | 0 | 0 | Battery-supported
2025-10-20 16:00 | 293 | 10 | Spring | 16 | 16.66 | -11.3 | 8.98 | 44.5 | 318.6 | 19.12 | 23.03 | 42.15 | 11.3 | 57.32 | 77.53 | -15.17 | 0 | 0 | 0 | Battery-supported
2025-10-20 17:00 | 293 | 10 | Spring | 17 | 16.66 | -7.8 | 11.99 | 68.6 | 187.2 | 11.23 | 85.65 | 96.88 | 7.8 | 45 | 95 | 47.47 | 0 | 0 | 0 | Normal
2025-10-20 18:00 | 293 | 10 | Spring | 18 | 16.66 | -8 | 5.3 | 66.5 | 139.8 | 8.39 | 0.82 | 9.21 | 8 | 52.9 | 77.52 | -43.69 | 0 | 0 | 0 | Battery-supported
2025-10-20 19:00 | 293 | 10 | Spring | 19 | 16.66 | -10.2 | 17.65 | 41 | 112.7 | 6.76 | 120 | 126.76 | 10.2 | 57.7 | 95 | 47.49 | 0 | 0 | 0 | Normal
2025-10-20 20:00 | 293 | 10 | Spring | 20 | 16.66 | -11.2 | 21.71 | 26.6 | 32.6 | 1.96 | 120 | 121.96 | 11.2 | 51.21 | 95 | 0 | 0 | 0 | 0 | Normal
2025-10-20 21:00 | 293 | 10 | Spring | 21 | 16.66 | -9.6 | 11.25 | 30.7 | 0 | 0 | 65.15 | 65.15 | 9.6 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-10-20 22:00 | 293 | 10 | Spring | 22 | 16.66 | -11.2 | 18.43 | 60.1 | 0 | 0 | 120 | 120 | 11.2 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-10-20 23:00 | 293 | 10 | Spring | 23 | 16.66 | -7.4 | 3.92 | 16.2 | 0 | 0 | 0.01 | 0.01 | 7.4 | 45 | 77 | -44.99 | 0 | 0 | 0 | Battery-supported
2025-10-21 | 294 | 10 | Spring | 0 | 16.83 | -11 | 9.7 | 20 | 0 | 0 | 33.36 | 33.36 | 11 | 50.08 | 70.32 | -16.72 | 0 | 0 | 0 | Battery-supported
2025-10-21 01:00 | 294 | 10 | Spring | 1 | 16.83 | -12.4 | 2.15 | 45.9 | 0 | 0 | 0 | 0 | 12.4 | 45.73 | 52.02 | -45.73 | 0 | 0 | 0 | Battery-supported
2025-10-21 02:00 | 294 | 10 | Spring | 2 | 16.83 | -12.9 | 6.57 | 48.6 | 0 | 0 | 4.05 | 4.05 | 12.9 | 49.9 | 33.68 | -45.85 | 0 | 0 | 0 | Battery-supported
2025-10-21 03:00 | 294 | 10 | Spring | 3 | 16.83 | -15 | 6.66 | 47.5 | 0 | 0 | 4.42 | 4.42 | 15 | 47.5 | 16.45 | -43.08 | 0 | 0 | 0 | Battery-supported
2025-10-21 04:00 | 294 | 10 | Spring | 4 | 16.83 | -11.4 | 5.67 | 14.9 | 45.1 | 2.71 | 1.43 | 4.14 | 11.4 | 45.95 | 15 | -3.63 | 38.18 | 12.551 | 0 | Diesel-backup
2025-10-21 05:00 | 294 | 10 | Spring | 5 | 16.83 | -14.8 | 3.96 | 32.4 | 129.6 | 7.78 | 0.01 | 7.79 | 14.8 | 54.78 | 15 | 0 | 46.99 | 15.037 | 0 | Diesel-backup
2025-10-21 06:00 | 294 | 10 | Spring | 6 | 16.83 | -10.8 | 11.14 | 64.6 | 147.3 | 8.84 | 62.42 | 71.26 | 10.8 | 51.19 | 22.39 | 20.07 | 0 | 0 | 0 | Normal
2025-10-21 07:00 | 294 | 10 | Spring | 7 | 16.83 | -16.2 | 5.03 | 77.4 | 163.8 | 9.83 | 0.5 | 10.33 | 16.2 | 51.81 | 15 | -18.46 | 23.02 | 8.013 | 0 | Diesel-backup
2025-10-21 08:00 | 294 | 10 | Spring | 8 | 16.83 | -13.1 | 11.14 | 70.7 | 226.2 | 13.57 | 62.42 | 75.99 | 13.1 | 55.27 | 22.62 | 20.72 | 0 | 0 | 0 | Normal
2025-10-21 09:00 | 294 | 10 | Spring | 9 | 16.83 | -10.8 | 8.03 | 20.8 | 469.2 | 28.15 | 13.01 | 41.16 | 10.8 | 50.64 | 18.83 | -9.48 | 0 | 0 | 0 | Battery-supported
2025-10-21 10:00 | 294 | 10 | Spring | 10 | 16.83 | -18 | 10.03 | 58.7 | 342 | 20.52 | 38.97 | 59.49 | 18 | 64.21 | 16.94 | -4.72 | 0 | 0 | 0 | Battery-supported
2025-10-21 11:00 | 294 | 10 | Spring | 11 | 16.83 | -8.5 | 6.02 | 69 | 311.1 | 18.67 | 2.24 | 20.91 | 8.5 | 51.02 | 15 | -4.86 | 25.25 | 8.718 | 0 | Diesel-backup
2025-10-21 12:00 | 294 | 10 | Spring | 12 | 16.83 | -13.6 | 7.99 | 12.7 | 593.3 | 35.6 | 12.67 | 48.27 | 13.6 | 61.78 | 15 | 0 | 13.51 | 4.868 | 0 | Diesel-backup
2025-10-21 13:00 | 294 | 10 | Spring | 13 | 16.83 | -12 | 23.75 | 73.7 | 288.2 | 17.29 | 120 | 137.29 | 12 | 48.27 | 47.76 | 89.02 | 0 | 0 | 0 | Normal
2025-10-21 14:00 | 294 | 10 | Spring | 14 | 16.83 | -10.7 | 9.84 | 0 | 610.8 | 36.65 | 35.67 | 72.32 | 10.7 | 51.97 | 55.25 | 20.35 | 0 | 0 | 0 | Normal
2025-10-21 15:00 | 294 | 10 | Spring | 15 | 16.83 | -9.9 | 17.61 | 74.9 | 243.5 | 14.61 | 120 | 134.61 | 9.9 | 52.31 | 85.53 | 82.3 | 0 | 0 | 0 | Normal
2025-10-21 16:00 | 294 | 10 | Spring | 16 | 16.83 | -10.6 | 17.11 | 14.1 | 430.5 | 25.83 | 120 | 145.83 | 10.6 | 55.65 | 95 | 25.72 | 0 | 0 | 0 | Normal
2025-10-21 17:00 | 294 | 10 | Spring | 17 | 16.83 | -8.7 | 28.55 | 31.7 | 297.6 | 17.86 | 0 | 17.86 | 8.7 | 46.53 | 83.53 | -28.67 | 0 | 0 | 0 | Battery-supported
2025-10-21 18:00 | 294 | 10 | Spring | 18 | 16.83 | -9.5 | 3.48 | 29.9 | 221.8 | 13.31 | 0 | 13.31 | 9.5 | 51.96 | 68.07 | -38.65 | 0 | 0 | 0 | Battery-supported
2025-10-21 19:00 | 294 | 10 | Spring | 19 | 16.83 | -6.6 | 17.08 | 44.9 | 113.6 | 6.82 | 120 | 126.82 | 6.6 | 53.5 | 95 | 73.17 | 0 | 0 | 0 | Normal
2025-10-21 20:00 | 294 | 10 | Spring | 20 | 16.83 | -9.3 | 7.99 | 32.9 | 38.3 | 2.3 | 12.67 | 14.97 | 9.3 | 53.56 | 79.56 | -38.59 | 0 | 0 | 0 | Battery-supported
2025-10-21 21:00 | 294 | 10 | Spring | 21 | 16.83 | -6.1 | 6.65 | 78.8 | 0 | 0 | 4.37 | 4.37 | 6.1 | 45 | 63.31 | -40.63 | 0 | 0 | 0 | Battery-supported
2025-10-21 22:00 | 294 | 10 | Spring | 22 | 16.83 | -8.6 | 4.36 | 25.9 | 0 | 0 | 0.09 | 0.09 | 8.6 | 45 | 45.35 | -44.91 | 0 | 0 | 0 | Battery-supported
2025-10-21 23:00 | 294 | 10 | Spring | 23 | 16.83 | -14.8 | 3.5 | 16.1 | 0 | 0 | 0 | 0 | 14.8 | 48.93 | 25.78 | -48.93 | 0 | 0 | 0 | Battery-supported
2025-10-22 | 295 | 10 | Spring | 0 | 17 | -5.2 | 10.92 | 42.7 | 0 | 0 | 57.18 | 57.18 | 5.2 | 45 | 30.26 | 12.18 | 0 | 0 | 0 | Normal
2025-10-22 01:00 | 295 | 10 | Spring | 1 | 17 | -12.6 | 3.4 | 40.9 | 0 | 0 | 0 | 0 | 12.6 | 51.65 | 15 | -38.15 | 13.5 | 4.866 | 0 | Diesel-backup
2025-10-22 02:00 | 295 | 10 | Spring | 2 | 17 | -8.4 | 11.19 | 19.7 | 0 | 0 | 63.65 | 63.65 | 8.4 | 45.09 | 21.83 | 18.56 | 0 | 0 | 0 | Normal
2025-10-22 03:00 | 295 | 10 | Spring | 3 | 17 | -12 | 1.59 | 42.3 | 0 | 0 | 0 | 0 | 12 | 47.51 | 15 | -17.08 | 30.43 | 10.307 | 0 | Diesel-backup
2025-10-22 04:00 | 295 | 10 | Spring | 4 | 17 | -10.1 | 4.58 | 44.5 | 40.5 | 2.43 | 0.18 | 2.61 | 10.1 | 45.81 | 15 | 0 | 43.2 | 13.924 | 0 | Diesel-backup
2025-10-22 05:00 | 295 | 10 | Spring | 5 | 17 | -14.3 | 7.28 | 9.8 | 166.5 | 9.99 | 7.56 | 17.55 | 14.3 | 54.16 | 15 | 0 | 36.61 | 12.108 | 0 | Diesel-backup
2025-10-22 06:00 | 295 | 10 | Spring | 6 | 17 | -11.6 | 8.52 | 88.5 | 98.3 | 5.9 | 17.71 | 23.61 | 11.6 | 54.67 | 15 | 0 | 31.06 | 10.493 | 0 | Diesel-backup
2025-10-22 07:00 | 295 | 10 | Spring | 7 | 17 | -13.7 | 4.74 | 82.6 | 150.5 | 9.03 | 0.27 | 9.3 | 13.7 | 49.03 | 15 | 0 | 39.73 | 12.982 | 0 | Diesel-backup
2025-10-22 08:00 | 295 | 10 | Spring | 8 | 17 | -9.7 | 3.72 | 86.4 | 170.6 | 10.24 | 0 | 10.24 | 9.7 | 53.03 | 15 | 0 | 42.79 | 13.814 | 0 | Diesel-backup
2025-10-22 09:00 | 295 | 10 | Spring | 9 | 17 | -12.2 | 6.8 | 27.9 | 441 | 26.46 | 5.03 | 31.49 | 12.2 | 56.79 | 15 | 0 | 25.3 | 8.734 | 0 | Diesel-backup
2025-10-22 10:00 | 295 | 10 | Spring | 10 | 17 | -11 | 5.74 | 12.3 | 555.4 | 33.32 | 1.57 | 34.89 | 11 | 59.81 | 15 | 0 | 24.92 | 8.615 | 0 | Diesel-backup
2025-10-22 11:00 | 295 | 10 | Spring | 11 | 17 | -17.5 | 6.2 | 76.4 | 275.1 | 16.51 | 2.75 | 19.26 | 17.5 | 63.6 | 15 | 0 | 44.34 | 14.226 | 0 | Diesel-backup
2025-10-22 12:00 | 295 | 10 | Spring | 12 | 17 | -12.6 | 11.51 | 49.8 | 411 | 24.66 | 71.93 | 96.59 | 12.6 | 57.2 | 29.5 | 39.39 | 0 | 0 | 0 | Normal
2025-10-22 13:00 | 295 | 10 | Spring | 13 | 17 | -11.2 | 15.54 | 51.2 | 397 | 23.82 | 120 | 143.82 | 11.2 | 57.29 | 61.34 | 86.53 | 0 | 0 | 0 | Normal
2025-10-22 14:00 | 295 | 10 | Spring | 14 | 17 | -11.2 | 6.56 | 79.9 | 245 | 14.7 | 4.01 | 18.71 | 11.2 | 55.87 | 46.47 | -37.16 | 0 | 0 | 0 | Battery-supported
2025-10-22 15:00 | 295 | 10 | Spring | 15 | 17 | -9.2 | 11.51 | 34.2 | 414.5 | 24.87 | 71.93 | 96.8 | 9.2 | 46.62 | 64.94 | 50.18 | 0 | 0 | 0 | Normal
2025-10-22 16:00 | 295 | 10 | Spring | 16 | 17 | -11.8 | 5.85 | 76.8 | 205.5 | 12.33 | 1.82 | 14.15 | 11.8 | 59.08 | 46.97 | -44.93 | 0 | 0 | 0 | Battery-supported
2025-10-22 17:00 | 295 | 10 | Spring | 17 | 17 | -10.5 | 5.57 | 59.1 | 220.2 | 13.21 | 1.24 | 14.45 | 10.5 | 50.32 | 32.62 | -35.87 | 0 | 0 | 0 | Battery-supported
2025-10-22 18:00 | 295 | 10 | Spring | 18 | 17 | -7.8 | 6.77 | 83.4 | 109.5 | 6.57 | 4.89 | 11.46 | 7.8 | 50.46 | 17.02 | -39 | 0 | 0 | 0 | Battery-supported
2025-10-22 19:00 | 295 | 10 | Spring | 19 | 17 | -15.3 | 14.28 | 57 | 102.8 | 6.17 | 120 | 126.17 | 15.3 | 55.2 | 43.14 | 70.97 | 0 | 0 | 0 | Normal
2025-10-22 20:00 | 295 | 10 | Spring | 20 | 17 | -8.9 | 2.88 | 55 | 35.7 | 2.14 | 0 | 2.14 | 8.9 | 50.85 | 23.65 | -48.71 | 0 | 0 | 0 | Battery-supported
2025-10-22 21:00 | 295 | 10 | Spring | 21 | 17 | -11 | 2.6 | 72.7 | 0 | 0 | 0 | 0 | 11 | 46.96 | 15 | -21.63 | 25.33 | 8.742 | 0 | Diesel-backup
2025-10-22 22:00 | 295 | 10 | Spring | 22 | 17 | -12.4 | 19.39 | 76.4 | 0 | 0 | 120 | 120 | 12.4 | 52.84 | 39.71 | 67.16 | 0 | 0 | 0 | Normal
2025-10-22 23:00 | 295 | 10 | Spring | 23 | 17 | -9.9 | 4.65 | 37 | 0 | 0 | 0.21 | 0.21 | 9.9 | 45 | 21.8 | -44.79 | 0 | 0 | 0 | Battery-supported
2025-10-23 | 296 | 10 | Spring | 0 | 17.18 | -8.1 | 7.31 | 95.9 | 0 | 0 | 7.74 | 7.74 | 8.1 | 48.95 | 15 | -17 | 24.21 | 8.392 | 0 | Diesel-backup
2025-10-23 01:00 | 296 | 10 | Spring | 1 | 17.18 | -8.8 | 6.14 | 26.9 | 0 | 0 | 2.58 | 2.58 | 8.8 | 45 | 15 | 0 | 42.42 | 13.714 | 0 | Diesel-backup
2025-10-23 02:00 | 296 | 10 | Spring | 2 | 17.18 | -11.8 | 17.23 | 41.8 | 0 | 0 | 120 | 120 | 11.8 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-10-23 03:00 | 296 | 10 | Spring | 3 | 17.18 | -10 | 14.15 | 22.9 | 0 | 0 | 120 | 120 | 10 | 45 | 70.2 | 75 | 0 | 0 | 0 | Normal
2025-10-23 04:00 | 296 | 10 | Spring | 4 | 17.18 | -10.3 | 3.67 | 64.2 | 36.6 | 2.2 | 0 | 2.2 | 10.3 | 48.36 | 51.74 | -46.16 | 0 | 0 | 0 | Battery-supported
2025-10-23 05:00 | 296 | 10 | Spring | 5 | 17.18 | -12.8 | 8.53 | 65.3 | 95.9 | 5.75 | 17.81 | 23.56 | 12.8 | 45 | 43.16 | -21.44 | 0 | 0 | 0 | Battery-supported
2025-10-23 06:00 | 296 | 10 | Spring | 6 | 17.18 | -14.3 | 9.85 | 88.3 | 100.9 | 6.05 | 35.84 | 41.89 | 14.3 | 45 | 41.92 | -3.11 | 0 | 0 | 0 | Battery-supported
2025-10-23 07:00 | 296 | 10 | Spring | 7 | 17.18 | -14.4 | 11.29 | 52 | 244.1 | 14.65 | 66.16 | 80.81 | 14.4 | 56.59 | 50.83 | 24.22 | 0 | 0 | 0 | Normal
2025-10-23 08:00 | 296 | 10 | Spring | 8 | 17.18 | -11.2 | 1.95 | 65.9 | 246.8 | 14.81 | 0 | 14.81 | 11.2 | 53.67 | 35.28 | -38.86 | 0 | 0 | 0 | Battery-supported
2025-10-23 09:00 | 296 | 10 | Spring | 9 | 17.18 | -13 | 2.59 | 19.3 | 478.5 | 28.71 | 0 | 28.71 | 13 | 61.95 | 21.99 | -33.24 | 0 | 0 | 0 | Battery-supported
2025-10-23 10:00 | 296 | 10 | Spring | 10 | 17.18 | -15.1 | 11.75 | 76.4 | 261.5 | 15.69 | 78.59 | 94.28 | 15.1 | 62.23 | 33.78 | 32.05 | 0 | 0 | 0 | Normal
2025-10-23 11:00 | 296 | 10 | Spring | 11 | 17.18 | -16.3 | 3.32 | 26 | 519.3 | 31.16 | 0 | 31.16 | 16.3 | 62.53 | 21.24 | -31.37 | 0 | 0 | 0 | Battery-supported
2025-10-23 12:00 | 296 | 10 | Spring | 12 | 17.18 | -10.4 | 9.76 | 73.5 | 294.1 | 17.65 | 34.33 | 51.98 | 10.4 | 58.43 | 18.66 | -6.45 | 0 | 0 | 0 | Battery-supported
2025-10-23 13:00 | 296 | 10 | Spring | 13 | 17.18 | -13.1 | 3.81 | 2.6 | 632.4 | 37.94 | 0 | 37.94 | 13.1 | 55.02 | 15 | -9.14 | 7.94 | 2.918 | 0 | Diesel-backup
2025-10-23 14:00 | 296 | 10 | Spring | 14 | 17.18 | -10.8 | 2.71 | 79.7 | 246.2 | 14.77 | 0 | 14.77 | 10.8 | 49.18 | 15 | 0 | 34.41 | 11.478 | 0 | Diesel-backup
2025-10-23 15:00 | 296 | 10 | Spring | 15 | 17.18 | -8.4 | 4.53 | 20.4 | 474.2 | 28.45 | 0.15 | 28.6 | 8.4 | 53.47 | 15 | 0 | 24.87 | 8.599 | 0 | Diesel-backup
2025-10-23 16:00 | 296 | 10 | Spring | 16 | 17.18 | -13.6 | 7.79 | 49 | 308.8 | 18.53 | 11.05 | 29.58 | 13.6 | 55.19 | 15 | 0 | 25.61 | 8.831 | 0 | Diesel-backup
2025-10-23 17:00 | 296 | 10 | Spring | 17 | 17.18 | -10.5 | 9.5 | 71.7 | 185 | 11.1 | 30.23 | 41.33 | 10.5 | 55.91 | 15 | 0 | 14.58 | 5.233 | 0 | Diesel-backup
2025-10-23 18:00 | 296 | 10 | Spring | 18 | 17.18 | -10.6 | 10.17 | 59.1 | 166.5 | 9.99 | 41.53 | 51.52 | 10.6 | 57.21 | 15 | 0 | 5.69 | 2.107 | 0 | Diesel-backup
2025-10-23 19:00 | 296 | 10 | Spring | 19 | 17.18 | -9.2 | 12.54 | 21.7 | 157.5 | 9.45 | 103.4 | 112.85 | 9.2 | 48.98 | 38.5 | 63.87 | 0 | 0 | 0 | Normal
2025-10-23 20:00 | 296 | 10 | Spring | 20 | 17.18 | -7.3 | 4.7 | 91.1 | 22.4 | 1.34 | 0.24 | 1.58 | 7.3 | 47.93 | 19.96 | -46.35 | 0 | 0 | 0 | Battery-supported
2025-10-23 21:00 | 296 | 10 | Spring | 21 | 17.18 | -13 | 12.14 | 40.4 | 0 | 0 | 90.27 | 90.27 | 13 | 47.64 | 35.65 | 42.63 | 0 | 0 | 0 | Normal
2025-10-23 22:00 | 296 | 10 | Spring | 22 | 17.18 | -9 | 8.24 | 26.3 | 0 | 0 | 14.91 | 14.91 | 9 | 49.08 | 21.98 | -34.17 | 0 | 0 | 0 | Battery-supported
2025-10-23 23:00 | 296 | 10 | Spring | 23 | 17.18 | -8.2 | 9 | 76.9 | 0 | 0 | 23.29 | 23.29 | 8.2 | 45 | 15 | -17.46 | 4.25 | 1.582 | 0 | Diesel-backup
2025-10-24 | 297 | 10 | Spring | 0 | 17.36 | -11 | 24.7 | 38.9 | 0 | 0 | 120 | 120 | 11 | 53.34 | 39.53 | 66.66 | 0 | 0 | 0 | Normal
2025-10-24 01:00 | 297 | 10 | Spring | 1 | 17.36 | -11.2 | 10.97 | 33 | 0 | 0 | 58.34 | 58.34 | 11.2 | 45 | 44.44 | 13.34 | 0 | 0 | 0 | Normal
2025-10-24 02:00 | 297 | 10 | Spring | 2 | 17.36 | -10.4 | 6.93 | 90.8 | 0 | 0 | 5.65 | 5.65 | 10.4 | 51.88 | 25.95 | -46.23 | 0 | 0 | 0 | Battery-supported
2025-10-24 03:00 | 297 | 10 | Spring | 3 | 17.36 | -10.9 | 6.25 | 23 | 0 | 0 | 2.91 | 2.91 | 10.9 | 46.86 | 15 | -27.37 | 16.58 | 5.909 | 0 | Diesel-backup
2025-10-24 04:00 | 297 | 10 | Spring | 4 | 17.36 | -10.8 | 7.81 | 12.7 | 72.7 | 4.36 | 11.21 | 15.57 | 10.8 | 47.94 | 15 | 0 | 32.37 | 10.882 | 0 | Diesel-backup
2025-10-24 05:00 | 297 | 10 | Spring | 5 | 17.36 | -11.1 | 2.97 | 24.8 | 159.7 | 9.58 | 0 | 9.58 | 11.1 | 48.4 | 15 | 0 | 38.82 | 12.729 | 0 | Diesel-backup
2025-10-24 06:00 | 297 | 10 | Spring | 6 | 17.36 | -14.8 | 9.71 | 83.4 | 114.4 | 6.86 | 33.52 | 40.38 | 14.8 | 45 | 15 | 0 | 4.62 | 1.717 | 0 | Diesel-backup
2025-10-24 07:00 | 297 | 10 | Spring | 7 | 17.36 | -10.6 | 7.75 | 54.4 | 240 | 14.4 | 10.74 | 25.14 | 10.6 | 45 | 15 | 0 | 19.86 | 6.994 | 0 | Diesel-backup
2025-10-24 08:00 | 297 | 10 | Spring | 8 | 17.36 | -10.2 | 8.91 | 79.7 | 197.7 | 11.86 | 22.16 | 34.02 | 10.2 | 52.61 | 15 | 0 | 18.59 | 6.577 | 0 | Diesel-backup
2025-10-24 09:00 | 297 | 10 | Spring | 9 | 17.36 | -12.3 | 8.18 | 80.2 | 223.6 | 13.42 | 14.35 | 27.77 | 12.3 | 60.15 | 15 | 0 | 32.38 | 10.885 | 0 | Diesel-backup
2025-10-24 10:00 | 297 | 10 | Spring | 10 | 17.36 | -15.9 | 3.19 | 61.1 | 332.1 | 19.93 | 0 | 19.93 | 15.9 | 58.57 | 15 | 0 | 38.64 | 12.679 | 0 | Diesel-backup
2025-10-24 11:00 | 297 | 10 | Spring | 11 | 17.36 | -12.6 | 11.19 | 59.6 | 356.9 | 21.41 | 63.65 | 85.06 | 12.6 | 61.3 | 23.74 | 23.76 | 0 | 0 | 0 | Normal
2025-10-24 12:00 | 297 | 10 | Spring | 12 | 17.36 | -11.6 | 5.44 | 26.5 | 525.4 | 31.52 | 1.02 | 32.54 | 11.6 | 61.89 | 15 | -21.86 | 7.49 | 2.757 | 0 | Diesel-backup
2025-10-24 13:00 | 297 | 10 | Spring | 13 | 17.36 | -14.2 | 13.31 | 62.2 | 344.4 | 20.66 | 120 | 140.66 | 14.2 | 59.55 | 44.85 | 81.11 | 0 | 0 | 0 | Normal
2025-10-24 14:00 | 297 | 10 | Spring | 14 | 17.36 | -12.1 | 11.72 | 90.9 | 195.4 | 11.72 | 77.74 | 89.46 | 12.1 | 55.88 | 57.21 | 33.58 | 0 | 0 | 0 | Normal
2025-10-24 15:00 | 297 | 10 | Spring | 15 | 17.36 | -14 | 18.66 | 98.7 | 145.8 | 8.75 | 120 | 128.75 | 14 | 52.92 | 85.11 | 75.83 | 0 | 0 | 0 | Normal
2025-10-24 16:00 | 297 | 10 | Spring | 16 | 17.36 | -9.2 | 7.79 | 62.3 | 261.9 | 15.71 | 11.05 | 26.76 | 9.2 | 54.78 | 73.9 | -28.02 | 0 | 0 | 0 | Battery-supported
2025-10-24 17:00 | 297 | 10 | Spring | 17 | 17.36 | -9.9 | 12.5 | 62.5 | 215.2 | 12.91 | 102.03 | 114.94 | 9.9 | 51.69 | 95 | 57.33 | 0 | 0 | 0 | Normal
2025-10-24 18:00 | 297 | 10 | Spring | 18 | 17.36 | -13.6 | 19.82 | 62.2 | 163.2 | 9.79 | 120 | 129.79 | 13.6 | 62.24 | 95 | 0 | 0 | 0 | 0 | Normal
2025-10-24 19:00 | 297 | 10 | Spring | 19 | 17.36 | -9.1 | 5.14 | 48 | 125.6 | 7.54 | 0.62 | 8.16 | 9.1 | 46.32 | 79.74 | -38.16 | 0 | 0 | 0 | Battery-supported
2025-10-24 20:00 | 297 | 10 | Spring | 20 | 17.36 | -9.9 | 14.21 | 39.5 | 56.5 | 3.39 | 120 | 123.39 | 9.9 | 50.29 | 95 | 41.48 | 0 | 0 | 0 | Normal
2025-10-24 21:00 | 297 | 10 | Spring | 21 | 17.36 | -8.7 | 10.86 | 74.1 | 0 | 0 | 55.8 | 55.8 | 8.7 | 47.5 | 95 | 0 | 0 | 0 | 0 | Normal
2025-10-24 22:00 | 297 | 10 | Spring | 22 | 17.36 | -10.9 | 4.12 | 11 | 0 | 0 | 0.03 | 0.03 | 10.9 | 52.87 | 73.86 | -52.84 | 0 | 0 | 0 | Battery-supported
2025-10-24 23:00 | 297 | 10 | Spring | 23 | 17.36 | -12 | 7.24 | 33.5 | 0 | 0 | 7.32 | 7.32 | 12 | 49.99 | 56.8 | -42.67 | 0 | 0 | 0 | Battery-supported
2025-10-25 | 298 | 10 | Spring | 0 | 17.54 | -12 | 26.74 | 64.3 | 0 | 0 | 120 | 120 | 12 | 52.21 | 81.74 | 67.79 | 0 | 0 | 0 | Normal
2025-10-25 01:00 | 298 | 10 | Spring | 1 | 17.54 | -11.9 | 13.73 | 25.8 | 0 | 0 | 120 | 120 | 11.9 | 47.75 | 95 | 36.03 | 0 | 0 | 0 | Normal
2025-10-25 02:00 | 298 | 10 | Spring | 2 | 17.54 | -11.1 | 10.24 | 30.7 | 0 | 0 | 42.85 | 42.85 | 11.1 | 53.05 | 90.92 | -10.2 | 0 | 0 | 0 | Battery-supported
2025-10-25 03:00 | 298 | 10 | Spring | 3 | 17.54 | -11.2 | 5.22 | 55 | 0 | 0 | 0.71 | 0.71 | 11.2 | 47.33 | 72.27 | -46.62 | 0 | 0 | 0 | Battery-supported
2025-10-25 04:00 | 298 | 10 | Spring | 4 | 17.54 | -12.3 | 1.61 | 44.5 | 59.9 | 3.59 | 0 | 3.59 | 12.3 | 49.53 | 53.9 | -45.94 | 0 | 0 | 0 | Battery-supported
2025-10-25 05:00 | 298 | 10 | Spring | 5 | 17.54 | -13.1 | 3.33 | 41 | 141.4 | 8.48 | 0 | 8.48 | 13.1 | 49.13 | 37.64 | -40.65 | 0 | 0 | 0 | Battery-supported
2025-10-25 06:00 | 298 | 10 | Spring | 6 | 17.54 | -13.2 | 7.95 | 38.2 | 222.6 | 13.36 | 12.33 | 25.69 | 13.2 | 47.36 | 28.97 | -21.67 | 0 | 0 | 0 | Battery-supported
2025-10-25 07:00 | 298 | 10 | Spring | 7 | 17.54 | -7 | 7.95 | 52.5 | 248.6 | 14.92 | 12.33 | 27.25 | 7 | 45 | 21.87 | -17.75 | 0 | 0 | 0 | Battery-supported
2025-10-25 08:00 | 298 | 10 | Spring | 8 | 17.54 | -14.3 | 15.82 | 51.6 | 303.1 | 18.19 | 120 | 138.19 | 14.3 | 58.53 | 51.18 | 79.66 | 0 | 0 | 0 | Normal
2025-10-25 09:00 | 298 | 10 | Spring | 9 | 17.54 | -13.8 | 4.44 | 58.5 | 316.4 | 18.98 | 0.12 | 19.1 | 13.8 | 58.85 | 35.28 | -39.75 | 0 | 0 | 0 | Battery-supported
2025-10-25 10:00 | 298 | 10 | Spring | 10 | 17.54 | -5.1 | 4.2 | 39 | 434.5 | 26.07 | 0.05 | 26.12 | 5.1 | 45 | 27.73 | -18.88 | 0 | 0 | 0 | Battery-supported
2025-10-25 11:00 | 298 | 10 | Spring | 11 | 17.54 | -11.2 | 10.92 | 50.7 | 400 | 24 | 57.18 | 81.18 | 11.2 | 50.96 | 38.85 | 30.22 | 0 | 0 | 0 | Normal
2025-10-25 12:00 | 298 | 10 | Spring | 12 | 17.54 | -14.9 | 6.3 | 54.6 | 387.4 | 23.24 | 3.07 | 26.31 | 14.9 | 56.05 | 26.96 | -29.74 | 0 | 0 | 0 | Battery-supported
2025-10-25 13:00 | 298 | 10 | Spring | 13 | 17.54 | -9.6 | 6.26 | 41.7 | 443.6 | 26.62 | 2.94 | 29.56 | 9.6 | 46.86 | 20.04 | -17.3 | 0 | 0 | 0 | Battery-supported
2025-10-25 14:00 | 298 | 10 | Spring | 14 | 17.54 | -13.1 | 14.95 | 52.7 | 371.3 | 22.28 | 120 | 142.28 | 13.1 | 52.59 | 53.04 | 89.69 | 0 | 0 | 0 | Normal
2025-10-25 15:00 | 298 | 10 | Spring | 15 | 17.54 | -8.7 | 4.03 | 98.1 | 149 | 8.94 | 0.02 | 8.96 | 8.7 | 54.75 | 34.73 | -45.79 | 0 | 0 | 0 | Battery-supported
2025-10-25 16:00 | 298 | 10 | Spring | 16 | 17.54 | -10.8 | 13.72 | 81.3 | 192.9 | 11.57 | 120 | 131.57 | 10.8 | 55.28 | 62.8 | 76.29 | 0 | 0 | 0 | Normal
2025-10-25 17:00 | 298 | 10 | Spring | 17 | 17.54 | -11 | 10.17 | 73.4 | 184.4 | 11.06 | 41.53 | 52.59 | 11 | 58.12 | 60.59 | -5.53 | 0 | 0 | 0 | Battery-supported
2025-10-25 18:00 | 298 | 10 | Spring | 18 | 17.54 | -6.3 | 5.9 | 46.2 | 204.1 | 12.25 | 1.93 | 14.18 | 6.3 | 53.15 | 45 | -38.97 | 0 | 0 | 0 | Battery-supported
2025-10-25 19:00 | 298 | 10 | Spring | 19 | 17.54 | -8.4 | 7.8 | 43.1 | 138.2 | 8.29 | 11.13 | 19.42 | 8.4 | 55.57 | 30.54 | -36.15 | 0 | 0 | 0 | Battery-supported
2025-10-25 20:00 | 298 | 10 | Spring | 20 | 17.54 | -7.5 | 4.75 | 49.1 | 56.8 | 3.41 | 0.27 | 3.68 | 7.5 | 50.88 | 15 | -38.85 | 8.35 | 3.063 | 0 | Diesel-backup
2025-10-25 21:00 | 298 | 10 | Spring | 21 | 17.54 | -8.7 | 7.05 | 0 | 0 | 0 | 6.26 | 6.26 | 8.7 | 49.3 | 15 | 0 | 43.04 | 13.881 | 0 | Diesel-backup
2025-10-25 22:00 | 298 | 10 | Spring | 22 | 17.54 | -10.8 | 19.15 | 28.7 | 0 | 0 | 120 | 120 | 10.8 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-10-25 23:00 | 298 | 10 | Spring | 23 | 17.54 | -8.7 | 5.1 | 9.1 | 0 | 0 | 0.57 | 0.57 | 8.7 | 49.1 | 23.19 | -48.53 | 0 | 0 | 0 | Battery-supported
2025-10-26 | 299 | 10 | Spring | 0 | 17.72 | -7.5 | 2.33 | 56.1 | 0 | 0 | 0 | 0 | 7.5 | 46.25 | 15 | -20.47 | 25.78 | 8.884 | 0 | Diesel-backup
2025-10-26 01:00 | 299 | 10 | Spring | 1 | 17.72 | -10.2 | 7.92 | 92.8 | 0 | 0 | 12.09 | 12.09 | 10.2 | 48.01 | 15 | 0 | 35.92 | 11.912 | 0 | Diesel-backup
2025-10-26 02:00 | 299 | 10 | Spring | 2 | 17.72 | -6.9 | 17.25 | 51.5 | 0 | 0 | 120 | 120 | 6.9 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-10-26 03:00 | 299 | 10 | Spring | 3 | 17.72 | -9.4 | 9 | 100 | 0 | 0 | 23.29 | 23.29 | 9.4 | 45 | 33.92 | -21.71 | 0 | 0 | 0 | Battery-supported
2025-10-26 04:00 | 299 | 10 | Spring | 4 | 17.72 | -11.2 | 6.76 | 86.8 | 34.7 | 2.08 | 4.85 | 6.93 | 11.2 | 46.39 | 18.13 | -39.46 | 0 | 0 | 0 | Battery-supported
2025-10-26 05:00 | 299 | 10 | Spring | 5 | 17.72 | -11.4 | 6.58 | 26.1 | 170.7 | 10.24 | 4.09 | 14.33 | 11.4 | 45 | 15 | -7.83 | 22.84 | 7.957 | 0 | Diesel-backup
2025-10-26 06:00 | 299 | 10 | Spring | 6 | 17.72 | -11.9 | 13.89 | 52.2 | 193.7 | 11.62 | 120 | 131.62 | 11.9 | 51.23 | 44.58 | 80.39 | 0 | 0 | 0 | Normal
2025-10-26 07:00 | 299 | 10 | Spring | 7 | 17.72 | -15.1 | 9.66 | 73.3 | 186.7 | 11.2 | 32.72 | 43.92 | 15.1 | 48.36 | 42.81 | -4.44 | 0 | 0 | 0 | Battery-supported
2025-10-26 08:00 | 299 | 10 | Spring | 8 | 17.72 | -12.6 | 3.77 | 41.7 | 342.1 | 20.53 | 0 | 20.53 | 12.6 | 54.11 | 29.38 | -33.58 | 0 | 0 | 0 | Battery-supported
2025-10-26 09:00 | 299 | 10 | Spring | 9 | 17.72 | -11.9 | 10.86 | 47.3 | 364.6 | 21.88 | 55.8 | 77.68 | 11.9 | 47.77 | 40.38 | 29.91 | 0 | 0 | 0 | Normal
2025-10-26 10:00 | 299 | 10 | Spring | 10 | 17.72 | -13.1 | 8.56 | 63.7 | 321.2 | 19.27 | 18.13 | 37.4 | 13.1 | 52.06 | 34.52 | -14.66 | 0 | 0 | 0 | Battery-supported
2025-10-26 11:00 | 299 | 10 | Spring | 11 | 17.72 | -11.2 | 12.61 | 13.8 | 578.7 | 34.72 | 105.82 | 140.54 | 11.2 | 64.85 | 62.37 | 75.69 | 0 | 0 | 0 | Normal
2025-10-26 12:00 | 299 | 10 | Spring | 12 | 17.72 | -11.6 | 19.08 | 66.2 | 330.4 | 19.82 | 120 | 139.82 | 11.6 | 52.18 | 94.62 | 87.64 | 0 | 0 | 0 | Normal
2025-10-26 13:00 | 299 | 10 | Spring | 13 | 17.72 | -9.6 | 20.37 | 31.6 | 492.7 | 29.56 | 120 | 149.56 | 9.6 | 56.83 | 95 | 1.02 | 0 | 0 | 0 | Normal
2025-10-26 14:00 | 299 | 10 | Spring | 14 | 17.72 | -9.4 | 7.84 | 44 | 412.2 | 24.73 | 11.44 | 36.17 | 9.4 | 47.37 | 90.52 | -11.2 | 0 | 0 | 0 | Battery-supported
2025-10-26 15:00 | 299 | 10 | Spring | 15 | 17.72 | -10.1 | 9.56 | 36 | 412.5 | 24.75 | 31.15 | 55.9 | 10.1 | 47.8 | 93.5 | 8.1 | 0 | 0 | 0 | Normal
2025-10-26 16:00 | 299 | 10 | Spring | 16 | 17.72 | -13.2 | 18.62 | 52 | 303.6 | 18.22 | 120 | 138.22 | 13.2 | 56.16 | 95 | 4.07 | 0 | 0 | 0 | Normal
2025-10-26 17:00 | 299 | 10 | Spring | 17 | 17.72 | -5.9 | 8.55 | 58.6 | 232.4 | 13.94 | 18.03 | 31.97 | 5.9 | 49.19 | 88.11 | -17.22 | 0 | 0 | 0 | Battery-supported
2025-10-26 18:00 | 299 | 10 | Spring | 18 | 17.72 | -9.9 | 13.78 | 69.5 | 152.6 | 9.16 | 120 | 129.16 | 9.9 | 50.53 | 95 | 18.72 | 0 | 0 | 0 | Normal
2025-10-26 19:00 | 299 | 10 | Spring | 19 | 17.72 | -9.6 | 4.53 | 19.1 | 181.8 | 10.91 | 0.15 | 11.06 | 9.6 | 52.61 | 78.38 | -41.55 | 0 | 0 | 0 | Battery-supported
2025-10-26 20:00 | 299 | 10 | Spring | 20 | 17.72 | -10.1 | 4.96 | 16.7 | 87 | 5.22 | 0.44 | 5.66 | 10.1 | 50.03 | 60.63 | -44.37 | 0 | 0 | 0 | Battery-supported
2025-10-26 21:00 | 299 | 10 | Spring | 21 | 17.72 | -10.5 | 21.58 | 28.3 | 0 | 0 | 120 | 120 | 10.5 | 50.39 | 86.25 | 69.61 | 0 | 0 | 0 | Normal
2025-10-26 22:00 | 299 | 10 | Spring | 22 | 17.72 | -6.2 | 12.01 | 21.8 | 0 | 0 | 86.26 | 86.26 | 6.2 | 49.28 | 95 | 23.78 | 0 | 0 | 0 | Normal
2025-10-26 23:00 | 299 | 10 | Spring | 23 | 17.72 | -6.8 | 7.24 | 56.3 | 0 | 0 | 7.32 | 7.32 | 6.8 | 46.01 | 79.52 | -38.69 | 0 | 0 | 0 | Battery-supported
2025-10-27 | 300 | 10 | Spring | 0 | 17.9 | -9 | 5.66 | 81.2 | 0 | 0 | 1.41 | 1.41 | 9 | 45 | 62.09 | -43.59 | 0 | 0 | 0 | Battery-supported
2025-10-27 01:00 | 300 | 10 | Spring | 1 | 17.9 | -10.5 | 6.56 | 0 | 0 | 0 | 4.01 | 4.01 | 10.5 | 47.32 | 44.76 | -43.31 | 0 | 0 | 0 | Battery-supported
2025-10-27 02:00 | 300 | 10 | Spring | 2 | 17.9 | -9.3 | 3.4 | 49 | 0 | 0 | 0 | 0 | 9.3 | 45 | 26.76 | -45 | 0 | 0 | 0 | Battery-supported
2025-10-27 03:00 | 300 | 10 | Spring | 3 | 17.9 | -10.9 | 11.4 | 21.2 | 0 | 0 | 69.01 | 69.01 | 10.9 | 45 | 35.6 | 24.01 | 0 | 0 | 0 | Normal
2025-10-27 04:00 | 300 | 10 | Spring | 4 | 17.9 | -11.9 | 10.76 | 56.6 | 62.7 | 3.76 | 53.56 | 57.32 | 11.9 | 49.76 | 38.38 | 7.56 | 0 | 0 | 0 | Normal
2025-10-27 05:00 | 300 | 10 | Spring | 5 | 17.9 | -11 | 10.61 | 32.1 | 167.1 | 10.03 | 50.31 | 60.34 | 11 | 46.46 | 43.49 | 13.88 | 0 | 0 | 0 | Normal
2025-10-27 06:00 | 300 | 10 | Spring | 6 | 17.9 | -13 | 16.28 | 68.4 | 158.2 | 9.49 | 120 | 129.49 | 13 | 48.48 | 73.3 | 81.01 | 0 | 0 | 0 | Normal
2025-10-27 07:00 | 300 | 10 | Spring | 7 | 17.9 | -11.6 | 8.24 | 63.2 | 220.6 | 13.24 | 14.91 | 28.15 | 11.6 | 46.81 | 65.84 | -18.66 | 0 | 0 | 0 | Battery-supported
2025-10-27 08:00 | 300 | 10 | Spring | 8 | 17.9 | -11.7 | 10.1 | 27.7 | 396.9 | 23.81 | 40.24 | 64.05 | 11.7 | 51.12 | 70.6 | 12.93 | 0 | 0 | 0 | Normal
2025-10-27 09:00 | 300 | 10 | Spring | 9 | 17.9 | -10.8 | 2.4 | 63.1 | 298.9 | 17.93 | 0 | 17.93 | 10.8 | 49.75 | 57.87 | -31.82 | 0 | 0 | 0 | Battery-supported
2025-10-27 10:00 | 300 | 10 | Spring | 10 | 17.9 | -13.4 | 12.04 | 38.9 | 436.4 | 26.18 | 87.17 | 113.35 | 13.4 | 55.28 | 79.24 | 58.07 | 0 | 0 | 0 | Normal
2025-10-27 11:00 | 300 | 10 | Spring | 11 | 17.9 | -10.2 | 10.91 | 62.1 | 345.1 | 20.71 | 56.95 | 77.66 | 10.2 | 52.43 | 88.52 | 25.23 | 0 | 0 | 0 | Normal
2025-10-27 12:00 | 300 | 10 | Spring | 12 | 17.9 | -13.4 | 3.7 | 34.9 | 484.3 | 29.06 | 0 | 29.06 | 13.4 | 58.06 | 76.92 | -29 | 0 | 0 | 0 | Battery-supported
2025-10-27 13:00 | 300 | 10 | Spring | 13 | 17.9 | -12.3 | 7.23 | 56.3 | 373 | 22.38 | 7.26 | 29.64 | 12.3 | 58.85 | 65.24 | -29.21 | 0 | 0 | 0 | Battery-supported
2025-10-27 14:00 | 300 | 10 | Spring | 14 | 17.9 | -11.9 | 15.03 | 51 | 380.5 | 22.83 | 120 | 142.83 | 11.9 | 54.2 | 95 | 80.88 | 0 | 0 | 0 | Normal
2025-10-27 15:00 | 300 | 10 | Spring | 15 | 17.9 | -12.7 | 9.92 | 66.4 | 284.5 | 17.07 | 37.04 | 54.11 | 12.7 | 56.41 | 94.08 | -2.3 | 0 | 0 | 0 | Battery-supported
2025-10-27 16:00 | 300 | 10 | Spring | 16 | 17.9 | -7.7 | 5.38 | 77.1 | 211.3 | 12.68 | 0.93 | 13.61 | 7.7 | 54.38 | 77.77 | -40.77 | 0 | 0 | 0 | Battery-supported
2025-10-27 17:00 | 300 | 10 | Spring | 17 | 17.9 | -11.8 | 10.93 | 22.9 | 347.2 | 20.83 | 57.41 | 78.24 | 11.8 | 53.8 | 86.77 | 24.44 | 0 | 0 | 0 | Normal
2025-10-27 18:00 | 300 | 10 | Spring | 18 | 17.9 | -10.9 | 20.38 | 3.9 | 315.3 | 18.92 | 120 | 138.92 | 10.9 | 55.63 | 95 | 22.38 | 0 | 0 | 0 | Normal
2025-10-27 19:00 | 300 | 10 | Spring | 19 | 17.9 | -6.5 | 2.98 | 52.5 | 133.4 | 8 | 0 | 8 | 6.5 | 50.37 | 78.05 | -42.37 | 0 | 0 | 0 | Battery-supported
2025-10-27 20:00 | 300 | 10 | Spring | 20 | 17.9 | -10.4 | 11.79 | 86.1 | 38.5 | 2.31 | 79.74 | 82.05 | 10.4 | 52.12 | 89.07 | 29.93 | 0 | 0 | 0 | Normal
2025-10-27 21:00 | 300 | 10 | Spring | 21 | 17.9 | -9.7 | 9.7 | 52.7 | 0 | 0 | 33.36 | 33.36 | 9.7 | 45 | 84.41 | -11.64 | 0 | 0 | 0 | Battery-supported
2025-10-27 22:00 | 300 | 10 | Spring | 22 | 17.9 | -11.6 | 3.46 | 35.6 | 0 | 0 | 0 | 0 | 11.6 | 45 | 66.41 | -45 | 0 | 0 | 0 | Battery-supported
2025-10-27 23:00 | 300 | 10 | Spring | 23 | 17.9 | -7.8 | 9.96 | 30.5 | 0 | 0 | 37.73 | 37.73 | 7.8 | 46.96 | 62.72 | -9.23 | 0 | 0 | 0 | Battery-supported
2025-10-28 | 301 | 10 | Spring | 0 | 18.09 | -7.9 | 5.69 | 77.7 | 0 | 0 | 1.47 | 1.47 | 7.9 | 45 | 45.31 | -43.53 | 0 | 0 | 0 | Battery-supported
2025-10-28 01:00 | 301 | 10 | Spring | 1 | 18.09 | -8.5 | 6.75 | 54.2 | 0 | 0 | 4.8 | 4.8 | 8.5 | 50.6 | 26.99 | -45.8 | 0 | 0 | 0 | Battery-supported
2025-10-28 02:00 | 301 | 10 | Spring | 2 | 18.09 | -9.3 | 10.92 | 70.3 | 0 | 0 | 57.18 | 57.18 | 9.3 | 45 | 31.47 | 12.18 | 0 | 0 | 0 | Normal
2025-10-28 03:00 | 301 | 10 | Spring | 3 | 18.09 | -10.7 | 10.68 | 52.7 | 3 | 0.18 | 51.81 | 51.99 | 10.7 | 45 | 34.04 | 6.99 | 0 | 0 | 0 | Normal
2025-10-28 04:00 | 301 | 10 | Spring | 4 | 18.09 | -12.4 | 10.55 | 29.8 | 91.8 | 5.51 | 49.04 | 54.55 | 12.4 | 45.23 | 37.47 | 9.32 | 0 | 0 | 0 | Normal
2025-10-28 05:00 | 301 | 10 | Spring | 5 | 18.09 | -13.3 | 26.38 | 24.1 | 186.7 | 11.2 | 120 | 131.2 | 13.3 | 45 | 69.19 | 86.2 | 0 | 0 | 0 | Normal
2025-10-28 06:00 | 301 | 10 | Spring | 6 | 18.09 | -8.9 | 7.39 | 48.8 | 209.8 | 12.59 | 8.24 | 20.83 | 8.9 | 45 | 59.52 | -24.17 | 0 | 0 | 0 | Battery-supported
2025-10-28 07:00 | 301 | 10 | Spring | 7 | 18.09 | -10.3 | 3.97 | 24.3 | 346.4 | 20.78 | 0.01 | 20.79 | 10.3 | 45.7 | 49.56 | -24.91 | 0 | 0 | 0 | Battery-supported
2025-10-28 08:00 | 301 | 10 | Spring | 8 | 18.09 | -13.5 | 11.83 | 73.3 | 226.8 | 13.61 | 80.9 | 94.51 | 13.5 | 50.24 | 65.85 | 44.27 | 0 | 0 | 0 | Normal
2025-10-28 09:00 | 301 | 10 | Spring | 9 | 18.09 | -11.8 | 9.62 | 61.7 | 305.4 | 18.32 | 32.08 | 50.4 | 11.8 | 48.74 | 66.46 | 1.66 | 0 | 0 | 0 | Normal
2025-10-28 10:00 | 301 | 10 | Spring | 10 | 18.09 | -12.4 | 5.87 | 57.5 | 350.9 | 21.05 | 1.86 | 22.91 | 12.4 | 55.62 | 53.38 | -32.71 | 0 | 0 | 0 | Battery-supported
2025-10-28 11:00 | 301 | 10 | Spring | 11 | 18.09 | -14 | 5.62 | 47.4 | 416.2 | 24.97 | 1.33 | 26.3 | 14 | 57.29 | 40.98 | -30.99 | 0 | 0 | 0 | Battery-supported
2025-10-28 12:00 | 301 | 10 | Spring | 12 | 18.09 | -10.8 | 16.82 | 60 | 360.6 | 21.64 | 120 | 141.64 | 10.8 | 55.79 | 72.58 | 85.85 | 0 | 0 | 0 | Normal
2025-10-28 13:00 | 301 | 10 | Spring | 13 | 18.09 | -11.8 | 1.79 | 36.8 | 467.8 | 28.07 | 0 | 28.07 | 11.8 | 55.72 | 61.52 | -27.65 | 0 | 0 | 0 | Battery-supported
2025-10-28 14:00 | 301 | 10 | Spring | 14 | 18.09 | -12.6 | 9.5 | 37 | 445.4 | 26.72 | 30.23 | 56.95 | 12.6 | 55.37 | 62.1 | 1.58 | 0 | 0 | 0 | Normal
2025-10-28 15:00 | 301 | 10 | Spring | 15 | 18.09 | -13.4 | 5.48 | 69.9 | 270.9 | 16.25 | 1.09 | 17.34 | 13.4 | 58.68 | 45.56 | -41.34 | 0 | 0 | 0 | Battery-supported
2025-10-28 16:00 | 301 | 10 | Spring | 16 | 18.09 | -13.2 | 10.28 | 60 | 277.1 | 16.63 | 43.62 | 60.25 | 13.2 | 59.83 | 45.72 | 0.42 | 0 | 0 | 0 | Normal
2025-10-28 17:00 | 301 | 10 | Spring | 17 | 18.09 | -10.2 | 4.95 | 90 | 137.8 | 8.27 | 0.43 | 8.7 | 10.2 | 53.45 | 27.82 | -44.75 | 0 | 0 | 0 | Battery-supported
2025-10-28 18:00 | 301 | 10 | Spring | 18 | 18.09 | -9.4 | 10.42 | 32.5 | 250.3 | 15.02 | 46.38 | 61.4 | 9.4 | 54.42 | 30.38 | 6.98 | 0 | 0 | 0 | Normal
2025-10-28 19:00 | 301 | 10 | Spring | 19 | 18.09 | -11 | 14.49 | 67.5 | 112.6 | 6.76 | 120 | 126.76 | 11 | 45 | 60.47 | 81.76 | 0 | 0 | 0 | Normal
2025-10-28 20:00 | 301 | 10 | Spring | 20 | 18.09 | -7.6 | 5.97 | 61 | 64.1 | 3.85 | 2.11 | 5.96 | 7.6 | 48.84 | 43.32 | -42.88 | 0 | 0 | 0 | Battery-supported
2025-10-28 21:00 | 301 | 10 | Spring | 21 | 18.09 | -9.2 | 6.54 | 70.6 | 2.3 | 0.14 | 3.93 | 4.07 | 9.2 | 49.95 | 24.97 | -45.88 | 0 | 0 | 0 | Battery-supported
2025-10-28 22:00 | 301 | 10 | Spring | 22 | 18.09 | -7.9 | 10.19 | 50.9 | 0 | 0 | 41.91 | 41.91 | 7.9 | 45 | 23.73 | -3.09 | 0 | 0 | 0 | Battery-supported
2025-10-28 23:00 | 301 | 10 | Spring | 23 | 18.09 | -9.8 | 12.41 | 64.8 | 0 | 0 | 99 | 99 | 9.8 | 46.8 | 42.94 | 52.2 | 0 | 0 | 0 | Normal
2025-10-29 | 302 | 10 | Spring | 0 | 18.28 | -11.3 | 23.54 | 86.6 | 0 | 0 | 120 | 120 | 11.3 | 47.22 | 69.72 | 72.78 | 0 | 0 | 0 | Normal
2025-10-29 01:00 | 302 | 10 | Spring | 1 | 18.28 | -9.6 | 6.6 | 53.5 | 0 | 0 | 4.17 | 4.17 | 9.6 | 45 | 53.39 | -40.83 | 0 | 0 | 0 | Battery-supported
2025-10-29 02:00 | 302 | 10 | Spring | 2 | 18.28 | -13.1 | 6.51 | 85.8 | 0 | 0 | 3.82 | 3.82 | 13.1 | 49.9 | 34.96 | -46.08 | 0 | 0 | 0 | Battery-supported
2025-10-29 03:00 | 302 | 10 | Spring | 3 | 18.28 | -9.5 | 4.14 | 65.7 | 7.9 | 0.47 | 0.04 | 0.51 | 9.5 | 45 | 17.16 | -44.49 | 0 | 0 | 0 | Battery-supported
2025-10-29 04:00 | 302 | 10 | Spring | 4 | 18.28 | -13.1 | 1.39 | 23.4 | 105.1 | 6.31 | 0 | 6.31 | 13.1 | 46.13 | 15 | -5.41 | 34.41 | 11.478 | 0 | Diesel-backup
2025-10-29 05:00 | 302 | 10 | Spring | 5 | 18.28 | -9.3 | 14.51 | 13.9 | 211.1 | 12.67 | 120 | 132.67 | 9.3 | 45 | 47.26 | 87.67 | 0 | 0 | 0 | Normal
2025-10-29 06:00 | 302 | 10 | Spring | 6 | 18.28 | -12.3 | 7.58 | 78.7 | 138.1 | 8.29 | 9.51 | 17.8 | 12.3 | 45 | 36.38 | -27.2 | 0 | 0 | 0 | Battery-supported
2025-10-29 07:00 | 302 | 10 | Spring | 7 | 18.28 | -9.4 | 4.05 | 56.9 | 245.5 | 14.73 | 0.02 | 14.75 | 9.4 | 45 | 24.28 | -30.25 | 0 | 0 | 0 | Battery-supported
2025-10-29 08:00 | 302 | 10 | Spring | 8 | 18.28 | -14.3 | 13.27 | 61.1 | 274.8 | 16.49 | 120 | 136.49 | 14.3 | 55.34 | 54.15 | 81.15 | 0 | 0 | 0 | Normal
2025-10-29 09:00 | 302 | 10 | Spring | 9 | 18.28 | -13.2 | 13.89 | 42.4 | 389.3 | 23.36 | 120 | 143.36 | 13.2 | 56.46 | 86.12 | 86.9 | 0 | 0 | 0 | Normal
2025-10-29 10:00 | 302 | 10 | Spring | 10 | 18.28 | -10.7 | 11.77 | 13.9 | 553.3 | 33.2 | 79.16 | 112.36 | 10.7 | 52.17 | 95 | 24.12 | 0 | 0 | 0 | Normal
2025-10-29 11:00 | 302 | 10 | Spring | 11 | 18.28 | -8.8 | 6.46 | 75.7 | 279.3 | 16.76 | 3.63 | 20.39 | 8.8 | 50.01 | 83.15 | -29.62 | 0 | 0 | 0 | Battery-supported
2025-10-29 12:00 | 302 | 10 | Spring | 12 | 18.28 | -7.4 | 9.69 | 28.6 | 515.2 | 30.91 | 33.2 | 64.11 | 7.4 | 60.66 | 84.42 | 3.45 | 0 | 0 | 0 | Normal
2025-10-29 13:00 | 302 | 10 | Spring | 13 | 18.28 | -10.6 | 4.51 | 49.6 | 405.9 | 24.35 | 0.14 | 24.49 | 10.6 | 56.49 | 71.62 | -32 | 0 | 0 | 0 | Battery-supported
2025-10-29 14:00 | 302 | 10 | Spring | 14 | 18.28 | -6.2 | 12.11 | 51.7 | 378.2 | 22.69 | 89.33 | 112.02 | 6.2 | 45 | 95 | 63.53 | 0 | 0 | 0 | Normal
2025-10-29 15:00 | 302 | 10 | Spring | 15 | 18.28 | -10.5 | 5.75 | 62.9 | 301.5 | 18.09 | 1.59 | 19.68 | 10.5 | 54.5 | 81.07 | -34.82 | 0 | 0 | 0 | Battery-supported
2025-10-29 16:00 | 302 | 10 | Spring | 16 | 18.28 | -7.1 | 15.46 | 54.1 | 301.1 | 18.07 | 120 | 138.07 | 7.1 | 51.26 | 95 | 37.85 | 0 | 0 | 0 | Normal
2025-10-29 17:00 | 302 | 10 | Spring | 17 | 18.28 | -11.3 | 10.97 | 41.9 | 293.7 | 17.62 | 58.34 | 75.96 | 11.3 | 68.33 | 95 | 0 | 0 | 0 | 0 | Normal
2025-10-29 18:00 | 302 | 10 | Spring | 18 | 18.28 | -8.1 | 3.51 | 75.7 | 145.7 | 8.74 | 0 | 8.74 | 8.1 | 52.45 | 77.52 | -43.71 | 0 | 0 | 0 | Battery-supported
2025-10-29 19:00 | 302 | 10 | Spring | 19 | 18.28 | -14 | 14.53 | 16.7 | 206.2 | 12.37 | 120 | 132.37 | 14 | 65.43 | 95 | 47.51 | 0 | 0 | 0 | Normal
2025-10-29 20:00 | 302 | 10 | Spring | 20 | 18.28 | -11.3 | 13.88 | 75.9 | 54.9 | 3.29 | 120 | 123.29 | 11.3 | 52.69 | 95 | 0 | 0 | 0 | 0 | Normal
2025-10-29 21:00 | 302 | 10 | Spring | 21 | 18.28 | -7.8 | 12.85 | 48 | 10 | 0.6 | 114.41 | 115.01 | 7.8 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-10-29 22:00 | 302 | 10 | Spring | 22 | 18.28 | -11.9 | 13.25 | 38.7 | 0 | 0 | 120 | 120 | 11.9 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-10-29 23:00 | 302 | 10 | Spring | 23 | 18.28 | -8.3 | 8.21 | 31.1 | 0 | 0 | 14.62 | 14.62 | 8.3 | 46.83 | 82.12 | -32.21 | 0 | 0 | 0 | Battery-supported
2025-10-30 | 303 | 10 | Spring | 0 | 18.47 | -7.3 | 9.56 | 17.1 | 0 | 0 | 31.15 | 31.15 | 7.3 | 45 | 76.58 | -13.85 | 0 | 0 | 0 | Battery-supported
2025-10-30 01:00 | 303 | 10 | Spring | 1 | 18.47 | -10.8 | 7.27 | 16.8 | 0 | 0 | 7.5 | 7.5 | 10.8 | 45 | 61.58 | -37.5 | 0 | 0 | 0 | Battery-supported
2025-10-30 02:00 | 303 | 10 | Spring | 2 | 18.47 | -12.2 | 2.36 | 58.6 | 0 | 0 | 0 | 0 | 12.2 | 49.26 | 41.87 | -49.26 | 0 | 0 | 0 | Battery-supported
2025-10-30 03:00 | 303 | 10 | Spring | 3 | 18.47 | -11.5 | 10.83 | 38.2 | 18.6 | 1.12 | 55.12 | 56.24 | 11.5 | 45.19 | 45.94 | 11.05 | 0 | 0 | 0 | Normal
2025-10-30 04:00 | 303 | 10 | Spring | 4 | 18.47 | -13 | 2.92 | 66.1 | 68.9 | 4.13 | 0 | 4.13 | 13 | 48.61 | 28.15 | -44.48 | 0 | 0 | 0 | Battery-supported
2025-10-30 05:00 | 303 | 10 | Spring | 5 | 18.47 | -11.4 | 4.12 | 24.6 | 198.5 | 11.91 | 0.03 | 11.94 | 11.4 | 45 | 15 | -32.87 | 0.19 | 0.073 | 0 | Diesel-backup
2025-10-30 06:00 | 303 | 10 | Spring | 6 | 18.47 | -11.2 | 5.53 | 54.2 | 203.5 | 12.21 | 1.17 | 13.38 | 11.2 | 45 | 15 | 0 | 31.62 | 10.66 | 0 | Diesel-backup
2025-10-30 07:00 | 303 | 10 | Spring | 7 | 18.47 | -12.2 | 8.48 | 49.5 | 272.1 | 16.33 | 17.29 | 33.62 | 12.2 | 52.34 | 15 | 0 | 18.72 | 6.62 | 0 | Diesel-backup
2025-10-30 08:00 | 303 | 10 | Spring | 8 | 18.47 | -7.9 | 20.89 | 75.4 | 221.6 | 13.3 | 120 | 133.3 | 7.9 | 55.53 | 43.62 | 77.77 | 0 | 0 | 0 | Normal
2025-10-30 09:00 | 303 | 10 | Spring | 9 | 18.47 | -13.1 | 5.5 | 94.8 | 165.2 | 9.91 | 1.12 | 11.03 | 13.1 | 55.11 | 25.99 | -44.08 | 0 | 0 | 0 | Battery-supported
2025-10-30 10:00 | 303 | 10 | Spring | 10 | 18.47 | -8.3 | 21.85 | 62.7 | 327.8 | 19.67 | 120 | 139.67 | 8.3 | 51.72 | 58.35 | 87.95 | 0 | 0 | 0 | Normal
2025-10-30 11:00 | 303 | 10 | Spring | 11 | 18.47 | -13.4 | 13.61 | 69.8 | 308.1 | 18.49 | 120 | 138.49 | 13.4 | 52.64 | 89.95 | 85.85 | 0 | 0 | 0 | Normal
2025-10-30 12:00 | 303 | 10 | Spring | 12 | 18.47 | -10.7 | 10.06 | 32.7 | 495.2 | 29.71 | 39.51 | 69.22 | 10.7 | 52.65 | 95 | 13.73 | 0 | 0 | 0 | Normal
2025-10-30 13:00 | 303 | 10 | Spring | 13 | 18.47 | -7.9 | 5.12 | 37.7 | 463.9 | 27.83 | 0.6 | 28.43 | 7.9 | 60.59 | 82.14 | -32.16 | 0 | 0 | 0 | Battery-supported
2025-10-30 14:00 | 303 | 10 | Spring | 14 | 18.47 | -7.6 | 8.56 | 62.5 | 328.6 | 19.72 | 18.13 | 37.85 | 7.6 | 57.77 | 74.17 | -19.92 | 0 | 0 | 0 | Battery-supported
2025-10-30 15:00 | 303 | 10 | Spring | 15 | 18.47 | -10.6 | 8.97 | 84.4 | 209.9 | 12.59 | 22.91 | 35.5 | 10.6 | 54.73 | 66.48 | -19.23 | 0 | 0 | 0 | Battery-supported
2025-10-30 16:00 | 303 | 10 | Spring | 16 | 18.47 | -8.1 | 11.98 | 29.6 | 396.7 | 23.8 | 85.35 | 109.15 | 8.1 | 45 | 90.08 | 64.15 | 0 | 0 | 0 | Normal
2025-10-30 17:00 | 303 | 10 | Spring | 17 | 18.47 | -8.1 | 5.29 | 91.6 | 135.5 | 8.13 | 0.8 | 8.93 | 8.1 | 53.19 | 72.38 | -44.26 | 0 | 0 | 0 | Battery-supported
2025-10-30 18:00 | 303 | 10 | Spring | 18 | 18.47 | -10 | 13.84 | 15.5 | 303 | 18.18 | 120 | 138.18 | 10 | 51.94 | 95 | 61.47 | 0 | 0 | 0 | Normal
2025-10-30 19:00 | 303 | 10 | Spring | 19 | 18.47 | -7.3 | 7.98 | 69.9 | 115.9 | 6.95 | 12.58 | 19.53 | 7.3 | 48.65 | 83.35 | -29.12 | 0 | 0 | 0 | Battery-supported
2025-10-30 20:00 | 303 | 10 | Spring | 20 | 18.47 | -4.5 | 10.81 | 39.7 | 96 | 5.76 | 54.67 | 60.43 | 4.5 | 47.48 | 88.12 | 12.95 | 0 | 0 | 0 | Normal
2025-10-30 21:00 | 303 | 10 | Spring | 21 | 18.47 | -7.6 | 7.6 | 55.4 | 15.3 | 0.92 | 9.65 | 10.57 | 7.6 | 50.31 | 72.22 | -39.74 | 0 | 0 | 0 | Battery-supported
2025-10-30 22:00 | 303 | 10 | Spring | 22 | 18.47 | -7.5 | 16.49 | 16.2 | 0 | 0 | 120 | 120 | 7.5 | 45 | 95 | 61.9 | 0 | 0 | 0 | Normal
2025-10-30 23:00 | 303 | 10 | Spring | 23 | 18.47 | -7.5 | 4.29 | 72.2 | 0 | 0 | 0.07 | 0.07 | 7.5 | 46.49 | 76.43 | -46.42 | 0 | 0 | 0 | Battery-supported
2025-10-31 | 304 | 10 | Spring | 0 | 18.66 | -12.4 | 9.68 | 71.3 | 0 | 0 | 33.04 | 33.04 | 12.4 | 49.11 | 70 | -16.07 | 0 | 0 | 0 | Battery-supported
2025-10-31 01:00 | 304 | 10 | Spring | 1 | 18.66 | -8.5 | 3.43 | 39.1 | 0 | 0 | 0 | 0 | 8.5 | 45.09 | 51.97 | -45.09 | 0 | 0 | 0 | Battery-supported
2025-10-31 02:00 | 304 | 10 | Spring | 2 | 18.66 | -12.1 | 11.28 | 75.2 | 0 | 0 | 65.91 | 65.91 | 12.1 | 49.78 | 57.9 | 16.13 | 0 | 0 | 0 | Normal
2025-10-31 03:00 | 304 | 10 | Spring | 3 | 18.66 | -11.6 | 4.04 | 49.6 | 23 | 1.38 | 0.02 | 1.4 | 11.6 | 45 | 40.46 | -43.6 | 0 | 0 | 0 | Battery-supported
2025-10-31 04:00 | 304 | 10 | Spring | 4 | 18.66 | -5.9 | 6.99 | 63.5 | 76.3 | 4.58 | 5.95 | 10.53 | 5.9 | 45 | 26.68 | -34.47 | 0 | 0 | 0 | Battery-supported
2025-10-31 05:00 | 304 | 10 | Spring | 5 | 18.66 | -11.5 | 6.49 | 38.5 | 178.4 | 10.7 | 3.74 | 14.44 | 11.5 | 52.9 | 15 | -29.19 | 9.27 | 3.39 | 0 | Diesel-backup
2025-10-31 06:00 | 304 | 10 | Spring | 6 | 18.66 | -12.8 | 24.77 | 12.8 | 315.4 | 18.92 | 120 | 138.92 | 12.8 | 45 | 49.56 | 93.92 | 0 | 0 | 0 | Normal
2025-10-31 07:00 | 304 | 10 | Spring | 7 | 18.66 | -8.8 | 5.2 | 88.9 | 145.5 | 8.73 | 0.69 | 9.42 | 8.8 | 45 | 35.33 | -35.58 | 0 | 0 | 0 | Battery-supported
2025-10-31 08:00 | 304 | 10 | Spring | 8 | 18.66 | -13.5 | 13.85 | 54 | 305 | 18.3 | 120 | 138.3 | 13.5 | 63.77 | 62.76 | 74.53 | 0 | 0 | 0 | Normal
2025-10-31 09:00 | 304 | 10 | Spring | 9 | 18.66 | -12.3 | 1.33 | 63.9 | 298.8 | 17.93 | 0 | 17.93 | 12.3 | 56.7 | 47.25 | -38.77 | 0 | 0 | 0 | Battery-supported
2025-10-31 10:00 | 304 | 10 | Spring | 10 | 18.66 | -8.4 | 8.47 | 46.4 | 403.8 | 24.23 | 17.18 | 41.41 | 8.4 | 53.82 | 42.29 | -12.41 | 0 | 0 | 0 | Battery-supported
2025-10-31 11:00 | 304 | 10 | Spring | 11 | 18.66 | -10.9 | 16.84 | 44.3 | 431.9 | 25.91 | 120 | 145.91 | 10.9 | 56.32 | 75.25 | 89.59 | 0 | 0 | 0 | Normal
2025-10-31 12:00 | 304 | 10 | Spring | 12 | 18.66 | -14.1 | 2.46 | 45.6 | 431.4 | 25.88 | 0 | 25.88 | 14.1 | 61.78 | 60.89 | -35.9 | 0 | 0 | 0 | Battery-supported
2025-10-31 13:00 | 304 | 10 | Spring | 13 | 18.66 | -9.1 | 13.51 | 85.1 | 234 | 14.04 | 120 | 134.04 | 9.1 | 57.55 | 89.04 | 76.49 | 0 | 0 | 0 | Normal
2025-10-31 14:00 | 304 | 10 | Spring | 14 | 18.66 | -10.8 | 7.61 | 44.7 | 411.6 | 24.7 | 9.72 | 34.42 | 10.8 | 48.09 | 83.58 | -13.67 | 0 | 0 | 0 | Battery-supported
2025-10-31 15:00 | 304 | 10 | Spring | 15 | 18.66 | -6.1 | 1.7 | 54.3 | 340.2 | 20.41 | 0 | 20.41 | 6.1 | 54.37 | 69.99 | -33.96 | 0 | 0 | 0 | Battery-supported
2025-10-31 16:00 | 304 | 10 | Spring | 16 | 18.66 | -10.5 | 14.61 | 42.7 | 348.4 | 20.9 | 120 | 140.9 | 10.5 | 53.26 | 95 | 67.96 | 0 | 0 | 0 | Normal
2025-10-31 17:00 | 304 | 10 | Spring | 17 | 18.66 | -6.5 | 11.59 | 30.7 | 336.5 | 20.19 | 74.11 | 94.3 | 6.5 | 46.48 | 95 | 0 | 0 | 0 | 0 | Normal
2025-10-31 18:00 | 304 | 10 | Spring | 18 | 18.66 | -4.7 | 4.73 | 63.5 | 182.8 | 10.97 | 0.26 | 11.23 | 4.7 | 45 | 81.49 | -33.77 | 0 | 0 | 0 | Battery-supported
2025-10-31 19:00 | 304 | 10 | Spring | 19 | 18.66 | -10.3 | 11.99 | 88.8 | 83.8 | 5.03 | 85.65 | 90.68 | 10.3 | 54.34 | 94.87 | 36.34 | 0 | 0 | 0 | Normal
2025-10-31 20:00 | 304 | 10 | Spring | 20 | 18.66 | -8.8 | 2.61 | 50.9 | 90.1 | 5.41 | 0 | 5.41 | 8.8 | 49.57 | 77.2 | -44.16 | 0 | 0 | 0 | Battery-supported
2025-10-31 21:00 | 304 | 10 | Spring | 21 | 18.66 | -7.6 | 5.73 | 42.6 | 24.9 | 1.49 | 1.55 | 3.04 | 7.6 | 45 | 60.42 | -41.96 | 0 | 0 | 0 | Battery-supported
2025-10-31 22:00 | 304 | 10 | Spring | 22 | 18.66 | -10.5 | 8.34 | 33.9 | 0 | 0 | 15.87 | 15.87 | 10.5 | 45.49 | 48.57 | -29.62 | 0 | 0 | 0 | Battery-supported
2025-10-31 23:00 | 304 | 10 | Spring | 23 | 18.66 | -8.2 | 8.08 | 71.3 | 0 | 0 | 13.45 | 13.45 | 8.2 | 45 | 35.95 | -31.55 | 0 | 0 | 0 | Battery-supported
2025-11-01 | 305 | 11 | Spring | 0 | 18.86 | -9.4 | 10.54 | 62.7 | 0 | 0 | 48.83 | 48.83 | 9.4 | 47.59 | 36.41 | 1.24 | 0 | 0 | 0 | Normal
2025-11-01 01:00 | 305 | 11 | Spring | 1 | 18.86 | -9.8 | 24.33 | 4.2 | 0 | 0 | 120 | 120 | 9.8 | 49.51 | 62.35 | 70.49 | 0 | 0 | 0 | Normal
2025-11-01 02:00 | 305 | 11 | Spring | 2 | 18.86 | -9.6 | 3.99 | 56.3 | 0 | 0 | 0.02 | 0.02 | 9.6 | 49.23 | 42.66 | -49.21 | 0 | 0 | 0 | Battery-supported
2025-11-01 03:00 | 305 | 11 | Spring | 3 | 18.86 | -9.9 | 9.27 | 63.8 | 24.6 | 1.48 | 26.89 | 28.37 | 9.9 | 50.98 | 33.62 | -22.61 | 0 | 0 | 0 | Battery-supported
2025-11-01 04:00 | 305 | 11 | Spring | 4 | 18.86 | -10.1 | 9.42 | 39.6 | 108.9 | 6.53 | 29.04 | 35.57 | 10.1 | 45 | 29.85 | -9.43 | 0 | 0 | 0 | Battery-supported
2025-11-01 05:00 | 305 | 11 | Spring | 5 | 18.86 | -12.1 | 15.32 | 85.5 | 92.7 | 5.56 | 120 | 125.56 | 12.1 | 45 | 59.49 | 80.56 | 0 | 0 | 0 | Normal
2025-11-01 06:00 | 305 | 11 | Spring | 6 | 18.86 | -12.2 | 8.02 | 4.7 | 342.3 | 20.54 | 12.92 | 33.46 | 12.2 | 46.86 | 54.13 | -13.4 | 0 | 0 | 0 | Battery-supported
2025-11-01 07:00 | 305 | 11 | Spring | 7 | 18.86 | -11.4 | 2.15 | 67.9 | 216.6 | 13 | 0 | 13 | 11.4 | 45 | 41.33 | -32 | 0 | 0 | 0 | Battery-supported
2025-11-01 08:00 | 305 | 11 | Spring | 8 | 18.86 | -11.3 | 8.73 | 85.4 | 185.2 | 11.11 | 20.02 | 31.13 | 11.3 | 49.05 | 34.16 | -17.92 | 0 | 0 | 0 | Battery-supported
2025-11-01 09:00 | 305 | 11 | Spring | 9 | 18.86 | -12.1 | 1.94 | 37.5 | 413.8 | 24.83 | 0 | 24.83 | 12.1 | 54.07 | 22.47 | -29.24 | 0 | 0 | 0 | Battery-supported
2025-11-01 10:00 | 305 | 11 | Spring | 10 | 18.86 | -10.3 | 14.51 | 54 | 368.9 | 22.13 | 120 | 142.13 | 10.3 | 56.05 | 54.15 | 86.08 | 0 | 0 | 0 | Normal
2025-11-01 11:00 | 305 | 11 | Spring | 11 | 18.86 | -14.7 | 8.25 | 38.9 | 457.9 | 27.47 | 15 | 42.47 | 14.7 | 62.54 | 46.12 | -20.07 | 0 | 0 | 0 | Battery-supported
2025-11-01 12:00 | 305 | 11 | Spring | 12 | 18.86 | -12 | 10.29 | 24.6 | 534.7 | 32.08 | 43.81 | 75.89 | 12 | 54.62 | 53.94 | 21.27 | 0 | 0 | 0 | Normal
2025-11-01 13:00 | 305 | 11 | Spring | 13 | 18.86 | -10.7 | 4.31 | 28.3 | 509.4 | 30.56 | 0.07 | 30.63 | 10.7 | 58.02 | 42.99 | -27.39 | 0 | 0 | 0 | Battery-supported
2025-11-01 14:00 | 305 | 11 | Spring | 14 | 18.86 | -11.6 | 4.45 | 53.1 | 372.8 | 22.37 | 0.12 | 22.49 | 11.6 | 54.63 | 30.13 | -32.14 | 0 | 0 | 0 | Battery-supported
2025-11-01 15:00 | 305 | 11 | Spring | 15 | 18.86 | -5.7 | 11.46 | 45.5 | 379.1 | 22.75 | 70.59 | 93.34 | 5.7 | 45 | 47.92 | 48.34 | 0 | 0 | 0 | Normal
2025-11-01 16:00 | 305 | 11 | Spring | 16 | 18.86 | -8.9 | 6.95 | 50.3 | 321.3 | 19.28 | 5.75 | 25.03 | 8.9 | 46.46 | 39.35 | -21.43 | 0 | 0 | 0 | Battery-supported
2025-11-01 17:00 | 305 | 11 | Spring | 17 | 18.86 | -8.2 | 5.2 | 69.9 | 210.1 | 12.61 | 0.69 | 13.3 | 8.2 | 52.83 | 23.54 | -39.53 | 0 | 0 | 0 | Battery-supported
2025-11-01 18:00 | 305 | 11 | Spring | 18 | 18.86 | -9.5 | 16.77 | 36.4 | 258 | 15.48 | 120 | 135.48 | 9.5 | 45.26 | 56.74 | 90.22 | 0 | 0 | 0 | Normal
2025-11-01 19:00 | 305 | 11 | Spring | 19 | 18.86 | -8.3 | 8.87 | 28.8 | 202.5 | 12.15 | 21.67 | 33.82 | 8.3 | 45.96 | 51.88 | -12.14 | 0 | 0 | 0 | Battery-supported
2025-11-01 20:00 | 305 | 11 | Spring | 20 | 18.86 | -10.9 | 5.67 | 53.8 | 92.4 | 5.54 | 1.43 | 6.97 | 10.9 | 47.8 | 35.55 | -40.83 | 0 | 0 | 0 | Battery-supported
2025-11-01 21:00 | 305 | 11 | Spring | 21 | 18.86 | -8.6 | 9.19 | 33.6 | 35.2 | 2.11 | 25.78 | 27.89 | 8.6 | 45 | 28.71 | -17.11 | 0 | 0 | 0 | Battery-supported
2025-11-01 22:00 | 305 | 11 | Spring | 22 | 18.86 | -10.4 | 6.32 | 57.3 | 0 | 0 | 3.14 | 3.14 | 10.4 | 46.35 | 15 | -34.27 | 8.94 | 3.275 | 0 | Diesel-backup
2025-11-01 23:00 | 305 | 11 | Spring | 23 | 18.86 | -9.2 | 10.91 | 18.9 | 0 | 0 | 56.95 | 56.95 | 9.2 | 45 | 19.4 | 11.95 | 0 | 0 | 0 | Normal
2025-11-02 | 306 | 11 | Spring | 0 | 19.07 | -14.4 | 4.12 | 69.8 | 0 | 0 | 0.03 | 0.03 | 14.4 | 52.42 | 15 | -10.99 | 41.4 | 13.438 | 0 | Diesel-backup
2025-11-02 01:00 | 306 | 11 | Spring | 1 | 19.07 | -11.6 | 14.59 | 58 | 0 | 0 | 120 | 120 | 11.6 | 46.64 | 42 | 73.36 | 0 | 0 | 0 | Normal
2025-11-02 02:00 | 306 | 11 | Spring | 2 | 19.07 | -6.3 | 6.29 | 46.8 | 0 | 0 | 3.04 | 3.04 | 6.3 | 45 | 25.21 | -41.96 | 0 | 0 | 0 | Battery-supported
2025-11-02 03:00 | 306 | 11 | Spring | 3 | 19.07 | -8.1 | 3.32 | 88.1 | 19.5 | 1.17 | 0 | 1.17 | 8.1 | 45 | 15 | -25.53 | 18.3 | 6.481 | 0 | Diesel-backup
2025-11-02 04:00 | 306 | 11 | Spring | 4 | 19.07 | -7.3 | 3.61 | 54.8 | 96.6 | 5.8 | 0 | 5.8 | 7.3 | 45 | 15 | 0 | 39.2 | 12.835 | 0 | Diesel-backup
2025-11-02 05:00 | 306 | 11 | Spring | 5 | 19.07 | -7.5 | 7.23 | 73.5 | 119.3 | 7.16 | 7.26 | 14.42 | 7.5 | 45 | 15 | 0 | 30.58 | 10.35 | 0 | Diesel-backup
2025-11-02 06:00 | 306 | 11 | Spring | 6 | 19.07 | -9.3 | 5.21 | 65.9 | 182.5 | 10.95 | 0.7 | 11.65 | 9.3 | 45 | 15 | 0 | 33.35 | 11.169 | 0 | Diesel-backup
2025-11-02 07:00 | 306 | 11 | Spring | 7 | 19.07 | -11.9 | 2.88 | 55.3 | 260.9 | 15.65 | 0 | 15.65 | 11.9 | 46.82 | 15 | 0 | 31.17 | 10.526 | 0 | Diesel-backup
2025-11-02 08:00 | 306 | 11 | Spring | 8 | 19.07 | -13.3 | 3 | 47.7 | 333.2 | 19.99 | 0 | 19.99 | 13.3 | 55.29 | 15 | 0 | 35.3 | 11.734 | 0 | Diesel-backup
2025-11-02 09:00 | 306 | 11 | Spring | 9 | 19.07 | -8.4 | 8.27 | 8.9 | 539 | 32.34 | 15.19 | 47.53 | 8.4 | 50.35 | 15 | 0 | 2.82 | 1.055 | 0 | Diesel-backup
2025-11-02 10:00 | 306 | 11 | Spring | 10 | 19.07 | -10.6 | 9.46 | 50 | 388.1 | 23.29 | 29.63 | 52.92 | 10.6 | 53.09 | 15 | 0 | 0.17 | 0.064 | 0 | Diesel-backup
2025-11-02 11:00 | 306 | 11 | Spring | 11 | 19.07 | -5.1 | 8.61 | 83.3 | 242.9 | 14.57 | 18.68 | 33.25 | 5.1 | 49.04 | 15 | 0 | 15.79 | 5.643 | 0 | Diesel-backup
2025-11-02 12:00 | 306 | 11 | Spring | 12 | 19.07 | -11 | 16.44 | 62.5 | 348.3 | 20.9 | 120 | 140.9 | 11 | 53.19 | 47.28 | 87.71 | 0 | 0 | 0 | Normal
2025-11-02 13:00 | 306 | 11 | Spring | 13 | 19.07 | -5.5 | 10.25 | 21.9 | 541 | 32.46 | 43.04 | 75.5 | 5.5 | 45 | 58.5 | 30.5 | 0 | 0 | 0 | Normal
2025-11-02 14:00 | 306 | 11 | Spring | 14 | 19.07 | -9.8 | 5.61 | 79.1 | 252.4 | 15.14 | 1.31 | 16.45 | 9.8 | 52.6 | 44.04 | -36.15 | 0 | 0 | 0 | Battery-supported
2025-11-02 15:00 | 306 | 11 | Spring | 15 | 19.07 | -6.2 | 32.98 | 41.6 | 397.2 | 23.83 | 0 | 23.83 | 6.2 | 45.32 | 35.45 | -21.49 | 0 | 0 | 0 | Battery-supported
2025-11-02 16:00 | 306 | 11 | Spring | 16 | 19.07 | -5 | 4.57 | 60.7 | 282.7 | 16.96 | 0.17 | 17.13 | 5 | 52.48 | 21.31 | -35.35 | 0 | 0 | 0 | Battery-supported
2025-11-02 17:00 | 306 | 11 | Spring | 17 | 19.07 | -10.7 | 2.64 | 39.3 | 314.3 | 18.86 | 0 | 18.86 | 10.7 | 55.4 | 15 | -15.76 | 20.78 | 7.293 | 0 | Diesel-backup
2025-11-02 18:00 | 306 | 11 | Spring | 18 | 19.07 | -9.3 | 11.77 | 91.5 | 113.1 | 6.79 | 79.16 | 85.95 | 9.3 | 56.24 | 25.93 | 29.71 | 0 | 0 | 0 | Normal
2025-11-02 19:00 | 306 | 11 | Spring | 19 | 19.07 | -10.3 | 20.73 | 42.6 | 181 | 10.86 | 120 | 130.86 | 10.3 | 51.1 | 55.28 | 79.76 | 0 | 0 | 0 | Normal
2025-11-02 20:00 | 306 | 11 | Spring | 20 | 19.07 | -10.7 | 13.17 | 67.5 | 81 | 4.86 | 120 | 124.86 | 10.7 | 57.26 | 80.16 | 67.6 | 0 | 0 | 0 | Normal
2025-11-02 21:00 | 306 | 11 | Spring | 21 | 19.07 | -6.6 | 6.98 | 65.3 | 29.4 | 1.76 | 5.9 | 7.66 | 6.6 | 45 | 65.23 | -37.34 | 0 | 0 | 0 | Battery-supported
2025-11-02 22:00 | 306 | 11 | Spring | 22 | 19.07 | -8.6 | 4.9 | 28.8 | 0 | 0 | 0.38 | 0.38 | 8.6 | 45 | 47.38 | -44.62 | 0 | 0 | 0 | Battery-supported
2025-11-02 23:00 | 306 | 11 | Spring | 23 | 19.07 | -8.3 | 11.3 | 19.2 | 0 | 0 | 66.42 | 66.42 | 8.3 | 45 | 55.26 | 21.42 | 0 | 0 | 0 | Normal
2025-11-03 | 307 | 11 | Spring | 0 | 19.28 | -7.3 | 7.19 | 24.6 | 0 | 0 | 7.03 | 7.03 | 7.3 | 45 | 40.07 | -37.97 | 0 | 0 | 0 | Battery-supported
2025-11-03 01:00 | 307 | 11 | Spring | 1 | 19.28 | -13 | 6.71 | 83.7 | 0 | 0 | 4.63 | 4.63 | 13 | 54.88 | 19.97 | -50.25 | 0 | 0 | 0 | Battery-supported
2025-11-03 02:00 | 307 | 11 | Spring | 2 | 19.28 | -6.5 | 17.12 | 71.9 | 0 | 0 | 120 | 120 | 6.5 | 45 | 47.57 | 75 | 0 | 0 | 0 | Normal
2025-11-03 03:00 | 307 | 11 | Spring | 3 | 19.28 | -10.4 | 2.19 | 23.3 | 56.2 | 3.37 | 0 | 3.37 | 10.4 | 45 | 30.92 | -41.63 | 0 | 0 | 0 | Battery-supported
2025-11-03 04:00 | 307 | 11 | Spring | 4 | 19.28 | -8.9 | 9.92 | 66.7 | 86.5 | 5.19 | 37.04 | 42.23 | 8.9 | 45 | 29.81 | -2.77 | 0 | 0 | 0 | Battery-supported
2025-11-03 05:00 | 307 | 11 | Spring | 5 | 19.28 | -9 | 5.11 | 67.7 | 134.6 | 8.08 | 0.58 | 8.66 | 9 | 56.23 | 15 | -37.03 | 10.54 | 3.837 | 0 | Diesel-backup
2025-11-03 06:00 | 307 | 11 | Spring | 6 | 19.28 | -7.6 | 8.03 | 39.4 | 258.3 | 15.5 | 13.01 | 28.51 | 7.6 | 45.87 | 15 | 0 | 17.36 | 6.169 | 0 | Diesel-backup
2025-11-03 07:00 | 307 | 11 | Spring | 7 | 19.28 | -11 | 4.46 | 23.1 | 371.9 | 22.31 | 0.12 | 22.43 | 11 | 45 | 15 | 0 | 22.57 | 7.87 | 0 | Diesel-backup
2025-11-03 08:00 | 307 | 11 | Spring | 8 | 19.28 | -15.5 | 7.19 | 76.8 | 221.2 | 13.27 | 7.03 | 20.3 | 15.5 | 62.18 | 15 | 0 | 41.88 | 13.569 | 0 | Diesel-backup
2025-11-03 09:00 | 307 | 11 | Spring | 9 | 19.28 | -10.6 | 26.73 | 54 | 344.6 | 20.68 | 120 | 140.68 | 10.6 | 54.09 | 46.87 | 86.59 | 0 | 0 | 0 | Normal
2025-11-03 10:00 | 307 | 11 | Spring | 10 | 19.28 | -10.1 | 12.42 | 30.9 | 477.3 | 28.64 | 99.34 | 127.98 | 10.1 | 63.6 | 70.56 | 64.38 | 0 | 0 | 0 | Normal
2025-11-03 11:00 | 307 | 11 | Spring | 11 | 19.28 | -12.6 | 11.25 | 10 | 598.6 | 35.92 | 65.15 | 101.07 | 12.6 | 55.88 | 87.19 | 45.19 | 0 | 0 | 0 | Normal
2025-11-03 12:00 | 307 | 11 | Spring | 12 | 19.28 | -9.7 | 8.16 | 54.8 | 386.4 | 23.18 | 14.16 | 37.34 | 9.7 | 51.68 | 81.45 | -14.34 | 0 | 0 | 0 | Battery-supported
2025-11-03 13:00 | 307 | 11 | Spring | 13 | 19.28 | -10.5 | 7.73 | 57.8 | 366.5 | 21.99 | 10.59 | 32.58 | 10.5 | 53.21 | 73.2 | -20.63 | 0 | 0 | 0 | Battery-supported
2025-11-03 14:00 | 307 | 11 | Spring | 14 | 19.28 | -12.2 | 8.49 | 54.4 | 367.9 | 22.07 | 17.39 | 39.46 | 12.2 | 53.65 | 67.52 | -14.19 | 0 | 0 | 0 | Battery-supported
2025-11-03 15:00 | 307 | 11 | Spring | 15 | 19.28 | -7.4 | 10.59 | 55.7 | 337 | 20.22 | 49.88 | 70.1 | 7.4 | 47.54 | 75.82 | 22.56 | 0 | 0 | 0 | Normal
2025-11-03 16:00 | 307 | 11 | Spring | 16 | 19.28 | -9.8 | 12.55 | 55.3 | 305.1 | 18.31 | 103.74 | 122.05 | 9.8 | 48.3 | 95 | 52.11 | 0 | 0 | 0 | Normal
2025-11-03 17:00 | 307 | 11 | Spring | 17 | 19.28 | -9.1 | 22.05 | 70.8 | 211.2 | 12.67 | 120 | 132.67 | 9.1 | 50.18 | 95 | 0 | 0 | 0 | 0 | Normal
2025-11-03 18:00 | 307 | 11 | Spring | 18 | 19.28 | -9 | 6.93 | 60.9 | 199.2 | 11.95 | 5.65 | 17.6 | 9 | 55.08 | 80.01 | -37.48 | 0 | 0 | 0 | Battery-supported
2025-11-03 19:00 | 307 | 11 | Spring | 19 | 19.28 | -5.1 | 16.88 | 57.9 | 154.7 | 9.28 | 120 | 129.28 | 5.1 | 47.07 | 95 | 40.74 | 0 | 0 | 0 | Normal
2025-11-03 20:00 | 307 | 11 | Spring | 20 | 19.28 | -7.9 | 22.19 | 6.1 | 165 | 9.9 | 120 | 129.9 | 7.9 | 48.59 | 95 | 0 | 0 | 0 | 0 | Normal
2025-11-03 21:00 | 307 | 11 | Spring | 21 | 19.28 | -7.7 | 13.1 | 69.7 | 32.5 | 1.95 | 120 | 121.95 | 7.7 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-11-03 22:00 | 307 | 11 | Spring | 22 | 19.28 | -9 | 7.65 | 38.9 | 0 | 0 | 10 | 10 | 9 | 46.82 | 80.27 | -36.82 | 0 | 0 | 0 | Battery-supported
2025-11-03 23:00 | 307 | 11 | Spring | 23 | 19.28 | -7.2 | 13.15 | 67.9 | 0 | 0 | 120 | 120 | 7.2 | 48.64 | 95 | 40.02 | 0 | 0 | 0 | Normal
2025-11-04 | 308 | 11 | Spring | 0 | 19.49 | -5.4 | 2.76 | 34.7 | 0 | 0 | 0 | 0 | 5.4 | 45 | 77 | -45 | 0 | 0 | 0 | Battery-supported
2025-11-04 01:00 | 308 | 11 | Spring | 1 | 19.49 | -7.3 | 20.02 | 69.5 | 0 | 0 | 120 | 120 | 7.3 | 45 | 95 | 48.91 | 0 | 0 | 0 | Normal
2025-11-04 02:00 | 308 | 11 | Spring | 2 | 19.49 | -7.6 | 13.75 | 88.3 | 0 | 0 | 120 | 120 | 7.6 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-11-04 03:00 | 308 | 11 | Spring | 3 | 19.49 | -8.2 | 7.43 | 17.9 | 68 | 4.08 | 8.5 | 12.58 | 8.2 | 46.47 | 81.44 | -33.89 | 0 | 0 | 0 | Battery-supported
2025-11-04 04:00 | 308 | 11 | Spring | 4 | 19.49 | -12.9 | 7.1 | 34 | 135.7 | 8.14 | 6.53 | 14.67 | 12.9 | 52.07 | 66.48 | -37.4 | 0 | 0 | 0 | Battery-supported
2025-11-04 05:00 | 308 | 11 | Spring | 5 | 19.49 | -12.1 | 3.24 | 87.2 | 97.2 | 5.83 | 0 | 5.83 | 12.1 | 47.71 | 49.73 | -41.88 | 0 | 0 | 0 | Battery-supported
2025-11-04 06:00 | 308 | 11 | Spring | 6 | 19.49 | -10.8 | 14.95 | 55 | 218.8 | 13.13 | 120 | 133.13 | 10.8 | 45 | 82.16 | 88.13 | 0 | 0 | 0 | Normal
2025-11-04 07:00 | 308 | 11 | Spring | 7 | 19.49 | -12.1 | 7.2 | 62.8 | 240.2 | 14.41 | 7.09 | 21.5 | 12.1 | 48.66 | 71.3 | -27.16 | 0 | 0 | 0 | Battery-supported
2025-11-04 08:00 | 308 | 11 | Spring | 8 | 19.49 | -12.9 | 21 | 12 | 476.9 | 28.61 | 120 | 148.61 | 12.9 | 56.84 | 95 | 64.4 | 0 | 0 | 0 | Normal
2025-11-04 09:00 | 308 | 11 | Spring | 9 | 19.49 | -14.7 | 2.73 | 27.3 | 461.8 | 27.71 | 0 | 27.71 | 14.7 | 59.03 | 82.47 | -31.32 | 0 | 0 | 0 | Battery-supported
2025-11-04 10:00 | 308 | 11 | Spring | 10 | 19.49 | -13.4 | 4.5 | 31.5 | 475.4 | 28.52 | 0.14 | 28.66 | 13.4 | 52.22 | 73.05 | -23.56 | 0 | 0 | 0 | Battery-supported
2025-11-04 11:00 | 308 | 11 | Spring | 11 | 19.49 | -10.7 | 4.16 | 60.6 | 353.2 | 21.19 | 0.04 | 21.23 | 10.7 | 49.25 | 61.84 | -28.02 | 0 | 0 | 0 | Battery-supported
2025-11-04 12:00 | 308 | 11 | Spring | 12 | 19.49 | -10 | 1.23 | 75.6 | 283.8 | 17.03 | 0 | 17.03 | 10 | 46.51 | 50.05 | -29.48 | 0 | 0 | 0 | Battery-supported
2025-11-04 13:00 | 308 | 11 | Spring | 13 | 19.49 | -11.2 | 11.71 | 80.5 | 256.6 | 15.4 | 77.45 | 92.85 | 11.2 | 58.81 | 62.57 | 34.04 | 0 | 0 | 0 | Normal
2025-11-04 14:00 | 308 | 11 | Spring | 14 | 19.49 | -8.9 | 3.71 | 35.7 | 455.6 | 27.34 | 0 | 27.34 | 8.9 | 56.64 | 50.85 | -29.3 | 0 | 0 | 0 | Battery-supported
2025-11-04 15:00 | 308 | 11 | Spring | 15 | 19.49 | -9.7 | 4.51 | 32.8 | 437.8 | 26.27 | 0.14 | 26.41 | 9.7 | 46.23 | 42.93 | -19.82 | 0 | 0 | 0 | Battery-supported
2025-11-04 16:00 | 308 | 11 | Spring | 16 | 19.49 | -5.9 | 3.87 | 74.7 | 230.7 | 13.84 | 0.01 | 13.85 | 5.9 | 45.71 | 30.18 | -31.86 | 0 | 0 | 0 | Battery-supported
2025-11-04 17:00 | 308 | 11 | Spring | 17 | 19.49 | -8.4 | 6.31 | 56.5 | 261.6 | 15.7 | 3.11 | 18.81 | 8.4 | 48.23 | 18.41 | -29.42 | 0 | 0 | 0 | Battery-supported
2025-11-04 18:00 | 308 | 11 | Spring | 18 | 19.49 | -6.3 | 18.66 | 61.3 | 201.3 | 12.08 | 120 | 132.08 | 6.3 | 52.94 | 47.54 | 79.14 | 0 | 0 | 0 | Normal
2025-11-04 19:00 | 308 | 11 | Spring | 19 | 19.49 | -7.2 | 10.55 | 72.6 | 128 | 7.68 | 49.04 | 56.72 | 7.2 | 50.55 | 49.81 | 6.17 | 0 | 0 | 0 | Normal
2025-11-04 20:00 | 308 | 11 | Spring | 20 | 19.49 | -10.7 | 8.99 | 63.7 | 95.1 | 5.71 | 23.16 | 28.87 | 10.7 | 59.87 | 37.41 | -31 | 0 | 0 | 0 | Battery-supported
2025-11-04 21:00 | 308 | 11 | Spring | 21 | 19.49 | -7.8 | 8.01 | 63.6 | 41.1 | 2.47 | 12.84 | 15.31 | 7.8 | 45 | 25.53 | -29.69 | 0 | 0 | 0 | Battery-supported
2025-11-04 22:00 | 308 | 11 | Spring | 22 | 19.49 | -10.5 | 5.69 | 19.5 | 0 | 0 | 1.47 | 1.47 | 10.5 | 45 | 15 | -26.33 | 17.2 | 6.115 | 0 | Diesel-backup
2025-11-04 23:00 | 308 | 11 | Spring | 23 | 19.49 | -8.3 | 5.75 | 43.6 | 0 | 0 | 1.59 | 1.59 | 8.3 | 45 | 15 | 0 | 43.41 | 13.98 | 0 | Diesel-backup
2025-11-05 | 309 | 11 | Spring | 0 | 19.71 | -9.8 | 8.7 | 64.5 | 0 | 0 | 19.68 | 19.68 | 9.8 | 45 | 15 | 0 | 25.32 | 8.74 | 0 | Diesel-backup
2025-11-05 01:00 | 309 | 11 | Spring | 1 | 19.71 | -7.7 | 17.45 | 19.1 | 0 | 0 | 120 | 120 | 7.7 | 46.91 | 41.9 | 73.09 | 0 | 0 | 0 | Normal
2025-11-05 02:00 | 309 | 11 | Spring | 2 | 19.71 | -11.9 | 5.42 | 76.1 | 0 | 0 | 0.99 | 0.99 | 11.9 | 54.59 | 20.46 | -53.6 | 0 | 0 | 0 | Battery-supported
2025-11-05 03:00 | 309 | 11 | Spring | 3 | 19.71 | -9.3 | 13.95 | 57.5 | 50.7 | 3.04 | 120 | 123.04 | 9.3 | 46.26 | 48.71 | 76.78 | 0 | 0 | 0 | Normal
2025-11-05 04:00 | 309 | 11 | Spring | 4 | 19.71 | -8.4 | 3.97 | 56.9 | 109.6 | 6.58 | 0.01 | 6.59 | 8.4 | 45 | 33.35 | -38.41 | 0 | 0 | 0 | Battery-supported
2025-11-05 05:00 | 309 | 11 | Spring | 5 | 19.71 | -8 | 11.61 | 65.9 | 145.9 | 8.75 | 74.66 | 83.41 | 8 | 45 | 47.48 | 38.41 | 0 | 0 | 0 | Normal
2025-11-05 06:00 | 309 | 11 | Spring | 6 | 19.71 | -11.9 | 17.06 | 92 | 117.3 | 7.04 | 120 | 127.04 | 11.9 | 45 | 77.67 | 82.04 | 0 | 0 | 0 | Normal
2025-11-05 07:00 | 309 | 11 | Spring | 7 | 19.71 | -10.3 | 7.61 | 21.9 | 383.2 | 22.99 | 9.72 | 32.71 | 10.3 | 45 | 72.76 | -12.29 | 0 | 0 | 0 | Battery-supported
2025-11-05 08:00 | 309 | 11 | Spring | 8 | 19.71 | -10 | 5.7 | 61.5 | 283.9 | 17.03 | 1.49 | 18.52 | 10 | 46.31 | 61.64 | -27.79 | 0 | 0 | 0 | Battery-supported
2025-11-05 09:00 | 309 | 11 | Spring | 9 | 19.71 | -6.9 | 11.59 | 71.7 | 269.1 | 16.15 | 74.11 | 90.26 | 6.9 | 51.82 | 75.79 | 38.44 | 0 | 0 | 0 | Normal
2025-11-05 10:00 | 309 | 11 | Spring | 10 | 19.71 | -13.5 | 19.74 | 30.4 | 480.8 | 28.85 | 120 | 148.85 | 13.5 | 55.83 | 95 | 52.21 | 0 | 0 | 0 | Normal
2025-11-05 11:00 | 309 | 11 | Spring | 11 | 19.71 | -12 | 13.6 | 41.2 | 447.3 | 26.84 | 120 | 146.84 | 12 | 58.28 | 95 | 0 | 0 | 0 | 0 | Normal
2025-11-05 12:00 | 309 | 11 | Spring | 12 | 19.71 | -3.5 | 21.26 | 67.1 | 325.6 | 19.54 | 120 | 139.54 | 3.5 | 49.47 | 95 | 0 | 0 | 0 | 0 | Normal
2025-11-05 13:00 | 309 | 11 | Spring | 13 | 19.71 | -9.9 | 8.06 | 75.2 | 282.2 | 16.93 | 13.27 | 30.2 | 9.9 | 50.68 | 86.81 | -20.48 | 0 | 0 | 0 | Battery-supported
2025-11-05 14:00 | 309 | 11 | Spring | 14 | 19.71 | -13.1 | 7.76 | 35.3 | 457.9 | 27.47 | 10.82 | 38.29 | 13.1 | 60.16 | 78.06 | -21.87 | 0 | 0 | 0 | Battery-supported
2025-11-05 15:00 | 309 | 11 | Spring | 15 | 19.71 | -9.8 | 2.94 | 23.8 | 478.2 | 28.69 | 0 | 28.69 | 9.8 | 48.06 | 70.31 | -19.37 | 0 | 0 | 0 | Battery-supported
2025-11-05 16:00 | 309 | 11 | Spring | 16 | 19.71 | -14.2 | 5.55 | 84.4 | 193.3 | 11.6 | 1.21 | 12.81 | 14.2 | 67.74 | 48.34 | -54.93 | 0 | 0 | 0 | Battery-supported
2025-11-05 17:00 | 309 | 11 | Spring | 17 | 19.71 | -7.3 | 7.42 | 33.9 | 341.8 | 20.51 | 8.43 | 28.94 | 7.3 | 45 | 41.92 | -16.06 | 0 | 0 | 0 | Battery-supported
2025-11-05 18:00 | 309 | 11 | Spring | 18 | 19.71 | -5.8 | 7.87 | 61.3 | 204.3 | 12.26 | 11.68 | 23.94 | 5.8 | 51.78 | 30.78 | -27.84 | 0 | 0 | 0 | Battery-supported
2025-11-05 19:00 | 309 | 11 | Spring | 19 | 19.71 | -9.5 | 11.47 | 41.6 | 198.3 | 11.9 | 70.86 | 82.76 | 9.5 | 57.47 | 40.09 | 25.29 | 0 | 0 | 0 | Normal
2025-11-05 20:00 | 309 | 11 | Spring | 20 | 19.71 | -8.4 | 5.91 | 63.8 | 99.6 | 5.98 | 1.96 | 7.94 | 8.4 | 52.12 | 22.41 | -44.18 | 0 | 0 | 0 | Battery-supported
2025-11-05 21:00 | 309 | 11 | Spring | 21 | 19.71 | -5.4 | 6.14 | 37.1 | 64.3 | 3.86 | 2.58 | 6.44 | 5.4 | 45 | 15 | -18.54 | 20.02 | 7.048 | 0 | Diesel-backup
2025-11-05 22:00 | 309 | 11 | Spring | 22 | 19.71 | -11.5 | 23.3 | 35.7 | 0 | 0 | 120 | 120 | 11.5 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-11-05 23:00 | 309 | 11 | Spring | 23 | 19.71 | -10.7 | 1.26 | 7.5 | 0 | 0 | 0 | 0 | 10.7 | 45 | 24.6 | -45 | 0 | 0 | 0 | Battery-supported
2025-11-06 | 310 | 11 | Spring | 0 | 19.94 | -8.5 | 1.6 | 30.7 | 0 | 0 | 0 | 0 | 8.5 | 45 | 15 | -24 | 21 | 7.365 | 0 | Diesel-backup
2025-11-06 01:00 | 310 | 11 | Spring | 1 | 19.94 | -10 | 4.38 | 45.7 | 0 | 0 | 0.1 | 0.1 | 10 | 48.17 | 15 | 0 | 48.07 | 15.382 | 0 | Diesel-backup
2025-11-06 02:00 | 310 | 11 | Spring | 2 | 19.94 | -9.4 | 1.54 | 34.4 | 0 | 0 | 0 | 0 | 9.4 | 46.33 | 15 | 0 | 46.33 | 14.826 | 0 | Diesel-backup
2025-11-06 03:00 | 310 | 11 | Spring | 3 | 19.94 | -11.9 | 1.84 | 52.9 | 60.2 | 3.61 | 0 | 3.61 | 11.9 | 47.12 | 15 | 0 | 43.51 | 14.006 | 0 | Diesel-backup
2025-11-06 04:00 | 310 | 11 | Spring | 4 | 19.94 | -9 | 6.36 | 22.7 | 166.2 | 9.97 | 3.27 | 13.24 | 9 | 45 | 15 | 0 | 31.76 | 10.701 | 0 | Diesel-backup
2025-11-06 05:00 | 310 | 11 | Spring | 5 | 19.94 | -10.1 | 9.61 | 61.5 | 159.4 | 9.56 | 31.93 | 41.49 | 10.1 | 51.9 | 15 | 0 | 10.41 | 3.792 | 0 | Diesel-backup
2025-11-06 06:00 | 310 | 11 | Spring | 6 | 19.94 | -8.8 | 6.2 | 61.3 | 207.3 | 12.44 | 2.75 | 15.19 | 8.8 | 45 | 15 | 0 | 29.81 | 10.119 | 0 | Diesel-backup
2025-11-06 07:00 | 310 | 11 | Spring | 7 | 19.94 | -9.7 | 9.95 | 15.9 | 407.6 | 24.46 | 37.56 | 62.02 | 9.7 | 45 | 21.26 | 17.02 | 0 | 0 | 0 | Normal
2025-11-06 08:00 | 310 | 11 | Spring | 8 | 19.94 | -9.8 | 12.46 | 63.4 | 277.9 | 16.67 | 100.68 | 117.35 | 9.8 | 53.72 | 44.68 | 63.63 | 0 | 0 | 0 | Normal
2025-11-06 09:00 | 310 | 11 | Spring | 9 | 19.94 | -13.3 | 8.97 | 47 | 378.1 | 22.69 | 22.91 | 45.6 | 13.3 | 49.67 | 43.05 | -4.07 | 0 | 0 | 0 | Battery-supported
2025-11-06 10:00 | 310 | 11 | Spring | 10 | 19.94 | -8.9 | 9.94 | 35.7 | 456.8 | 27.41 | 37.38 | 64.79 | 8.9 | 51.67 | 47.88 | 13.12 | 0 | 0 | 0 | Normal
2025-11-06 11:00 | 310 | 11 | Spring | 11 | 19.94 | -10.5 | 6.71 | 37.7 | 464.5 | 27.87 | 4.63 | 32.5 | 10.5 | 52.66 | 39.82 | -20.16 | 0 | 0 | 0 | Battery-supported
2025-11-06 12:00 | 310 | 11 | Spring | 12 | 19.94 | -9.8 | 5.88 | 70 | 311.5 | 18.69 | 1.89 | 20.58 | 9.8 | 52.12 | 27.2 | -31.54 | 0 | 0 | 0 | Battery-supported
2025-11-06 13:00 | 310 | 11 | Spring | 13 | 19.94 | -6.8 | 1.42 | 55.2 | 379.7 | 22.78 | 0 | 22.78 | 6.8 | 54.68 | 15 | -30.5 | 1.4 | 0.527 | 0 | Diesel-backup
2025-11-06 14:00 | 310 | 11 | Spring | 14 | 19.94 | -10.3 | 12.82 | 35.3 | 458.7 | 27.52 | 113.31 | 140.83 | 10.3 | 48.3 | 49.05 | 92.53 | 0 | 0 | 0 | Normal
2025-11-06 15:00 | 310 | 11 | Spring | 15 | 19.94 | -5.3 | 8.74 | 17.9 | 505.6 | 30.34 | 20.14 | 50.48 | 5.3 | 48.15 | 49.91 | 2.33 | 0 | 0 | 0 | Normal
2025-11-06 16:00 | 310 | 11 | Spring | 16 | 19.94 | -4.8 | 9.5 | 59.6 | 293.1 | 17.59 | 30.23 | 47.82 | 4.8 | 45.34 | 50.82 | 2.48 | 0 | 0 | 0 | Normal
2025-11-06 17:00 | 310 | 11 | Spring | 17 | 19.94 | -6 | 2.82 | 28.5 | 363.8 | 21.83 | 0 | 21.83 | 6 | 48.14 | 40.3 | -26.31 | 0 | 0 | 0 | Battery-supported
2025-11-06 18:00 | 310 | 11 | Spring | 18 | 19.94 | -9.6 | 4.56 | 64.9 | 197.1 | 11.83 | 0.17 | 12 | 9.6 | 55.93 | 22.73 | -43.93 | 0 | 0 | 0 | Battery-supported
2025-11-06 19:00 | 310 | 11 | Spring | 19 | 19.94 | -12.1 | 6.48 | 37.9 | 211.6 | 12.7 | 3.7 | 16.4 | 12.1 | 54.59 | 15 | -19.31 | 18.88 | 6.672 | 0 | Diesel-backup
2025-11-06 20:00 | 310 | 11 | Spring | 20 | 19.94 | -4.8 | 3.67 | 35 | 147.7 | 8.86 | 0 | 8.86 | 4.8 | 46.7 | 15 | 0 | 37.84 | 12.456 | 0 | Diesel-backup
2025-11-06 21:00 | 310 | 11 | Spring | 21 | 19.94 | -7 | 8.89 | 50.9 | 61.7 | 3.7 | 21.92 | 25.62 | 7 | 45 | 15 | 0 | 19.38 | 6.837 | 0 | Diesel-backup
2025-11-06 22:00 | 310 | 11 | Spring | 22 | 19.94 | -9 | 8.53 | 47.7 | 0 | 0 | 17.81 | 17.81 | 9 | 47.14 | 15 | 0 | 29.33 | 9.974 | 0 | Diesel-backup
2025-11-06 23:00 | 310 | 11 | Spring | 23 | 19.94 | -5.1 | 8.21 | 37.1 | 0 | 0 | 14.62 | 14.62 | 5.1 | 45 | 15 | 0 | 30.38 | 10.29 | 0 | Diesel-backup
2025-11-07 | 311 | 11 | Spring | 0 | 20.17 | -9.7 | 12.67 | 14.3 | 0 | 0 | 107.92 | 107.92 | 9.7 | 45 | 38.15 | 62.92 | 0 | 0 | 0 | Normal
2025-11-07 01:00 | 311 | 11 | Spring | 1 | 20.17 | -9.1 | 8.98 | 17.3 | 0 | 0 | 23.03 | 23.03 | 9.1 | 45 | 29.37 | -21.97 | 0 | 0 | 0 | Battery-supported
2025-11-07 02:00 | 311 | 11 | Spring | 2 | 20.17 | -7.4 | 16.17 | 50 | 5.6 | 0.34 | 120 | 120.34 | 7.4 | 45 | 57.09 | 75.34 | 0 | 0 | 0 | Normal
2025-11-07 03:00 | 311 | 11 | Spring | 3 | 20.17 | -11.4 | 9.17 | 38.7 | 78.4 | 4.7 | 25.51 | 30.21 | 11.4 | 46.96 | 50.39 | -16.75 | 0 | 0 | 0 | Battery-supported
2025-11-07 04:00 | 311 | 11 | Spring | 4 | 20.17 | -9.5 | 5.15 | 37.4 | 150.7 | 9.04 | 0.63 | 9.67 | 9.5 | 45 | 36.26 | -35.33 | 0 | 0 | 0 | Battery-supported
2025-11-07 05:00 | 311 | 11 | Spring | 5 | 20.17 | -7.2 | 7.73 | 28.9 | 237.6 | 14.26 | 10.59 | 24.85 | 7.2 | 45 | 28.2 | -20.15 | 0 | 0 | 0 | Battery-supported
2025-11-07 06:00 | 311 | 11 | Spring | 6 | 20.17 | -9.3 | 0.95 | 12.3 | 353.9 | 21.23 | 0 | 21.23 | 9.3 | 46.48 | 18.1 | -25.25 | 0 | 0 | 0 | Battery-supported
2025-11-07 07:00 | 311 | 11 | Spring | 7 | 20.17 | -7.2 | 9.53 | 64.6 | 240.7 | 14.44 | 30.69 | 45.13 | 7.2 | 45 | 18.15 | 0.13 | 0 | 0 | 0 | Normal
2025-11-07 08:00 | 311 | 11 | Spring | 8 | 20.17 | -7.5 | 4.64 | 58.5 | 298.9 | 17.93 | 0.21 | 18.14 | 7.5 | 52.53 | 15 | -7.87 | 26.52 | 9.114 | 0 | Diesel-backup
2025-11-07 09:00 | 311 | 11 | Spring | 9 | 20.17 | -9.9 | 8.38 | 46.3 | 382.4 | 22.94 | 16.27 | 39.21 | 9.9 | 54.87 | 15 | 0 | 15.66 | 5.599 | 0 | Diesel-backup
2025-11-07 10:00 | 311 | 11 | Spring | 10 | 20.17 | -15 | 5.11 | 28.2 | 492.4 | 29.54 | 0.58 | 30.12 | 15 | 61.82 | 15 | 0 | 31.7 | 10.684 | 0 | Diesel-backup
2025-11-07 11:00 | 311 | 11 | Spring | 11 | 20.17 | -12 | 3.65 | 48.8 | 410.6 | 24.64 | 0 | 24.64 | 12 | 56.44 | 15 | 0 | 31.8 | 10.713 | 0 | Diesel-backup
2025-11-07 12:00 | 311 | 11 | Spring | 12 | 20.17 | -7.6 | 19.01 | 50.3 | 408.7 | 24.52 | 120 | 144.52 | 7.6 | 51.46 | 49.25 | 93.06 | 0 | 0 | 0 | Normal
2025-11-07 13:00 | 311 | 11 | Spring | 13 | 20.17 | -12.3 | 5.04 | 37.9 | 463.8 | 27.83 | 0.51 | 28.34 | 12.3 | 54.63 | 38.73 | -26.29 | 0 | 0 | 0 | Battery-supported
2025-11-07 14:00 | 311 | 11 | Spring | 14 | 20.17 | -9.2 | 4.47 | 34.5 | 462.6 | 27.76 | 0.13 | 27.89 | 9.2 | 53.23 | 28.59 | -25.34 | 0 | 0 | 0 | Battery-supported
2025-11-07 15:00 | 311 | 11 | Spring | 15 | 20.17 | -7.4 | 11.66 | 29 | 458.2 | 27.49 | 76.05 | 103.54 | 7.4 | 52.48 | 47.38 | 51.06 | 0 | 0 | 0 | Normal
2025-11-07 16:00 | 311 | 11 | Spring | 16 | 20.17 | -4.5 | 6.33 | 48.9 | 337.4 | 20.24 | 3.17 | 23.41 | 4.5 | 49.46 | 36.96 | -26.05 | 0 | 0 | 0 | Battery-supported
2025-11-07 17:00 | 311 | 11 | Spring | 17 | 20.17 | -8.7 | 4.8 | 63.2 | 245.6 | 14.74 | 0.31 | 15.05 | 8.7 | 50.98 | 22.59 | -35.93 | 0 | 0 | 0 | Battery-supported
2025-11-07 18:00 | 311 | 11 | Spring | 18 | 20.17 | -8.6 | 11.84 | 70.8 | 182.8 | 10.97 | 81.19 | 92.16 | 8.6 | 60.09 | 34.39 | 32.07 | 0 | 0 | 0 | Normal
2025-11-07 19:00 | 311 | 11 | Spring | 19 | 20.17 | -7.2 | 7.59 | 95.3 | 86.5 | 5.19 | 9.58 | 14.77 | 7.2 | 56.33 | 17.77 | -41.56 | 0 | 0 | 0 | Battery-supported
2025-11-07 20:00 | 311 | 11 | Spring | 20 | 20.17 | -6.2 | 12.75 | 52 | 127.7 | 7.66 | 110.77 | 118.43 | 6.2 | 45.92 | 44.45 | 72.51 | 0 | 0 | 0 | Normal
2025-11-07 21:00 | 311 | 11 | Spring | 21 | 20.17 | -7.4 | 16.49 | 47.4 | 71.2 | 4.27 | 120 | 124.27 | 7.4 | 45 | 73.62 | 79.27 | 0 | 0 | 0 | Normal
2025-11-07 22:00 | 311 | 11 | Spring | 22 | 20.17 | -4.9 | 6.23 | 69 | 4.3 | 0.26 | 2.85 | 3.11 | 4.9 | 46.34 | 56.33 | -43.23 | 0 | 0 | 0 | Battery-supported
2025-11-07 23:00 | 311 | 11 | Spring | 23 | 20.17 | -9.2 | 11.29 | 84.4 | 0 | 0 | 66.16 | 66.16 | 9.2 | 45 | 64.12 | 21.16 | 0 | 0 | 0 | Normal
2025-11-08 | 312 | 11 | Spring | 0 | 20.42 | -7.3 | 16.86 | 38 | 0 | 0 | 120 | 120 | 7.3 | 45 | 91.72 | 75 | 0 | 0 | 0 | Normal
2025-11-08 01:00 | 312 | 11 | Spring | 1 | 20.42 | -7 | 19.38 | 25.8 | 0 | 0 | 120 | 120 | 7 | 52.7 | 95 | 8.91 | 0 | 0 | 0 | Normal
2025-11-08 02:00 | 312 | 11 | Spring | 2 | 20.42 | -9.2 | 5.42 | 81 | 8.3 | 0.5 | 0.99 | 1.49 | 9.2 | 45 | 77.6 | -43.51 | 0 | 0 | 0 | Battery-supported
2025-11-08 03:00 | 312 | 11 | Spring | 3 | 20.42 | -6.9 | 13.75 | 55.6 | 70.8 | 4.25 | 120 | 124.25 | 6.9 | 45 | 95 | 47.29 | 0 | 0 | 0 | Normal
2025-11-08 04:00 | 312 | 11 | Spring | 4 | 20.42 | -8.7 | 1.61 | 7.5 | 206.4 | 12.38 | 0 | 12.38 | 8.7 | 45 | 81.95 | -32.62 | 0 | 0 | 0 | Battery-supported
2025-11-08 05:00 | 312 | 11 | Spring | 5 | 20.42 | -7.6 | 9.06 | 22 | 259.5 | 15.57 | 24.06 | 39.63 | 7.6 | 45 | 79.8 | -5.37 | 0 | 0 | 0 | Battery-supported
2025-11-08 06:00 | 312 | 11 | Spring | 6 | 20.42 | -9.2 | 3.07 | 71.7 | 183 | 10.98 | 0 | 10.98 | 9.2 | 47.44 | 65.22 | -36.46 | 0 | 0 | 0 | Battery-supported
2025-11-08 07:00 | 312 | 11 | Spring | 7 | 20.42 | -8.9 | 6.21 | 56.8 | 270.5 | 16.23 | 2.79 | 19.02 | 8.9 | 45 | 54.83 | -25.98 | 0 | 0 | 0 | Battery-supported
2025-11-08 08:00 | 312 | 11 | Spring | 8 | 20.42 | -11.2 | 24.18 | 49 | 338.6 | 20.32 | 120 | 140.32 | 11.2 | 48.55 | 88.6 | 91.77 | 0 | 0 | 0 | Normal
2025-11-08 09:00 | 312 | 11 | Spring | 9 | 20.42 | -11.2 | 12.84 | 33.2 | 441.2 | 26.47 | 114.04 | 140.51 | 11.2 | 45 | 95 | 17.39 | 0 | 0 | 0 | Normal
2025-11-08 10:00 | 312 | 11 | Spring | 10 | 20.42 | -6.9 | 3.12 | 7 | 592.4 | 35.54 | 0 | 35.54 | 6.9 | 51.85 | 88.48 | -16.31 | 0 | 0 | 0 | Battery-supported
2025-11-08 11:00 | 312 | 11 | Spring | 11 | 20.42 | -8 | 3.85 | 30.6 | 499.2 | 29.95 | 0.01 | 29.96 | 8 | 51.24 | 79.96 | -21.28 | 0 | 0 | 0 | Battery-supported
2025-11-08 12:00 | 312 | 11 | Spring | 12 | 20.42 | -11.3 | 14.52 | 37.3 | 472.3 | 28.34 | 120 | 148.34 | 11.3 | 59.12 | 95 | 40.86 | 0 | 0 | 0 | Normal
2025-11-08 13:00 | 312 | 11 | Spring | 13 | 20.42 | -8.3 | 14.25 | 96.3 | 179.9 | 10.79 | 120 | 130.79 | 8.3 | 48.75 | 95 | 0 | 0 | 0 | 0 | Normal
2025-11-08 14:00 | 312 | 11 | Spring | 14 | 20.42 | -13.5 | 14.68 | 67.8 | 307.3 | 18.44 | 120 | 138.44 | 13.5 | 55.4 | 95 | 0 | 0 | 0 | 0 | Normal
2025-11-08 15:00 | 312 | 11 | Spring | 15 | 20.42 | -9.2 | 9.03 | 28 | 463.8 | 27.83 | 23.67 | 51.5 | 9.2 | 50.02 | 95 | 0 | 0 | 0 | 0 | Normal
2025-11-08 16:00 | 312 | 11 | Spring | 16 | 20.42 | -5.5 | 12.81 | 42.1 | 366.4 | 21.98 | 112.94 | 134.92 | 5.5 | 46.03 | 95 | 0 | 0 | 0 | 0 | Normal
2025-11-08 17:00 | 312 | 11 | Spring | 17 | 20.42 | -7.5 | 6.4 | 13.9 | 422.3 | 25.34 | 3.41 | 28.75 | 7.5 | 52.01 | 85.7 | -23.26 | 0 | 0 | 0 | Battery-supported
2025-11-08 18:00 | 312 | 11 | Spring | 18 | 20.42 | -6.8 | 6.22 | 74.7 | 174.2 | 10.45 | 2.82 | 13.27 | 6.8 | 47.95 | 71.82 | -34.68 | 0 | 0 | 0 | Battery-supported
2025-11-08 19:00 | 312 | 11 | Spring | 19 | 20.42 | -13.5 | 8.74 | 33.9 | 231.8 | 13.91 | 20.14 | 34.05 | 13.5 | 49.74 | 65.55 | -15.69 | 0 | 0 | 0 | Battery-supported
2025-11-08 20:00 | 312 | 11 | Spring | 20 | 20.42 | -7.7 | 4.73 | 35.2 | 161 | 9.66 | 0.26 | 9.92 | 7.7 | 55.93 | 47.14 | -46.01 | 0 | 0 | 0 | Battery-supported
2025-11-08 21:00 | 312 | 11 | Spring | 21 | 20.42 | -6.1 | 4.24 | 63.9 | 63.2 | 3.79 | 0.06 | 3.85 | 6.1 | 45 | 30.68 | -41.15 | 0 | 0 | 0 | Battery-supported
2025-11-08 22:00 | 312 | 11 | Spring | 22 | 20.42 | -6 | 10.84 | 81.5 | 8.3 | 0.5 | 55.35 | 55.85 | 6 | 45 | 34.68 | 10.85 | 0 | 0 | 0 | Normal
2025-11-08 23:00 | 312 | 11 | Spring | 23 | 20.42 | -5.1 | 11.4 | 50.4 | 0 | 0 | 69.01 | 69.01 | 5.1 | 45.32 | 43.39 | 23.69 | 0 | 0 | 0 | Normal
2025-11-09 | 313 | 11 | Spring | 0 | 20.68 | -7.8 | 4.3 | 63.3 | 0 | 0 | 0.07 | 0.07 | 7.8 | 45 | 25.42 | -44.93 | 0 | 0 | 0 | Battery-supported
2025-11-09 01:00 | 313 | 11 | Spring | 1 | 20.68 | -8.1 | 5.42 | 34.3 | 0 | 0 | 0.99 | 0.99 | 8.1 | 45 | 15 | -26.06 | 17.95 | 6.367 | 0 | Diesel-backup
2025-11-09 02:00 | 313 | 11 | Spring | 2 | 20.68 | -11.1 | 9.94 | 42.9 | 23 | 1.38 | 37.38 | 38.76 | 11.1 | 45 | 15 | 0 | 6.24 | 2.306 | 0 | Diesel-backup
2025-11-09 03:00 | 313 | 11 | Spring | 3 | 20.68 | -9 | 9.46 | 64.6 | 68.3 | 4.1 | 29.63 | 33.73 | 9 | 47.41 | 15 | 0 | 13.68 | 4.926 | 0 | Diesel-backup
2025-11-09 04:00 | 313 | 11 | Spring | 4 | 20.68 | -11.7 | 9.01 | 35.7 | 167.2 | 10.03 | 23.41 | 33.44 | 11.7 | 45 | 15 | 0 | 11.56 | 4.194 | 0 | Diesel-backup
2025-11-09 05:00 | 313 | 11 | Spring | 5 | 20.68 | -13.3 | 4.44 | 8.5 | 298.4 | 17.9 | 0.12 | 18.02 | 13.3 | 49.08 | 15 | 0 | 31.06 | 10.493 | 0 | Diesel-backup
2025-11-09 06:00 | 313 | 11 | Spring | 6 | 20.68 | -11.8 | 25.91 | 45.9 | 263.4 | 15.8 | 120 | 135.8 | 11.8 | 48.87 | 46.99 | 86.93 | 0 | 0 | 0 | Normal
2025-11-09 07:00 | 313 | 11 | Spring | 7 | 20.68 | -6.3 | 5.86 | 18.2 | 410.8 | 24.65 | 1.84 | 26.49 | 6.3 | 45 | 39.59 | -18.51 | 0 | 0 | 0 | Battery-supported
2025-11-09 08:00 | 313 | 11 | Spring | 8 | 20.68 | -10.2 | 10.17 | 74.2 | 239 | 14.34 | 41.53 | 55.87 | 10.2 | 58.11 | 38.69 | -2.24 | 0 | 0 | 0 | Battery-supported
2025-11-09 09:00 | 313 | 11 | Spring | 9 | 20.68 | -9.1 | 3.62 | 57.4 | 335.4 | 20.12 | 0 | 20.12 | 9.1 | 45 | 28.74 | -24.88 | 0 | 0 | 0 | Battery-supported
2025-11-09 10:00 | 313 | 11 | Spring | 10 | 20.68 | -10.6 | 7.54 | 27.3 | 497.9 | 29.87 | 9.23 | 39.1 | 10.6 | 48.28 | 25.07 | -9.18 | 0 | 0 | 0 | Battery-supported
2025-11-09 11:00 | 313 | 11 | Spring | 11 | 20.68 | -13.1 | 4.23 | 27.2 | 516 | 30.96 | 0.05 | 31.01 | 13.1 | 55.96 | 15.09 | -24.95 | 0 | 0 | 0 | Battery-supported
2025-11-09 12:00 | 313 | 11 | Spring | 12 | 20.68 | -6.8 | 5.71 | 20.6 | 554.7 | 33.28 | 1.51 | 34.79 | 6.8 | 52.65 | 15 | -0.22 | 17.64 | 6.264 | 0 | Diesel-backup
2025-11-09 13:00 | 313 | 11 | Spring | 13 | 20.68 | -13.3 | 9.11 | 68.5 | 315.3 | 18.92 | 24.71 | 43.63 | 13.3 | 50.83 | 15 | 0 | 7.2 | 2.652 | 0 | Diesel-backup
2025-11-09 14:00 | 313 | 11 | Spring | 14 | 20.68 | -9.4 | 15.89 | 60.9 | 340.1 | 20.41 | 120 | 140.41 | 9.4 | 55.29 | 46.32 | 85.12 | 0 | 0 | 0 | Normal
2025-11-09 15:00 | 313 | 11 | Spring | 15 | 20.68 | -7.9 | 5.34 | 64.8 | 302.5 | 18.15 | 0.87 | 19.02 | 7.9 | 54.17 | 32.26 | -35.15 | 0 | 0 | 0 | Battery-supported
2025-11-09 16:00 | 313 | 11 | Spring | 16 | 20.68 | -6.9 | 8.85 | 92.2 | 166.1 | 9.97 | 21.43 | 31.4 | 6.9 | 48.32 | 25.5 | -16.92 | 0 | 0 | 0 | Battery-supported
2025-11-09 17:00 | 313 | 11 | Spring | 17 | 20.68 | -8.7 | 10.1 | 70.2 | 225.1 | 13.51 | 40.24 | 53.75 | 8.7 | 52.22 | 26.06 | 1.53 | 0 | 0 | 0 | Normal
2025-11-09 18:00 | 313 | 11 | Spring | 18 | 20.68 | -10.9 | 11.65 | 77.9 | 167.2 | 10.03 | 75.77 | 85.8 | 10.9 | 58.57 | 36.08 | 27.23 | 0 | 0 | 0 | Normal
2025-11-09 19:00 | 313 | 11 | Spring | 19 | 20.68 | -8.4 | 2.02 | 44.6 | 212.1 | 12.73 | 0 | 12.73 | 8.4 | 57.5 | 18.17 | -44.77 | 0 | 0 | 0 | Battery-supported
2025-11-09 20:00 | 313 | 11 | Spring | 20 | 20.68 | -8.3 | 12.63 | 63.3 | 119.9 | 7.19 | 106.52 | 113.71 | 8.3 | 49.24 | 41.9 | 64.47 | 0 | 0 | 0 | Normal
2025-11-09 21:00 | 313 | 11 | Spring | 21 | 20.68 | -8.4 | 10.16 | 66.9 | 66 | 3.96 | 41.35 | 45.31 | 8.4 | 45 | 42.01 | 0.31 | 0 | 0 | 0 | Normal
2025-11-09 22:00 | 313 | 11 | Spring | 22 | 20.68 | -4.7 | 9 | 21.5 | 28.4 | 1.7 | 23.29 | 24.99 | 4.7 | 45 | 34.01 | -20.01 | 0 | 0 | 0 | Battery-supported
2025-11-09 23:00 | 313 | 11 | Spring | 23 | 20.68 | -9.7 | 24.97 | 30.1 | 0 | 0 | 120 | 120 | 9.7 | 45 | 61.61 | 75 | 0 | 0 | 0 | Normal
2025-11-10 | 314 | 11 | Spring | 0 | 20.96 | -6.5 | 4.92 | 0.7 | 0 | 0 | 0.4 | 0.4 | 6.5 | 46.5 | 43.17 | -46.1 | 0 | 0 | 0 | Battery-supported
2025-11-10 01:00 | 314 | 11 | Spring | 1 | 20.96 | -7.2 | 9.44 | 91.5 | 0 | 0 | 29.33 | 29.33 | 7.2 | 45 | 36.9 | -15.67 | 0 | 0 | 0 | Battery-supported
2025-11-10 02:00 | 314 | 11 | Spring | 2 | 20.96 | -5.8 | 21.97 | 43 | 31.8 | 1.91 | 120 | 121.91 | 5.8 | 45 | 65.2 | 76.91 | 0 | 0 | 0 | Normal
2025-11-10 03:00 | 314 | 11 | Spring | 3 | 20.96 | -8.6 | 14.85 | 31.4 | 110.2 | 6.61 | 120 | 126.61 | 8.6 | 48.07 | 94.1 | 78.54 | 0 | 0 | 0 | Normal
2025-11-10 04:00 | 314 | 11 | Spring | 4 | 20.96 | -7 | 6.15 | 55.8 | 138.5 | 8.31 | 2.6 | 10.91 | 7 | 45.09 | 80.43 | -34.18 | 0 | 0 | 0 | Battery-supported
2025-11-10 05:00 | 314 | 11 | Spring | 5 | 20.96 | -9.4 | 8.89 | 92.1 | 100.9 | 6.05 | 21.92 | 27.97 | 9.4 | 48.3 | 72.3 | -20.33 | 0 | 0 | 0 | Battery-supported
2025-11-10 06:00 | 314 | 11 | Spring | 6 | 20.96 | -8.3 | 9.05 | 39.3 | 287.6 | 17.26 | 23.93 | 41.19 | 8.3 | 45.52 | 70.57 | -4.33 | 0 | 0 | 0 | Battery-supported
2025-11-10 07:00 | 314 | 11 | Spring | 7 | 20.96 | -12.7 | 6.72 | 76 | 206.6 | 12.4 | 4.67 | 17.07 | 12.7 | 53.36 | 56.05 | -36.29 | 0 | 0 | 0 | Battery-supported
2025-11-10 08:00 | 314 | 11 | Spring | 8 | 20.96 | -15.3 | 3.18 | 68.7 | 262.3 | 15.74 | 0 | 15.74 | 15.3 | 52.82 | 41.22 | -37.08 | 0 | 0 | 0 | Battery-supported
2025-11-10 09:00 | 314 | 11 | Spring | 9 | 20.96 | -8.6 | 6.21 | 25.4 | 478.2 | 28.69 | 2.79 | 31.48 | 8.6 | 53.69 | 32.34 | -22.21 | 0 | 0 | 0 | Battery-supported
2025-11-10 10:00 | 314 | 11 | Spring | 10 | 20.96 | -8.3 | 10.56 | 66.2 | 315.3 | 18.92 | 49.25 | 68.17 | 8.3 | 57.59 | 36.23 | 10.58 | 0 | 0 | 0 | Normal
2025-11-10 11:00 | 314 | 11 | Spring | 11 | 20.96 | -8 | 6.13 | 44.9 | 430 | 25.8 | 2.55 | 28.35 | 8 | 49.73 | 27.68 | -21.38 | 0 | 0 | 0 | Battery-supported
2025-11-10 12:00 | 314 | 11 | Spring | 12 | 20.96 | -9.9 | 7.51 | 67.8 | 322.6 | 19.36 | 9.02 | 28.38 | 9.9 | 50.61 | 18.79 | -22.23 | 0 | 0 | 0 | Battery-supported
2025-11-10 13:00 | 314 | 11 | Spring | 13 | 20.96 | -5.1 | 15.94 | 16 | 571 | 34.26 | 120 | 154.26 | 5.1 | 46.62 | 58.4 | 107.64 | 0 | 0 | 0 | Normal
2025-11-10 14:00 | 314 | 11 | Spring | 14 | 20.96 | -9 | 7.53 | 54.7 | 369.8 | 22.19 | 9.16 | 31.35 | 9 | 52.01 | 50.13 | -20.66 | 0 | 0 | 0 | Battery-supported
2025-11-10 15:00 | 314 | 11 | Spring | 15 | 20.96 | -6.6 | 7.83 | 61.9 | 316.3 | 18.98 | 11.36 | 30.34 | 6.6 | 53.92 | 40.7 | -23.58 | 0 | 0 | 0 | Battery-supported
2025-11-10 16:00 | 314 | 11 | Spring | 16 | 20.96 | -5.9 | 8.43 | 54.3 | 321 | 19.26 | 16.77 | 36.03 | 5.9 | 48.92 | 35.55 | -12.89 | 0 | 0 | 0 | Battery-supported
2025-11-10 17:00 | 314 | 11 | Spring | 17 | 20.96 | -3.1 | 5.79 | 23.5 | 395.4 | 23.72 | 1.68 | 25.4 | 3.1 | 50.63 | 25.45 | -25.23 | 0 | 0 | 0 | Battery-supported
2025-11-10 18:00 | 314 | 11 | Spring | 18 | 20.96 | -7.3 | 12.81 | 38.4 | 290.4 | 17.42 | 112.94 | 130.36 | 7.3 | 52.23 | 54.21 | 78.13 | 0 | 0 | 0 | Normal
2025-11-10 19:00 | 314 | 11 | Spring | 19 | 20.96 | -7.9 | 3.61 | 84.1 | 120.6 | 7.24 | 0 | 7.24 | 7.9 | 54.65 | 35.24 | -47.41 | 0 | 0 | 0 | Battery-supported
2025-11-10 20:00 | 314 | 11 | Spring | 20 | 20.96 | -9.7 | 5.77 | 72.6 | 108.4 | 6.5 | 1.64 | 8.14 | 9.7 | 52.89 | 17.34 | -44.75 | 0 | 0 | 0 | Battery-supported
2025-11-10 21:00 | 314 | 11 | Spring | 21 | 20.96 | -3.1 | 8.92 | 69.4 | 69.1 | 4.15 | 22.28 | 26.43 | 3.1 | 45 | 15 | -5.85 | 12.72 | 4.595 | 0 | Diesel-backup
2025-11-10 22:00 | 314 | 11 | Spring | 22 | 20.96 | -5.7 | 6.36 | 11.6 | 42.8 | 2.57 | 3.27 | 5.84 | 5.7 | 45 | 15 | 0 | 39.16 | 12.824 | 0 | Diesel-backup
2025-11-10 23:00 | 314 | 11 | Spring | 23 | 20.96 | -5.9 | 18.26 | 42.3 | 0 | 0 | 120 | 120 | 5.9 | 45 | 42.6 | 75 | 0 | 0 | 0 | Normal
2025-11-11 | 315 | 11 | Spring | 0 | 21.25 | -0.2 | 7.84 | 60.7 | 0 | 0 | 11.44 | 11.44 | 0.2 | 45 | 29.18 | -33.56 | 0 | 0 | 0 | Battery-supported
2025-11-11 01:00 | 315 | 11 | Spring | 1 | 21.25 | -6.7 | 7.72 | 10.9 | 0 | 0 | 10.52 | 10.52 | 6.7 | 45 | 15.38 | -34.48 | 0 | 0 | 0 | Battery-supported
2025-11-11 02:00 | 315 | 11 | Spring | 2 | 21.25 | -10.6 | 4.26 | 83.1 | 22.8 | 1.37 | 0.06 | 1.43 | 10.6 | 45.22 | 15 | -0.96 | 42.83 | 13.825 | 0 | Diesel-backup
2025-11-11 03:00 | 315 | 11 | Spring | 3 | 21.25 | -8.6 | 6.42 | 58.5 | 87.6 | 5.26 | 3.48 | 8.74 | 8.6 | 46.24 | 15 | 0 | 37.5 | 12.36 | 0 | Diesel-backup
2025-11-11 04:00 | 315 | 11 | Spring | 4 | 21.25 | -10.7 | 12.45 | 31.1 | 190.3 | 11.42 | 100.34 | 111.76 | 10.7 | 45.79 | 39.28 | 65.97 | 0 | 0 | 0 | Normal
2025-11-11 05:00 | 315 | 11 | Spring | 5 | 21.25 | -9.7 | 5.06 | 31.5 | 255.9 | 15.35 | 0.53 | 15.88 | 9.7 | 45 | 27.63 | -29.12 | 0 | 0 | 0 | Battery-supported
2025-11-11 06:00 | 315 | 11 | Spring | 6 | 21.25 | -9.9 | 2.38 | 79.7 | 166.7 | 10 | 0 | 10 | 9.9 | 45 | 15 | -31.57 | 3.43 | 1.279 | 0 | Diesel-backup
2025-11-11 07:00 | 315 | 11 | Spring | 7 | 21.25 | -10.5 | 7.09 | 21 | 408.6 | 24.52 | 6.48 | 31 | 10.5 | 47.59 | 15 | 0 | 16.59 | 5.912 | 0 | Diesel-backup
2025-11-11 08:00 | 315 | 11 | Spring | 8 | 21.25 | -12.3 | 8.06 | 50.8 | 336.9 | 20.21 | 13.27 | 33.48 | 12.3 | 60.3 | 15 | 0 | 26.82 | 9.207 | 0 | Diesel-backup
2025-11-11 09:00 | 315 | 11 | Spring | 9 | 21.25 | -5.7 | 5.99 | 38.5 | 421.3 | 25.28 | 2.16 | 27.44 | 5.7 | 50.71 | 15 | 0 | 23.27 | 8.094 | 0 | Diesel-backup
2025-11-11 10:00 | 315 | 11 | Spring | 10 | 21.25 | -8.4 | 16.02 | 56.8 | 360.4 | 21.62 | 120 | 141.62 | 8.4 | 51.3 | 48.24 | 90.32 | 0 | 0 | 0 | Normal
2025-11-11 11:00 | 315 | 11 | Spring | 11 | 21.25 | -9.3 | 23.88 | 57.8 | 367.4 | 22.04 | 120 | 142.04 | 9.3 | 54.09 | 80.6 | 87.95 | 0 | 0 | 0 | Normal
2025-11-11 12:00 | 315 | 11 | Spring | 12 | 21.25 | -6.8 | 8.85 | 81 | 257.5 | 15.45 | 21.43 | 36.88 | 6.8 | 57.09 | 72.52 | -20.21 | 0 | 0 | 0 | Battery-supported
2025-11-11 13:00 | 315 | 11 | Spring | 13 | 21.25 | -7.1 | 6.38 | 88.3 | 219.2 | 13.15 | 3.34 | 16.49 | 7.1 | 50.12 | 59.07 | -33.63 | 0 | 0 | 0 | Battery-supported
2025-11-11 14:00 | 315 | 11 | Spring | 14 | 21.25 | -7.2 | 10.52 | 39.4 | 442 | 26.52 | 48.42 | 74.94 | 7.2 | 45 | 70.09 | 29.94 | 0 | 0 | 0 | Normal
2025-11-11 15:00 | 315 | 11 | Spring | 15 | 21.25 | -5.9 | 16.08 | 62.1 | 316.4 | 18.98 | 120 | 138.98 | 5.9 | 46.93 | 95 | 67.7 | 0 | 0 | 0 | Normal
2025-11-11 16:00 | 315 | 11 | Spring | 16 | 21.25 | -6.7 | 5.31 | 61.2 | 294.6 | 17.68 | 0.83 | 18.51 | 6.7 | 46.63 | 83.75 | -28.12 | 0 | 0 | 0 | Battery-supported
2025-11-11 17:00 | 315 | 11 | Spring | 17 | 21.25 | -5.2 | 12.08 | 79 | 197.4 | 11.84 | 88.4 | 100.24 | 5.2 | 45 | 95 | 30.57 | 0 | 0 | 0 | Normal
2025-11-11 18:00 | 315 | 11 | Spring | 18 | 21.25 | -4.8 | 7.09 | 42.5 | 282.2 | 16.93 | 6.48 | 23.41 | 4.8 | 45 | 86.36 | -21.59 | 0 | 0 | 0 | Battery-supported
2025-11-11 19:00 | 315 | 11 | Spring | 19 | 21.25 | -6 | 14.3 | 84.6 | 122.4 | 7.34 | 120 | 127.34 | 6 | 59.95 | 95 | 23.47 | 0 | 0 | 0 | Normal
2025-11-11 20:00 | 315 | 11 | Spring | 20 | 21.25 | -6.7 | 4.26 | 64.6 | 128 | 7.68 | 0.06 | 7.74 | 6.7 | 45.52 | 79.89 | -37.78 | 0 | 0 | 0 | Battery-supported
2025-11-11 21:00 | 315 | 11 | Spring | 21 | 21.25 | -2.9 | 17.2 | 40.7 | 108.5 | 6.51 | 120 | 126.51 | 2.9 | 45 | 95 | 41.07 | 0 | 0 | 0 | Normal
2025-11-11 22:00 | 315 | 11 | Spring | 22 | 21.25 | -7.5 | 9.02 | 44.4 | 40.4 | 2.42 | 23.54 | 25.96 | 7.5 | 53.56 | 83.96 | -27.6 | 0 | 0 | 0 | Battery-supported
2025-11-11 23:00 | 315 | 11 | Spring | 23 | 21.25 | -5.8 | 10.51 | 0 | 0 | 0 | 48.21 | 48.21 | 5.8 | 45 | 85.14 | 3.21 | 0 | 0 | 0 | Normal
2025-11-12 | 316 | 11 | Spring | 0 | 21.57 | -5.9 | 3.81 | 28.8 | 0 | 0 | 0 | 0 | 5.9 | 45 | 67.14 | -45 | 0 | 0 | 0 | Battery-supported
2025-11-12 01:00 | 316 | 11 | Spring | 1 | 21.57 | -8.5 | 3.73 | 76.2 | 0 | 0 | 0 | 0 | 8.5 | 45.51 | 48.94 | -45.51 | 0 | 0 | 0 | Battery-supported
2025-11-12 02:00 | 316 | 11 | Spring | 2 | 21.57 | -9.4 | 9.52 | 26.9 | 59.9 | 3.59 | 30.54 | 34.13 | 9.4 | 45.02 | 44.58 | -10.89 | 0 | 0 | 0 | Battery-supported
2025-11-12 03:00 | 316 | 11 | Spring | 3 | 21.57 | -8.7 | 10.65 | 49.8 | 105.8 | 6.35 | 51.16 | 57.51 | 8.7 | 45 | 49.18 | 12.51 | 0 | 0 | 0 | Normal
2025-11-12 04:00 | 316 | 11 | Spring | 4 | 21.57 | -9.4 | 6.7 | 98.5 | 67.7 | 4.06 | 4.59 | 8.65 | 9.4 | 45.54 | 34.43 | -36.89 | 0 | 0 | 0 | Battery-supported
2025-11-12 05:00 | 316 | 11 | Spring | 5 | 21.57 | -11.8 | 11.29 | 74.2 | 152.4 | 9.14 | 66.16 | 75.3 | 11.8 | 48.84 | 44.17 | 26.46 | 0 | 0 | 0 | Normal
2025-11-12 06:00 | 316 | 11 | Spring | 6 | 21.57 | -10.3 | 3.79 | 55.3 | 246.6 | 14.8 | 0 | 14.8 | 10.3 | 45 | 32.09 | -30.2 | 0 | 0 | 0 | Battery-supported
2025-11-12 07:00 | 316 | 11 | Spring | 7 | 21.57 | -8.4 | 3 | 17.7 | 424.6 | 25.48 | 0 | 25.48 | 8.4 | 45 | 24.28 | -19.52 | 0 | 0 | 0 | Battery-supported
2025-11-12 08:00 | 316 | 11 | Spring | 8 | 21.57 | -6.3 | 8.4 | 96.2 | 152.5 | 9.15 | 16.47 | 25.62 | 6.3 | 45 | 16.53 | -19.38 | 0 | 0 | 0 | Battery-supported
2025-11-12 09:00 | 316 | 11 | Spring | 9 | 21.57 | -7.8 | 3.69 | 50.9 | 367.2 | 22.03 | 0 | 22.03 | 7.8 | 47.04 | 15 | -3.82 | 21.19 | 7.428 | 0 | Diesel-backup
2025-11-12 10:00 | 316 | 11 | Spring | 10 | 21.57 | -14.6 | 2.41 | 34.5 | 465.5 | 27.93 | 0 | 27.93 | 14.6 | 59.53 | 15 | 0 | 31.6 | 10.654 | 0 | Diesel-backup
2025-11-12 11:00 | 316 | 11 | Spring | 11 | 21.57 | -7.2 | 4.47 | 34.5 | 481.1 | 28.87 | 0.13 | 29 | 7.2 | 48.32 | 15 | 0 | 19.32 | 6.817 | 0 | Diesel-backup
2025-11-12 12:00 | 316 | 11 | Spring | 12 | 21.57 | -9.6 | 10.44 | 86.8 | 228.7 | 13.72 | 46.78 | 60.5 | 9.6 | 51.48 | 18.32 | 9.02 | 0 | 0 | 0 | Normal
2025-11-12 13:00 | 316 | 11 | Spring | 13 | 21.57 | -7 | 8.88 | 45.8 | 426.1 | 25.57 | 21.8 | 47.37 | 7 | 45 | 19.19 | 2.37 | 0 | 0 | 0 | Normal
2025-11-12 14:00 | 316 | 11 | Spring | 14 | 21.57 | -7.6 | 16.13 | 51.2 | 387 | 23.22 | 120 | 143.22 | 7.6 | 45.03 | 55.33 | 98.19 | 0 | 0 | 0 | Normal
2025-11-12 15:00 | 316 | 11 | Spring | 15 | 21.57 | -7.6 | 9.23 | 57.6 | 337.6 | 20.26 | 26.33 | 46.59 | 7.6 | 45.79 | 55.62 | 0.8 | 0 | 0 | 0 | Normal
2025-11-12 16:00 | 316 | 11 | Spring | 16 | 21.57 | -7.1 | 3.89 | 25.6 | 442.6 | 26.56 | 0.01 | 26.57 | 7.1 | 45 | 48.25 | -18.43 | 0 | 0 | 0 | Battery-supported
2025-11-12 17:00 | 316 | 11 | Spring | 17 | 21.57 | -6.6 | 10.84 | 70.9 | 229.4 | 13.76 | 55.35 | 69.11 | 6.6 | 50.2 | 55.21 | 18.91 | 0 | 0 | 0 | Normal
2025-11-12 18:00 | 316 | 11 | Spring | 18 | 21.57 | -3.3 | 5.2 | 18.2 | 363.7 | 21.82 | 0.69 | 22.51 | 3.3 | 46.47 | 45.62 | -23.96 | 0 | 0 | 0 | Battery-supported
2025-11-12 19:00 | 316 | 11 | Spring | 19 | 21.57 | -6.2 | 6.62 | 82.5 | 131 | 7.86 | 4.25 | 12.11 | 6.2 | 52.4 | 29.51 | -40.29 | 0 | 0 | 0 | Battery-supported
2025-11-12 20:00 | 316 | 11 | Spring | 20 | 21.57 | -3.7 | 5.26 | 60.4 | 141.6 | 8.5 | 0.76 | 9.26 | 3.7 | 51.78 | 15 | -36.27 | 6.25 | 2.311 | 0 | Diesel-backup
2025-11-12 21:00 | 316 | 11 | Spring | 21 | 21.57 | -4.1 | 3.53 | 92.2 | 52 | 3.12 | 0 | 3.12 | 4.1 | 45 | 15 | 0 | 41.88 | 13.569 | 0 | Diesel-backup
2025-11-12 22:00 | 316 | 11 | Spring | 22 | 21.57 | -4.8 | 30.81 | 27.7 | 59.4 | 3.56 | 0 | 3.56 | 4.8 | 45 | 15 | 0 | 41.44 | 13.45 | 0 | Diesel-backup
2025-11-12 23:00 | 316 | 11 | Spring | 23 | 21.57 | -10.4 | 4.7 | 36.4 | 0 | 0 | 0.24 | 0.24 | 10.4 | 46.16 | 15 | 0 | 45.92 | 14.694 | 0 | Diesel-backup
2025-11-13 | 317 | 11 | Spring | 0 | 21.94 | -4.2 | 2.17 | 96.3 | 0 | 0 | 0 | 0 | 4.2 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-11-13 01:00 | 317 | 11 | Spring | 1 | 21.94 | -8 | 11.54 | 36.9 | 0 | 0 | 72.74 | 72.74 | 8 | 45 | 25.21 | 27.74 | 0 | 0 | 0 | Normal
2025-11-13 02:00 | 317 | 11 | Spring | 2 | 21.94 | -5.8 | 1.76 | 27 | 72.3 | 4.34 | 0 | 4.34 | 5.8 | 45 | 15 | -25.52 | 15.14 | 5.423 | 0 | Diesel-backup
2025-11-13 03:00 | 317 | 11 | Spring | 3 | 21.94 | -9.9 | 7.07 | 22.3 | 152 | 9.12 | 6.37 | 15.49 | 9.9 | 45 | 15 | 0 | 29.51 | 10.028 | 0 | Diesel-backup
2025-11-13 04:00 | 317 | 11 | Spring | 4 | 21.94 | -10.7 | 12.54 | 52 | 165 | 9.9 | 103.4 | 113.3 | 10.7 | 45 | 40.13 | 68.3 | 0 | 0 | 0 | Normal
2025-11-13 05:00 | 317 | 11 | Spring | 5 | 21.94 | -4.1 | 3.21 | 77.1 | 148.9 | 8.93 | 0 | 8.93 | 4.1 | 45 | 25.71 | -36.07 | 0 | 0 | 0 | Battery-supported
2025-11-13 06:00 | 317 | 11 | Spring | 6 | 21.94 | -10.8 | 7.8 | 50.1 | 267.5 | 16.05 | 11.13 | 27.18 | 10.8 | 45 | 18.58 | -17.82 | 0 | 0 | 0 | Battery-supported
2025-11-13 07:00 | 317 | 11 | Spring | 7 | 21.94 | -6.3 | 6.43 | 62.2 | 263.8 | 15.83 | 3.52 | 19.35 | 6.3 | 45 | 15 | -8.95 | 16.7 | 5.95 | 0 | Diesel-backup
2025-11-13 08:00 | 317 | 11 | Spring | 8 | 21.94 | -8.6 | 4.63 | 17.6 | 478.5 | 28.71 | 0.2 | 28.91 | 8.6 | 48.87 | 15 | 0 | 19.96 | 7.027 | 0 | Diesel-backup
2025-11-13 09:00 | 317 | 11 | Spring | 9 | 21.94 | -9.8 | 16.1 | 45.7 | 392.2 | 23.53 | 120 | 143.53 | 9.8 | 49.79 | 49.5 | 93.74 | 0 | 0 | 0 | Normal
2025-11-13 10:00 | 317 | 11 | Spring | 10 | 21.94 | -8.8 | 6.4 | 78.1 | 260.4 | 15.62 | 3.41 | 19.03 | 8.8 | 47.17 | 38.24 | -28.14 | 0 | 0 | 0 | Battery-supported
2025-11-13 11:00 | 317 | 11 | Spring | 11 | 21.94 | -11.3 | 11.4 | 6.2 | 619.2 | 37.15 | 69.01 | 106.16 | 11.3 | 52.05 | 58.15 | 54.11 | 0 | 0 | 0 | Normal
2025-11-13 12:00 | 317 | 11 | Spring | 12 | 21.94 | -8.2 | 13.14 | 64.1 | 340.4 | 20.42 | 120 | 140.42 | 8.2 | 46.81 | 92.6 | 93.61 | 0 | 0 | 0 | Normal
2025-11-13 13:00 | 317 | 11 | Spring | 13 | 21.94 | -10.2 | 6.88 | 29.4 | 506.1 | 30.37 | 5.4 | 35.77 | 10.2 | 53.57 | 85.48 | -17.8 | 0 | 0 | 0 | Battery-supported
2025-11-13 14:00 | 317 | 11 | Spring | 14 | 21.94 | -8.3 | 3.93 | 86.9 | 219.1 | 13.15 | 0.01 | 13.16 | 8.3 | 54.25 | 69.05 | -41.09 | 0 | 0 | 0 | Battery-supported
2025-11-13 15:00 | 317 | 11 | Spring | 15 | 21.94 | -5 | 13.32 | 43.2 | 403.3 | 24.2 | 120 | 144.2 | 5 | 46.04 | 95 | 70.53 | 0 | 0 | 0 | Normal
2025-11-13 16:00 | 317 | 11 | Spring | 16 | 21.94 | -6.1 | 7.08 | 99.1 | 141.3 | 8.48 | 6.42 | 14.9 | 6.1 | 53.45 | 79.58 | -38.55 | 0 | 0 | 0 | Battery-supported
2025-11-13 17:00 | 317 | 11 | Spring | 17 | 21.94 | -9.6 | 7.55 | 64.8 | 254.3 | 15.26 | 9.3 | 24.56 | 9.6 | 49.49 | 69.61 | -24.93 | 0 | 0 | 0 | Battery-supported
2025-11-13 18:00 | 317 | 11 | Spring | 18 | 21.94 | -4.2 | 6.15 | 71.9 | 197.4 | 11.84 | 2.6 | 14.44 | 4.2 | 45 | 57.38 | -30.56 | 0 | 0 | 0 | Battery-supported
2025-11-13 19:00 | 317 | 11 | Spring | 19 | 21.94 | -6 | 13.05 | 52.9 | 213.1 | 12.79 | 120 | 132.79 | 6 | 54.45 | 86.21 | 78.34 | 0 | 0 | 0 | Normal
2025-11-13 20:00 | 317 | 11 | Spring | 20 | 21.94 | -7.1 | 3.61 | 46.4 | 176.3 | 10.58 | 0 | 10.58 | 7.1 | 45 | 72.45 | -34.42 | 0 | 0 | 0 | Battery-supported
2025-11-13 21:00 | 317 | 11 | Spring | 21 | 21.94 | -4.3 | 7.61 | 83.6 | 68.1 | 4.09 | 9.72 | 13.81 | 4.3 | 45 | 59.97 | -31.19 | 0 | 0 | 0 | Battery-supported
2025-11-13 22:00 | 317 | 11 | Spring | 22 | 21.94 | -6.5 | 3.99 | 21.2 | 76.3 | 4.58 | 0.02 | 4.6 | 6.5 | 45 | 43.81 | -40.4 | 0 | 0 | 0 | Battery-supported
2025-11-13 23:00 | 317 | 11 | Spring | 23 | 21.94 | -8.9 | 6.14 | 68.1 | 0 | 0 | 2.58 | 2.58 | 8.9 | 48.86 | 25.3 | -46.28 | 0 | 0 | 0 | Battery-supported
2025-11-14 | 318 | 11 | Spring | 0 | 22.37 | -2.4 | 14.01 | 6.4 | 0 | 0 | 120 | 120 | 2.4 | 45 | 52.9 | 75 | 0 | 0 | 0 | Normal
2025-11-14 01:00 | 318 | 11 | Spring | 1 | 22.37 | -6.9 | 13.91 | 29.9 | 13.2 | 0.79 | 120 | 120.79 | 6.9 | 45 | 80.79 | 75.79 | 0 | 0 | 0 | Normal
2025-11-14 02:00 | 318 | 11 | Spring | 2 | 22.37 | -7.4 | 6.7 | 30.5 | 83.8 | 5.03 | 4.59 | 9.62 | 7.4 | 50.8 | 64.32 | -41.18 | 0 | 0 | 0 | Battery-supported
2025-11-14 03:00 | 318 | 11 | Spring | 3 | 22.37 | -8.5 | 9.16 | 61.9 | 106.2 | 6.37 | 25.38 | 31.75 | 8.5 | 47.18 | 58.14 | -15.43 | 0 | 0 | 0 | Battery-supported
2025-11-14 04:00 | 318 | 11 | Spring | 4 | 22.37 | -5.4 | 9.06 | 21.2 | 238.6 | 14.32 | 24.06 | 38.38 | 5.4 | 45 | 55.5 | -6.62 | 0 | 0 | 0 | Battery-supported
2025-11-14 05:00 | 318 | 11 | Spring | 5 | 22.37 | -9.4 | 3.99 | 41.4 | 250.6 | 15.04 | 0.02 | 15.06 | 9.4 | 46.3 | 43 | -31.24 | 0 | 0 | 0 | Battery-supported
2025-11-14 06:00 | 318 | 11 | Spring | 6 | 22.37 | -11.9 | 10.52 | 63.4 | 228.9 | 13.73 | 48.42 | 62.15 | 11.9 | 49.32 | 47.72 | 12.83 | 0 | 0 | 0 | Normal
2025-11-14 07:00 | 318 | 11 | Spring | 7 | 22.37 | -10.2 | 4.27 | 68.7 | 242.6 | 14.56 | 0.06 | 14.62 | 10.2 | 46.23 | 35.08 | -31.61 | 0 | 0 | 0 | Battery-supported
2025-11-14 08:00 | 318 | 11 | Spring | 8 | 22.37 | -5.8 | 5.89 | 25.9 | 447.4 | 26.84 | 1.91 | 28.75 | 5.8 | 48.27 | 27.27 | -19.52 | 0 | 0 | 0 | Battery-supported
2025-11-14 09:00 | 318 | 11 | Spring | 9 | 22.37 | -6.8 | 2.24 | 61.5 | 322.7 | 19.36 | 0 | 19.36 | 6.8 | 45 | 17.01 | -25.64 | 0 | 0 | 0 | Battery-supported
2025-11-14 10:00 | 318 | 11 | Spring | 10 | 22.37 | -9.1 | 11.56 | 59.9 | 347 | 20.82 | 73.29 | 94.11 | 9.1 | 46.74 | 34.45 | 47.37 | 0 | 0 | 0 | Normal
2025-11-14 11:00 | 318 | 11 | Spring | 11 | 22.37 | -5.2 | 13.04 | 80.7 | 256.4 | 15.38 | 120 | 135.38 | 5.2 | 50.91 | 65.53 | 84.47 | 0 | 0 | 0 | Normal
2025-11-14 12:00 | 318 | 11 | Spring | 12 | 22.37 | -6.3 | 9.36 | 34.9 | 484.3 | 29.06 | 28.16 | 57.22 | 6.3 | 54.1 | 66.68 | 3.12 | 0 | 0 | 0 | Normal
2025-11-14 13:00 | 318 | 11 | Spring | 13 | 22.37 | -8.2 | 7.8 | 74.9 | 284.6 | 17.08 | 11.13 | 28.21 | 8.2 | 51.92 | 57.19 | -23.71 | 0 | 0 | 0 | Battery-supported
2025-11-14 14:00 | 318 | 11 | Spring | 14 | 22.37 | -7.6 | 5.7 | 32.3 | 477.8 | 28.67 | 1.49 | 30.16 | 7.6 | 46.19 | 50.78 | -16.03 | 0 | 0 | 0 | Battery-supported
2025-11-14 15:00 | 318 | 11 | Spring | 15 | 22.37 | -6.1 | 11.73 | 73.9 | 266.6 | 16 | 78.02 | 94.02 | 6.1 | 49.9 | 67.02 | 44.12 | 0 | 0 | 0 | Normal
2025-11-14 16:00 | 318 | 11 | Spring | 16 | 22.37 | -8.3 | 18.2 | 20.2 | 471.1 | 28.27 | 120 | 148.27 | 8.3 | 52.81 | 95 | 76.04 | 0 | 0 | 0 | Normal
2025-11-14 17:00 | 318 | 11 | Spring | 17 | 22.37 | -6.1 | 4.66 | 18.5 | 431.3 | 25.88 | 0.22 | 26.1 | 6.1 | 45 | 87.44 | -18.9 | 0 | 0 | 0 | Battery-supported
2025-11-14 18:00 | 318 | 11 | Spring | 18 | 22.37 | -5.2 | 6.8 | 14.3 | 389.6 | 23.38 | 5.03 | 28.41 | 5.2 | 54.2 | 77.12 | -25.79 | 0 | 0 | 0 | Battery-supported
2025-11-14 19:00 | 318 | 11 | Spring | 19 | 22.37 | -9.5 | 3.83 | 53.3 | 218.3 | 13.1 | 0.01 | 13.11 | 9.5 | 55.94 | 59.99 | -42.83 | 0 | 0 | 0 | Battery-supported
2025-11-14 20:00 | 318 | 11 | Spring | 20 | 22.37 | -6.1 | 7.82 | 2.7 | 277.9 | 16.67 | 11.28 | 27.95 | 6.1 | 45 | 53.17 | -17.05 | 0 | 0 | 0 | Battery-supported
2025-11-14 21:00 | 318 | 11 | Spring | 21 | 22.37 | -6.4 | 6.07 | 19.4 | 169.3 | 10.16 | 2.38 | 12.54 | 6.4 | 45 | 40.19 | -32.46 | 0 | 0 | 0 | Battery-supported
2025-11-14 22:00 | 318 | 11 | Spring | 22 | 22.37 | -3.6 | 7.1 | 47.6 | 69.8 | 4.19 | 6.53 | 10.72 | 3.6 | 45 | 26.48 | -34.28 | 0 | 0 | 0 | Battery-supported
2025-11-14 23:00 | 318 | 11 | Spring | 23 | 22.37 | -10.2 | 11.82 | 66.7 | 8.5 | 0.51 | 80.61 | 81.12 | 10.2 | 50.35 | 37.8 | 30.77 | 0 | 0 | 0 | Normal
2025-11-15 | 319 | 11 | Spring | 0 | 22.95 | -7.1 | 13.68 | 91.3 | 0 | 0 | 120 | 120 | 7.1 | 45 | 65.4 | 75 | 0 | 0 | 0 | Normal
2025-11-15 01:00 | 319 | 11 | Spring | 1 | 22.95 | -7.7 | 3.43 | 33.4 | 31.9 | 1.91 | 0 | 1.91 | 7.7 | 45 | 48.16 | -43.09 | 0 | 0 | 0 | Battery-supported
2025-11-15 02:00 | 319 | 11 | Spring | 2 | 22.95 | -4.9 | 8.97 | 61.8 | 70.6 | 4.24 | 22.91 | 27.15 | 4.9 | 45 | 41.02 | -17.85 | 0 | 0 | 0 | Battery-supported
2025-11-15 03:00 | 319 | 11 | Spring | 3 | 22.95 | -7.5 | 16.02 | 65.7 | 110.5 | 6.63 | 120 | 126.63 | 7.5 | 45 | 71.06 | 81.63 | 0 | 0 | 0 | Normal
2025-11-15 04:00 | 319 | 11 | Spring | 4 | 22.95 | -3.8 | 10.12 | 40.3 | 209.5 | 12.57 | 40.61 | 53.18 | 3.8 | 45 | 74.07 | 8.18 | 0 | 0 | 0 | Normal
2025-11-15 05:00 | 319 | 11 | Spring | 5 | 22.95 | -6.6 | 4.03 | 40.2 | 263.4 | 15.8 | 0.02 | 15.82 | 6.6 | 45 | 62.4 | -29.18 | 0 | 0 | 0 | Battery-supported
2025-11-15 06:00 | 319 | 11 | Spring | 6 | 22.95 | -9.2 | 13.34 | 22.5 | 371.3 | 22.28 | 120 | 142.28 | 9.2 | 45 | 95 | 88.58 | 0 | 0 | 0 | Normal
2025-11-15 07:00 | 319 | 11 | Spring | 7 | 22.95 | -8 | 10.53 | 39.3 | 358.3 | 21.5 | 48.63 | 70.13 | 8 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-11-15 08:00 | 319 | 11 | Spring | 8 | 22.95 | -9.3 | 9.94 | 41.7 | 384.8 | 23.09 | 37.38 | 60.47 | 9.3 | 50.41 | 95 | 0 | 0 | 0 | 0 | Normal
2025-11-15 09:00 | 319 | 11 | Spring | 9 | 22.95 | -6.6 | 6.66 | 48 | 384.7 | 23.08 | 4.42 | 27.5 | 6.6 | 48.3 | 86.68 | -20.8 | 0 | 0 | 0 | Battery-supported
2025-11-15 10:00 | 319 | 11 | Spring | 10 | 22.95 | -11.3 | 9.6 | 84.4 | 231.6 | 13.9 | 31.77 | 45.67 | 11.3 | 47.68 | 85.88 | -2.01 | 0 | 0 | 0 | Battery-supported
2025-11-15 11:00 | 319 | 11 | Spring | 11 | 22.95 | -9.9 | 29.47 | 16.7 | 568.3 | 34.1 | 0 | 34.1 | 9.9 | 48.18 | 80.24 | -14.08 | 0 | 0 | 0 | Battery-supported
2025-11-15 12:00 | 319 | 11 | Spring | 12 | 22.95 | -6.8 | 1.95 | 34.9 | 484.3 | 29.06 | 0 | 29.06 | 6.8 | 50.81 | 71.54 | -21.75 | 0 | 0 | 0 | Battery-supported
2025-11-15 13:00 | 319 | 11 | Spring | 13 | 22.95 | -4.7 | 5.83 | 46.5 | 423 | 25.38 | 1.77 | 27.15 | 4.7 | 52.75 | 61.3 | -25.6 | 0 | 0 | 0 | Battery-supported
2025-11-15 14:00 | 319 | 11 | Spring | 14 | 22.95 | -11.9 | 6.19 | 68.8 | 305.5 | 18.33 | 2.72 | 21.05 | 11.9 | 52.76 | 48.62 | -31.71 | 0 | 0 | 0 | Battery-supported
2025-11-15 15:00 | 319 | 11 | Spring | 15 | 22.95 | -3.6 | 1.08 | 51.5 | 369.1 | 22.15 | 0 | 22.15 | 3.6 | 46.9 | 38.72 | -24.75 | 0 | 0 | 0 | Battery-supported
2025-11-15 16:00 | 319 | 11 | Spring | 16 | 22.95 | -6.6 | 21.97 | 94.8 | 162 | 9.72 | 120 | 129.72 | 6.6 | 58.86 | 64.8 | 70.86 | 0 | 0 | 0 | Normal
2025-11-15 17:00 | 319 | 11 | Spring | 17 | 22.95 | -10.1 | 3.82 | 75.7 | 219.8 | 13.19 | 0 | 13.19 | 10.1 | 53.99 | 48.48 | -40.8 | 0 | 0 | 0 | Battery-supported
2025-11-15 18:00 | 319 | 11 | Spring | 18 | 22.95 | -12.3 | 3.66 | 56.5 | 257.5 | 15.45 | 0 | 15.45 | 12.3 | 47.43 | 35.68 | -31.98 | 0 | 0 | 0 | Battery-supported
2025-11-15 19:00 | 319 | 11 | Spring | 19 | 22.95 | -8.9 | 2.63 | 69.3 | 181.3 | 10.88 | 0 | 10.88 | 8.9 | 54.07 | 18.41 | -43.19 | 0 | 0 | 0 | Battery-supported
2025-11-15 20:00 | 319 | 11 | Spring | 20 | 22.95 | -5.6 | 5.79 | 31.2 | 230.1 | 13.81 | 1.68 | 15.49 | 5.6 | 49.38 | 15 | -8.52 | 25.37 | 8.755 | 0 | Diesel-backup
2025-11-15 21:00 | 319 | 11 | Spring | 21 | 22.95 | -5.7 | 9.92 | 23.6 | 179.3 | 10.76 | 37.04 | 47.8 | 5.7 | 45 | 16.03 | 2.8 | 0 | 0 | 0 | Normal
2025-11-15 22:00 | 319 | 11 | Spring | 22 | 22.95 | -4.3 | 7.44 | 11.7 | 119.9 | 7.19 | 8.56 | 15.75 | 4.3 | 45 | 15 | -2.58 | 26.67 | 9.161 | 0 | Diesel-backup
2025-11-15 23:00 | 319 | 11 | Spring | 23 | 22.95 | -7.2 | 4.19 | 61.5 | 22.9 | 1.37 | 0.05 | 1.42 | 7.2 | 45.4 | 15 | 0 | 43.98 | 14.131 | 0 | Diesel-backup
2025-11-16 | 320 | 11 | Spring | 0 | 24 | -8.5 | 9.57 | 52.4 | 0 | 0 | 31.3 | 31.3 | 8.5 | 45 | 15 | 0 | 13.7 | 4.933 | 0 | Diesel-backup
2025-11-16 01:00 | 320 | 11 | Spring | 1 | 24 | -7.4 | 7.47 | 74.3 | 37.9 | 2.27 | 8.76 | 11.03 | 7.4 | 45 | 15 | 0 | 33.97 | 11.35 | 0 | Diesel-backup
2025-11-16 02:00 | 320 | 11 | Spring | 2 | 24 | -6.8 | 14.92 | 60.4 | 92.9 | 5.57 | 120 | 125.57 | 6.8 | 45 | 44.65 | 80.57 | 0 | 0 | 0 | Normal
2025-11-16 03:00 | 320 | 11 | Spring | 3 | 24 | -6.7 | 5 | 66.7 | 125.5 | 7.53 | 0.47 | 8 | 6.7 | 45 | 29.85 | -37 | 0 | 0 | 0 | Battery-supported
2025-11-16 04:00 | 320 | 11 | Spring | 4 | 24 | -9.3 | 4.7 | 63.3 | 172.2 | 10.33 | 0.24 | 10.57 | 9.3 | 45 | 16.08 | -34.43 | 0 | 0 | 0 | Battery-supported
2025-11-16 05:00 | 320 | 11 | Spring | 5 | 24 | -5.9 | 12.06 | 10.4 | 368.2 | 22.09 | 87.79 | 109.88 | 5.9 | 45 | 39.95 | 64.88 | 0 | 0 | 0 | Normal
2025-11-16 06:00 | 320 | 11 | Spring | 6 | 24 | -9.5 | 3.71 | 30.4 | 358.2 | 21.49 | 0 | 21.49 | 9.5 | 46.64 | 29.89 | -25.15 | 0 | 0 | 0 | Battery-supported
2025-11-16 07:00 | 320 | 11 | Spring | 7 | 24 | -10.2 | 2.56 | 26.3 | 417.6 | 25.06 | 0 | 25.06 | 10.2 | 56.81 | 17.19 | -31.75 | 0 | 0 | 0 | Battery-supported
2025-11-16 08:00 | 320 | 11 | Spring | 8 | 24 | -9.5 | 7.33 | 61.1 | 307.8 | 18.47 | 7.86 | 26.33 | 9.5 | 48.81 | 15 | -5.48 | 17 | 6.048 | 0 | Diesel-backup
2025-11-16 09:00 | 320 | 11 | Spring | 9 | 24 | -5.9 | 10.07 | 53.4 | 363.4 | 21.8 | 39.69 | 61.49 | 5.9 | 50.49 | 19.05 | 11 | 0 | 0 | 0 | Normal
2025-11-16 10:00 | 320 | 11 | Spring | 10 | 24 | -8.4 | 2.42 | 34.3 | 470.6 | 28.24 | 0 | 28.24 | 8.4 | 51.98 | 15 | -10.12 | 13.62 | 4.905 | 0 | Diesel-backup
2025-11-16 11:00 | 320 | 11 | Spring | 11 | 24 | -9.4 | 12.81 | 71.6 | 300.9 | 18.05 | 112.94 | 130.99 | 9.4 | 53.18 | 43.63 | 77.81 | 0 | 0 | 0 | Normal
2025-11-16 12:00 | 320 | 11 | Spring | 12 | 24 | -5.6 | 2.24 | 88.6 | 219.9 | 13.19 | 0 | 13.19 | 5.6 | 46.7 | 30.23 | -33.51 | 0 | 0 | 0 | Battery-supported
2025-11-16 13:00 | 320 | 11 | Spring | 13 | 24 | -2.5 | 5.17 | 27.2 | 517.9 | 31.07 | 0.65 | 31.72 | 2.5 | 45.51 | 24.71 | -13.79 | 0 | 0 | 0 | Battery-supported
2025-11-16 14:00 | 320 | 11 | Spring | 14 | 24 | -6.4 | 7.45 | 70 | 300.8 | 18.05 | 8.63 | 26.68 | 6.4 | 50.22 | 15.3 | -23.54 | 0 | 0 | 0 | Battery-supported
2025-11-16 15:00 | 320 | 11 | Spring | 15 | 24 | -3.7 | 15.73 | 62.4 | 322.2 | 19.33 | 120 | 139.33 | 3.7 | 49.89 | 48.21 | 89.44 | 0 | 0 | 0 | Normal
2025-11-16 16:00 | 320 | 11 | Spring | 16 | 24 | -3.8 | 16.28 | 68 | 278.4 | 16.7 | 120 | 136.7 | 3.8 | 49.71 | 80.22 | 86.99 | 0 | 0 | 0 | Normal
2025-11-16 17:00 | 320 | 11 | Spring | 17 | 24 | -7.1 | 8.31 | 60 | 286.1 | 17.17 | 15.58 | 32.75 | 7.1 | 55.22 | 71.24 | -22.47 | 0 | 0 | 0 | Battery-supported
2025-11-16 18:00 | 320 | 11 | Spring | 18 | 24 | -5.5 | 5.73 | 26 | 373.2 | 22.39 | 1.55 | 23.94 | 5.5 | 45.54 | 62.6 | -21.6 | 0 | 0 | 0 | Battery-supported
2025-11-16 19:00 | 320 | 11 | Spring | 19 | 24 | -8.2 | 5.95 | 55.5 | 233.1 | 13.99 | 2.06 | 16.05 | 8.2 | 51.92 | 48.25 | -35.87 | 0 | 0 | 0 | Battery-supported
2025-11-16 20:00 | 320 | 11 | Spring | 20 | 24 | -5.8 | 20.69 | 78.4 | 135 | 8.1 | 120 | 128.1 | 5.8 | 48.17 | 77.66 | 79.93 | 0 | 0 | 0 | Normal
2025-11-16 21:00 | 320 | 11 | Spring | 21 | 24 | -6.8 | 14.24 | 32.2 | 190.3 | 11.42 | 120 | 131.42 | 6.8 | 45.21 | 95 | 47.11 | 0 | 0 | 0 | Normal
2025-11-16 22:00 | 320 | 11 | Spring | 22 | 24 | -6.4 | 9.33 | 42.6 | 115.5 | 6.93 | 27.73 | 34.66 | 6.4 | 45 | 90.86 | -10.34 | 0 | 0 | 0 | Battery-supported
2025-11-16 23:00 | 320 | 11 | Spring | 23 | 24 | -7.4 | 8.46 | 90.6 | 27.4 | 1.64 | 17.08 | 18.72 | 7.4 | 46.77 | 79.64 | -28.05 | 0 | 0 | 0 | Battery-supported
2025-11-17 | 321 | 11 | Spring | 0 | 24 | -6.6 | 7.98 | 52.4 | 0 | 0 | 12.58 | 12.58 | 6.6 | 45 | 66.68 | -32.42 | 0 | 0 | 0 | Battery-supported
2025-11-17 01:00 | 321 | 11 | Spring | 1 | 24 | -5.1 | 1.87 | 78 | 35.6 | 2.14 | 0 | 2.14 | 5.1 | 45 | 49.53 | -42.86 | 0 | 0 | 0 | Battery-supported
2025-11-17 02:00 | 321 | 11 | Spring | 2 | 24 | -6.9 | 0.74 | 66.1 | 85.6 | 5.14 | 0 | 5.14 | 6.9 | 45 | 33.59 | -39.86 | 0 | 0 | 0 | Battery-supported
2025-11-17 03:00 | 321 | 11 | Spring | 3 | 24 | -11.2 | 6.48 | 63.3 | 131.8 | 7.91 | 3.7 | 11.61 | 11.2 | 45.47 | 20.04 | -33.86 | 0 | 0 | 0 | Battery-supported
2025-11-17 04:00 | 321 | 11 | Spring | 4 | 24 | -9.1 | 3.39 | 75.8 | 141.5 | 8.49 | 0 | 8.49 | 9.1 | 45 | 15 | -12.61 | 23.9 | 8.293 | 0 | Diesel-backup
2025-11-17 05:00 | 321 | 11 | Spring | 5 | 24 | -11.1 | 8.49 | 38.5 | 284 | 17.04 | 17.39 | 34.43 | 11.1 | 45 | 15 | 0 | 10.57 | 3.848 | 0 | Diesel-backup
2025-11-17 06:00 | 321 | 11 | Spring | 6 | 24 | -7.4 | 8.12 | 83.4 | 173.9 | 10.43 | 13.8 | 24.23 | 7.4 | 45 | 15 | 0 | 20.77 | 7.291 | 0 | Diesel-backup
2025-11-17 07:00 | 321 | 11 | Spring | 7 | 24 | -7 | 2.51 | 87.9 | 177.2 | 10.63 | 0 | 10.63 | 7 | 45 | 15 | 0 | 34.37 | 11.466 | 0 | Diesel-backup
2025-11-17 08:00 | 321 | 11 | Spring | 8 | 24 | -7.6 | 8.6 | 80.4 | 225.4 | 13.52 | 18.57 | 32.09 | 7.6 | 48.48 | 15 | 0 | 16.39 | 5.845 | 0 | Diesel-backup
2025-11-17 09:00 | 321 | 11 | Spring | 9 | 24 | -9.9 | 8.89 | 47.3 | 390.8 | 23.45 | 21.92 | 45.37 | 9.9 | 53.26 | 15 | 0 | 7.89 | 2.9 | 0 | Diesel-backup
2025-11-17 10:00 | 321 | 11 | Spring | 10 | 24 | -7.4 | 8.74 | 65.4 | 322.8 | 19.37 | 20.14 | 39.51 | 7.4 | 47.58 | 15 | 0 | 8.07 | 2.964 | 0 | Diesel-backup
2025-11-17 11:00 | 321 | 11 | Spring | 11 | 24 | -8.8 | 5.02 | 81.6 | 252.5 | 15.15 | 0.49 | 15.64 | 8.8 | 53.19 | 15 | 0 | 37.55 | 12.374 | 0 | Diesel-backup
2025-11-17 12:00 | 321 | 11 | Spring | 12 | 24 | -9.9 | 9.76 | 5.5 | 629 | 37.74 | 34.33 | 72.07 | 9.9 | 52.35 | 22.26 | 19.72 | 0 | 0 | 0 | Normal
2025-11-17 13:00 | 321 | 11 | Spring | 13 | 24 | -5.4 | 10.13 | 61.9 | 348.3 | 20.9 | 40.79 | 61.69 | 5.4 | 45 | 28.4 | 16.69 | 0 | 0 | 0 | Normal
2025-11-17 14:00 | 321 | 11 | Spring | 14 | 24 | -4.9 | 9.71 | 58.8 | 354.2 | 21.25 | 33.52 | 54.77 | 4.9 | 48.07 | 30.86 | 6.7 | 0 | 0 | 0 | Normal
2025-11-17 15:00 | 321 | 11 | Spring | 15 | 24 | -4.2 | 6.29 | 54 | 360.4 | 21.62 | 3.04 | 24.66 | 4.2 | 50.47 | 20.54 | -25.81 | 0 | 0 | 0 | Battery-supported
2025-11-17 16:00 | 321 | 11 | Spring | 16 | 24 | -7.3 | 16.88 | 38.4 | 404.4 | 24.26 | 120 | 144.26 | 7.3 | 53.87 | 53.8 | 90.39 | 0 | 0 | 0 | Normal
2025-11-17 17:00 | 321 | 11 | Spring | 17 | 24 | -3 | 14.93 | 54.5 | 307.7 | 18.46 | 120 | 138.46 | 3 | 45 | 88.2 | 93.46 | 0 | 0 | 0 | Normal
2025-11-17 18:00 | 321 | 11 | Spring | 18 | 24 | -6.5 | 7.72 | 47 | 300.3 | 18.02 | 10.52 | 28.54 | 6.5 | 45 | 81.61 | -16.46 | 0 | 0 | 0 | Battery-supported
2025-11-17 19:00 | 321 | 11 | Spring | 19 | 24 | -3.8 | 4.73 | 57.5 | 227 | 13.62 | 0.26 | 13.88 | 3.8 | 51.15 | 66.71 | -37.27 | 0 | 0 | 0 | Battery-supported
2025-11-17 20:00 | 321 | 11 | Spring | 20 | 24 | -6.3 | 4.37 | 75.6 | 141.9 | 8.51 | 0.09 | 8.6 | 6.3 | 50.94 | 49.77 | -42.34 | 0 | 0 | 0 | Battery-supported
2025-11-17 21:00 | 321 | 11 | Spring | 21 | 24 | -5.7 | 10.26 | 61.9 | 134.4 | 8.06 | 43.24 | 51.3 | 5.7 | 45 | 52.09 | 6.3 | 0 | 0 | 0 | Normal
2025-11-17 22:00 | 321 | 11 | Spring | 22 | 24 | -10.7 | 3.05 | 34.1 | 126.3 | 7.58 | 0 | 7.58 | 10.7 | 45 | 37.12 | -37.42 | 0 | 0 | 0 | Battery-supported
2025-11-17 23:00 | 321 | 11 | Spring | 23 | 24 | -6.3 | 10.68 | 42.1 | 58.6 | 3.52 | 51.81 | 55.33 | 6.3 | 45 | 40.92 | 10.33 | 0 | 0 | 0 | Normal
2025-11-18 | 322 | 11 | Spring | 0 | 24 | -5.6 | 2.73 | 79.7 | 0 | 0 | 0 | 0 | 5.6 | 45 | 22.92 | -45 | 0 | 0 | 0 | Battery-supported
2025-11-18 01:00 | 322 | 11 | Spring | 1 | 24 | -7 | 6.95 | 37.1 | 61.8 | 3.71 | 5.75 | 9.46 | 7 | 45 | 15 | -19.8 | 15.74 | 5.625 | 0 | Diesel-backup
2025-11-18 02:00 | 322 | 11 | Spring | 2 | 24 | -2.6 | 10.18 | 67.6 | 83.7 | 5.02 | 41.72 | 46.74 | 2.6 | 45 | 15.64 | 1.74 | 0 | 0 | 0 | Normal
2025-11-18 03:00 | 322 | 11 | Spring | 3 | 24 | -9.4 | 4.49 | 41.3 | 173.2 | 10.39 | 0.14 | 10.53 | 9.4 | 45 | 15 | -1.6 | 32.87 | 11.029 | 0 | Diesel-backup
2025-11-18 04:00 | 322 | 11 | Spring | 4 | 24 | -8.5 | 12.59 | 69.8 | 156.2 | 9.37 | 105.12 | 114.49 | 8.5 | 45 | 40.57 | 69.49 | 0 | 0 | 0 | Normal
2025-11-18 05:00 | 322 | 11 | Spring | 5 | 24 | -9.6 | 5.81 | 60 | 219.5 | 13.17 | 1.73 | 14.9 | 9.6 | 45 | 28.53 | -30.1 | 0 | 0 | 0 | Battery-supported
2025-11-18 06:00 | 322 | 11 | Spring | 6 | 24 | -9 | 7.35 | 17.9 | 401.4 | 24.08 | 7.99 | 32.07 | 9 | 45 | 23.36 | -12.93 | 0 | 0 | 0 | Battery-supported
2025-11-18 07:00 | 322 | 11 | Spring | 7 | 24 | -5.7 | 1.59 | 47.1 | 336.6 | 20.2 | 0 | 20.2 | 5.7 | 46.33 | 15 | -20.9 | 5.23 | 1.94 | 0 | Diesel-backup
2025-11-18 08:00 | 322 | 11 | Spring | 8 | 24 | -4.7 | 2.68 | 27.6 | 450.3 | 27.02 | 0 | 27.02 | 4.7 | 45 | 15 | 0 | 17.98 | 6.375 | 0 | Diesel-backup
2025-11-18 09:00 | 322 | 11 | Spring | 9 | 24 | -9.5 | 1.7 | 32.9 | 456.5 | 27.39 | 0 | 27.39 | 9.5 | 49.52 | 15 | 0 | 22.13 | 7.729 | 0 | Diesel-backup
2025-11-18 10:00 | 322 | 11 | Spring | 10 | 24 | -9.4 | 11.28 | 15.3 | 561 | 33.66 | 65.91 | 99.57 | 9.4 | 60.97 | 29.2 | 38.6 | 0 | 0 | 0 | Normal
2025-11-18 11:00 | 322 | 11 | Spring | 11 | 24 | -10.1 | 5.64 | 59.3 | 361.3 | 21.68 | 1.37 | 23.05 | 10.1 | 49.87 | 18.48 | -26.82 | 0 | 0 | 0 | Battery-supported
2025-11-18 12:00 | 322 | 11 | Spring | 12 | 24 | -4.4 | 13.31 | 73.3 | 295.3 | 17.72 | 120 | 137.72 | 4.4 | 47.32 | 51.74 | 90.4 | 0 | 0 | 0 | Normal
2025-11-18 13:00 | 322 | 11 | Spring | 13 | 24 | -4.4 | 1.2 | 67.5 | 321.3 | 19.28 | 0 | 19.28 | 4.4 | 53.04 | 38.24 | -33.76 | 0 | 0 | 0 | Battery-supported
2025-11-18 14:00 | 322 | 11 | Spring | 14 | 24 | -6.7 | 9.47 | 52.4 | 384.8 | 23.09 | 29.78 | 52.87 | 6.7 | 49.22 | 39.58 | 3.65 | 0 | 0 | 0 | Normal
2025-11-18 15:00 | 322 | 11 | Spring | 15 | 24 | -9.2 | 1.58 | 55.6 | 353.4 | 21.2 | 0 | 21.2 | 9.2 | 53.74 | 26.57 | -32.54 | 0 | 0 | 0 | Battery-supported
2025-11-18 16:00 | 322 | 11 | Spring | 16 | 24 | -8.6 | 4.14 | 71.9 | 261.6 | 15.7 | 0.04 | 15.74 | 8.6 | 48.91 | 15 | -28.92 | 4.25 | 1.582 | 0 | Diesel-backup
2025-11-18 17:00 | 322 | 11 | Spring | 17 | 24 | -5.1 | 6.87 | 57.3 | 296.9 | 17.81 | 5.36 | 23.17 | 5.1 | 45 | 15 | 0 | 21.83 | 7.633 | 0 | Diesel-backup
2025-11-18 18:00 | 322 | 11 | Spring | 18 | 24 | -4 | 5.53 | 63.3 | 243.6 | 14.62 | 1.17 | 15.79 | 4 | 45 | 15 | 0 | 29.21 | 9.938 | 0 | Diesel-backup
2025-11-18 19:00 | 322 | 11 | Spring | 19 | 24 | -9.6 | 8.71 | 44.8 | 265 | 15.9 | 19.79 | 35.69 | 9.6 | 51.73 | 15 | 0 | 16.04 | 5.727 | 0 | Diesel-backup
2025-11-18 20:00 | 322 | 11 | Spring | 20 | 24 | -5.7 | 4.98 | 100 | 82 | 4.92 | 0.45 | 5.37 | 5.7 | 50.2 | 15 | 0 | 44.83 | 14.355 | 0 | Diesel-backup
2025-11-18 21:00 | 322 | 11 | Spring | 21 | 24 | -1.5 | 6.4 | 47.3 | 161.9 | 9.71 | 3.41 | 13.12 | 1.5 | 45 | 15 | 0 | 31.88 | 10.737 | 0 | Diesel-backup
2025-11-18 22:00 | 322 | 11 | Spring | 22 | 24 | -5.7 | 3.65 | 71.2 | 79.1 | 4.75 | 0 | 4.75 | 5.7 | 45 | 15 | 0 | 40.25 | 13.125 | 0 | Diesel-backup
2025-11-18 23:00 | 322 | 11 | Spring | 23 | 24 | -2.2 | 10.49 | 59.3 | 47.5 | 2.85 | 47.8 | 50.65 | 2.2 | 45 | 17.08 | 5.65 | 0 | 0 | 0 | Normal
2025-11-19 | 323 | 11 | Spring | 0 | 24 | -4.1 | 7.85 | 69.2 | 0 | 0 | 11.52 | 11.52 | 4.1 | 45 | 15 | -5.2 | 28.28 | 9.655 | 0 | Diesel-backup
2025-11-19 01:00 | 323 | 11 | Spring | 1 | 24 | -8.3 | 9.38 | 31.2 | 65.6 | 3.94 | 28.45 | 32.39 | 8.3 | 45 | 15 | 0 | 12.61 | 4.558 | 0 | Diesel-backup
2025-11-19 02:00 | 323 | 11 | Spring | 2 | 24 | -7 | 7.18 | 14.2 | 151.7 | 9.1 | 6.98 | 16.08 | 7 | 45 | 15 | 0 | 28.92 | 9.85 | 0 | Diesel-backup
2025-11-19 03:00 | 323 | 11 | Spring | 3 | 24 | -7 | 11.55 | 96.4 | 69.6 | 4.18 | 73.01 | 77.19 | 7 | 45 | 26.85 | 32.19 | 0 | 0 | 0 | Normal
2025-11-19 04:00 | 323 | 11 | Spring | 4 | 24 | -9.2 | 5.02 | 47.9 | 210.1 | 12.61 | 0.49 | 13.1 | 9.2 | 45 | 15 | -29.61 | 2.29 | 0.856 | 0 | Diesel-backup
2025-11-19 05:00 | 323 | 11 | Spring | 5 | 24 | -9.5 | 7.61 | 29 | 312.4 | 18.74 | 9.72 | 28.46 | 9.5 | 45 | 15 | 0 | 16.54 | 5.895 | 0 | Diesel-backup
2025-11-19 06:00 | 323 | 11 | Spring | 6 | 24 | -4.3 | 31.08 | 41.9 | 318 | 19.08 | 0 | 19.08 | 4.3 | 45 | 15 | 0 | 25.92 | 8.927 | 0 | Diesel-backup
2025-11-19 07:00 | 323 | 11 | Spring | 7 | 24 | -9.9 | 3.22 | 53.8 | 310.4 | 18.62 | 0 | 18.62 | 9.9 | 45 | 15 | 0 | 26.38 | 9.07 | 0 | Diesel-backup
2025-11-19 08:00 | 323 | 11 | Spring | 8 | 24 | -5.5 | 13.68 | 4 | 550.9 | 33.05 | 120 | 153.05 | 5.5 | 47.85 | 53.71 | 105.2 | 0 | 0 | 0 | Normal
2025-11-19 09:00 | 323 | 11 | Spring | 9 | 24 | -8.7 | 23.38 | 22.9 | 501.9 | 30.11 | 120 | 150.11 | 8.7 | 51.49 | 90.01 | 98.62 | 0 | 0 | 0 | Normal
2025-11-19 10:00 | 323 | 11 | Spring | 10 | 24 | -7.7 | 9.91 | 3.4 | 617.4 | 37.04 | 36.86 | 73.9 | 7.7 | 48.28 | 95 | 13.57 | 0 | 0 | 0 | Normal
2025-11-19 11:00 | 323 | 11 | Spring | 11 | 24 | -6.2 | 0.87 | 46 | 425.7 | 25.54 | 0 | 25.54 | 6.2 | 45 | 87.22 | -19.46 | 0 | 0 | 0 | Battery-supported
2025-11-19 12:00 | 323 | 11 | Spring | 12 | 24 | -8.4 | 3.33 | 78.3 | 270.8 | 16.25 | 0 | 16.25 | 8.4 | 45 | 75.72 | -28.75 | 0 | 0 | 0 | Battery-supported
2025-11-19 13:00 | 323 | 11 | Spring | 13 | 24 | -5.5 | 8.75 | 18.5 | 560.1 | 33.61 | 20.25 | 53.86 | 5.5 | 52.22 | 76.32 | 1.64 | 0 | 0 | 0 | Normal
2025-11-19 14:00 | 323 | 11 | Spring | 14 | 24 | -10.8 | 7.24 | 15.9 | 558.2 | 33.49 | 7.32 | 40.81 | 10.8 | 53.88 | 71.09 | -13.07 | 0 | 0 | 0 | Battery-supported
2025-11-19 15:00 | 323 | 11 | Spring | 15 | 24 | -5 | 17.16 | 23.1 | 501.2 | 30.07 | 120 | 150.07 | 5 | 52.08 | 95 | 64.97 | 0 | 0 | 0 | Normal
2025-11-19 16:00 | 323 | 11 | Spring | 16 | 24 | -11 | 17.48 | 57.7 | 322 | 19.32 | 120 | 139.32 | 11 | 53.36 | 95 | 0 | 0 | 0 | 0 | Normal
2025-11-19 17:00 | 323 | 11 | Spring | 17 | 24 | -5.8 | 6.9 | 27.5 | 413.2 | 24.79 | 5.5 | 30.29 | 5.8 | 48.71 | 87.63 | -18.42 | 0 | 0 | 0 | Battery-supported
2025-11-19 18:00 | 323 | 11 | Spring | 18 | 24 | -3.1 | 7.23 | 35.3 | 340.9 | 20.45 | 7.26 | 27.71 | 3.1 | 45 | 80.72 | -17.29 | 0 | 0 | 0 | Battery-supported
2025-11-19 19:00 | 323 | 11 | Spring | 19 | 24 | -3.5 | 5.23 | 83.4 | 149.5 | 8.97 | 0.72 | 9.69 | 3.5 | 45.01 | 66.59 | -35.32 | 0 | 0 | 0 | Battery-supported
2025-11-19 20:00 | 323 | 11 | Spring | 20 | 24 | -7.7 | 9.64 | 48.2 | 209.4 | 12.56 | 32.4 | 44.96 | 7.7 | 51.63 | 63.92 | -6.67 | 0 | 0 | 0 | Battery-supported
2025-11-19 21:00 | 323 | 11 | Spring | 21 | 24 | -7.5 | 3.98 | 78.2 | 103.8 | 6.23 | 0.02 | 6.25 | 7.5 | 45 | 48.42 | -38.75 | 0 | 0 | 0 | Battery-supported
2025-11-19 22:00 | 323 | 11 | Spring | 22 | 24 | -6.5 | 6.73 | 20.5 | 143.6 | 8.62 | 4.72 | 13.34 | 6.5 | 45.33 | 35.62 | -31.99 | 0 | 0 | 0 | Battery-supported
2025-11-19 23:00 | 323 | 11 | Spring | 23 | 24 | -4.9 | 4.18 | 59.1 | 47.7 | 2.86 | 0.04 | 2.9 | 4.9 | 45.43 | 18.61 | -42.53 | 0 | 0 | 0 | Battery-supported
2025-11-20 | 324 | 11 | Spring | 0 | 24 | -9.9 | 8.36 | 15.8 | 0 | 0 | 16.07 | 16.07 | 9.9 | 50.09 | 15 | -9.03 | 24.99 | 8.637 | 0 | Diesel-backup
2025-11-20 01:00 | 324 | 11 | Spring | 1 | 24 | -5.8 | 13.14 | 65.1 | 43.8 | 2.63 | 120 | 122.63 | 5.8 | 46.96 | 42.85 | 75.67 | 0 | 0 | 0 | Normal
2025-11-20 02:00 | 324 | 11 | Spring | 2 | 24 | -5.5 | 2.7 | 62.4 | 90.3 | 5.42 | 0 | 5.42 | 5.5 | 45 | 27.01 | -39.58 | 0 | 0 | 0 | Battery-supported
2025-11-20 03:00 | 324 | 11 | Spring | 3 | 24 | -7.2 | 6.43 | 88.8 | 83.8 | 5.03 | 3.52 | 8.55 | 7.2 | 47 | 15 | -30.04 | 8.41 | 3.086 | 0 | Diesel-backup
2025-11-20 04:00 | 324 | 11 | Spring | 4 | 24 | -5.8 | 15.53 | 86.1 | 116.3 | 6.98 | 120 | 126.98 | 5.8 | 45 | 45.17 | 81.98 | 0 | 0 | 0 | Normal
2025-11-20 05:00 | 324 | 11 | Spring | 5 | 24 | -6.7 | 18.19 | 30 | 309.6 | 18.58 | 120 | 138.58 | 6.7 | 45 | 79.61 | 93.58 | 0 | 0 | 0 | Normal
2025-11-20 06:00 | 324 | 11 | Spring | 6 | 24 | -8.6 | 5.24 | 0.7 | 461.3 | 27.68 | 0.74 | 28.42 | 8.6 | 45 | 72.97 | -16.58 | 0 | 0 | 0 | Battery-supported
2025-11-20 07:00 | 324 | 11 | Spring | 7 | 24 | -11.9 | 4.3 | 38.2 | 371.3 | 22.28 | 0.07 | 22.35 | 11.9 | 45.39 | 63.76 | -23.04 | 0 | 0 | 0 | Battery-supported
2025-11-20 08:00 | 324 | 11 | Spring | 8 | 24 | -7.4 | 0.61 | 57.2 | 324.3 | 19.46 | 0 | 19.46 | 7.4 | 45 | 53.54 | -25.54 | 0 | 0 | 0 | Battery-supported
2025-11-20 09:00 | 324 | 11 | Spring | 9 | 24 | -9.7 | 13.98 | 18.3 | 522.8 | 31.37 | 120 | 151.37 | 9.7 | 54.92 | 89.04 | 96.45 | 0 | 0 | 0 | Normal
2025-11-20 10:00 | 324 | 11 | Spring | 10 | 24 | -8.7 | 13.46 | 84 | 234.6 | 14.08 | 120 | 134.08 | 8.7 | 50.88 | 95 | 16.21 | 0 | 0 | 0 | Normal
2025-11-20 11:00 | 324 | 11 | Spring | 11 | 24 | -6.2 | 7.8 | 53.7 | 388.4 | 23.3 | 11.13 | 34.43 | 6.2 | 47.13 | 89.92 | -12.7 | 0 | 0 | 0 | Battery-supported
2025-11-20 12:00 | 324 | 11 | Spring | 12 | 24 | -3.8 | 24.77 | 38.1 | 468.4 | 28.1 | 120 | 148.1 | 3.8 | 52.14 | 95 | 13.8 | 0 | 0 | 0 | Normal
2025-11-20 13:00 | 324 | 11 | Spring | 13 | 24 | -6.6 | 7.21 | 31.7 | 495.9 | 29.75 | 7.15 | 36.9 | 6.6 | 49.64 | 89.9 | -12.74 | 0 | 0 | 0 | Battery-supported
2025-11-20 14:00 | 324 | 11 | Spring | 14 | 24 | -4.9 | 14.23 | 9.2 | 589.9 | 35.39 | 120 | 155.39 | 4.9 | 45 | 95 | 13.85 | 0 | 0 | 0 | Normal
2025-11-20 15:00 | 324 | 11 | Spring | 15 | 24 | -8.9 | 5.44 | 13.2 | 545.9 | 32.75 | 1.02 | 33.77 | 8.9 | 51.83 | 87.78 | -18.06 | 0 | 0 | 0 | Battery-supported
2025-11-20 16:00 | 324 | 11 | Spring | 16 | 24 | -4.9 | 6.27 | 61.4 | 306.4 | 18.38 | 2.97 | 21.35 | 4.9 | 54.75 | 74.42 | -33.4 | 0 | 0 | 0 | Battery-supported
2025-11-20 17:00 | 324 | 11 | Spring | 17 | 24 | -5.2 | 8.69 | 46.9 | 337.2 | 20.23 | 19.57 | 39.8 | 5.2 | 47.68 | 71.26 | -7.88 | 0 | 0 | 0 | Battery-supported
2025-11-20 18:00 | 324 | 11 | Spring | 18 | 24 | -2.2 | 4.2 | 47.9 | 297.2 | 17.83 | 0.05 | 17.88 | 2.2 | 48.43 | 59.04 | -30.55 | 0 | 0 | 0 | Battery-supported
2025-11-20 19:00 | 324 | 11 | Spring | 19 | 24 | -5.9 | 12.04 | 94.5 | 116.4 | 6.98 | 87.17 | 94.15 | 5.9 | 46.01 | 76.76 | 48.14 | 0 | 0 | 0 | Normal
2025-11-20 20:00 | 324 | 11 | Spring | 20 | 24 | -5.2 | 7.97 | 41.4 | 226 | 13.56 | 12.5 | 26.06 | 5.2 | 50.18 | 67.11 | -24.12 | 0 | 0 | 0 | Battery-supported
2025-11-20 21:00 | 324 | 11 | Spring | 21 | 24 | -2.4 | 1.91 | 30 | 194.5 | 11.67 | 0 | 11.67 | 2.4 | 45 | 53.78 | -33.33 | 0 | 0 | 0 | Battery-supported
2025-11-20 22:00 | 324 | 11 | Spring | 22 | 24 | -5.1 | 14.42 | 78.3 | 70.1 | 4.21 | 120 | 124.21 | 5.1 | 45 | 82.93 | 79.21 | 0 | 0 | 0 | Normal
2025-11-20 23:00 | 324 | 11 | Spring | 23 | 24 | -7.5 | 3.96 | 46.4 | 55.8 | 3.35 | 0.01 | 3.36 | 7.5 | 45 | 66.27 | -41.64 | 0 | 0 | 0 | Battery-supported
2025-11-21 | 325 | 11 | Spring | 0 | 24 | 0.4 | 4.22 | 80.7 | 0 | 0 | 0.05 | 0.05 | 0 | 45 | 48.29 | -44.95 | 0 | 0 | 0 | Battery-supported
2025-11-21 01:00 | 325 | 11 | Spring | 1 | 24 | -8 | 6.22 | 5.6 | 82 | 4.92 | 2.82 | 7.74 | 8 | 45 | 33.39 | -37.26 | 0 | 0 | 0 | Battery-supported
2025-11-21 02:00 | 325 | 11 | Spring | 2 | 24 | -6.1 | 9.73 | 34.4 | 125.9 | 7.55 | 33.84 | 41.39 | 6.1 | 45 | 31.94 | -3.61 | 0 | 0 | 0 | Battery-supported
2025-11-21 03:00 | 325 | 11 | Spring | 3 | 24 | -5.6 | 8.99 | 57.1 | 143.6 | 8.62 | 23.16 | 31.78 | 5.6 | 45 | 26.66 | -13.22 | 0 | 0 | 0 | Battery-supported
2025-11-21 04:00 | 325 | 11 | Spring | 4 | 24 | -6.1 | 17.12 | 46.1 | 214.6 | 12.88 | 120 | 132.88 | 6.1 | 45 | 59 | 87.88 | 0 | 0 | 0 | Normal
2025-11-21 05:00 | 325 | 11 | Spring | 5 | 24 | -7.5 | 8.72 | 46.1 | 261.3 | 15.68 | 19.91 | 35.59 | 7.5 | 45 | 55.23 | -9.41 | 0 | 0 | 0 | Battery-supported
2025-11-21 06:00 | 325 | 11 | Spring | 6 | 24 | -7.7 | 2.51 | 25.8 | 374 | 22.44 | 0 | 22.44 | 7.7 | 45 | 46.21 | -22.56 | 0 | 0 | 0 | Battery-supported
2025-11-21 07:00 | 325 | 11 | Spring | 7 | 24 | -8 | 3.59 | 77.1 | 219.5 | 13.17 | 0 | 13.17 | 8 | 45 | 33.48 | -31.83 | 0 | 0 | 0 | Battery-supported
2025-11-21 08:00 | 325 | 11 | Spring | 8 | 24 | -9.9 | 2.35 | 22.7 | 471.4 | 28.28 | 0 | 28.28 | 9.9 | 57.69 | 21.71 | -29.41 | 0 | 0 | 0 | Battery-supported
2025-11-21 09:00 | 325 | 11 | Spring | 9 | 24 | -2.7 | 2.32 | 43 | 410.6 | 24.64 | 0 | 24.64 | 2.7 | 45 | 15 | -16.78 | 3.58 | 1.335 | 0 | Diesel-backup
2025-11-21 10:00 | 325 | 11 | Spring | 10 | 24 | -7.8 | 5.76 | 23.6 | 521.3 | 31.28 | 1.62 | 32.9 | 7.8 | 54.35 | 15 | 0 | 21.45 | 7.511 | 0 | Diesel-backup
2025-11-21 11:00 | 325 | 11 | Spring | 11 | 24 | -5.7 | 13.78 | 81 | 255.3 | 15.32 | 120 | 135.32 | 5.7 | 45 | 48.24 | 90.32 | 0 | 0 | 0 | Normal
2025-11-21 12:00 | 325 | 11 | Spring | 12 | 24 | -7.5 | 7.92 | 66.9 | 326.6 | 19.6 | 12.09 | 31.69 | 7.5 | 52.16 | 40.05 | -20.47 | 0 | 0 | 0 | Battery-supported
2025-11-21 13:00 | 325 | 11 | Spring | 13 | 24 | -7.2 | 9.95 | 99.2 | 166.3 | 9.98 | 37.56 | 47.54 | 7.2 | 54.12 | 37.42 | -6.58 | 0 | 0 | 0 | Battery-supported
2025-11-21 14:00 | 325 | 11 | Spring | 14 | 24 | -7 | 11.88 | 28.6 | 497.9 | 29.87 | 82.36 | 112.23 | 7 | 51.57 | 59.74 | 60.66 | 0 | 0 | 0 | Normal
2025-11-21 15:00 | 325 | 11 | Spring | 15 | 24 | -9 | 14.35 | 28.1 | 478.1 | 28.69 | 120 | 148.69 | 9 | 50.2 | 95 | 95.81 | 0 | 0 | 0 | Normal
2025-11-21 16:00 | 325 | 11 | Spring | 16 | 24 | -5.6 | 4.52 | 76.4 | 242.6 | 14.56 | 0.15 | 14.71 | 5.6 | 47.44 | 81.91 | -32.73 | 0 | 0 | 0 | Battery-supported
2025-11-21 17:00 | 325 | 11 | Spring | 17 | 24 | -5.8 | 13.24 | 67.2 | 258 | 15.48 | 120 | 135.48 | 5.8 | 50.14 | 95 | 35.58 | 0 | 0 | 0 | Normal
2025-11-21 18:00 | 325 | 11 | Spring | 18 | 24 | -2.1 | 12.23 | 34.1 | 345 | 20.7 | 93.12 | 113.82 | 2.1 | 45.31 | 95 | 0 | 0 | 0 | 0 | Normal
2025-11-21 19:00 | 325 | 11 | Spring | 19 | 24 | -7.2 | 5.61 | 52.8 | 241.3 | 14.48 | 1.31 | 15.79 | 7.2 | 54.55 | 79.5 | -38.76 | 0 | 0 | 0 | Battery-supported
2025-11-21 20:00 | 325 | 11 | Spring | 20 | 24 | -5.8 | 4.33 | 4.7 | 316.4 | 18.98 | 0.08 | 19.06 | 5.8 | 45.01 | 69.12 | -25.95 | 0 | 0 | 0 | Battery-supported
2025-11-21 21:00 | 325 | 11 | Spring | 21 | 24 | -6.5 | 6.63 | 63.1 | 132.2 | 7.93 | 4.29 | 12.22 | 6.5 | 45.33 | 55.87 | -33.11 | 0 | 0 | 0 | Battery-supported
2025-11-21 22:00 | 325 | 11 | Spring | 22 | 24 | -1.5 | 16.84 | 41.2 | 117.3 | 7.04 | 120 | 127.04 | 1.5 | 45 | 86.06 | 82.04 | 0 | 0 | 0 | Normal
2025-11-21 23:00 | 325 | 11 | Spring | 23 | 24 | -6.8 | 14.21 | 66.5 | 42.9 | 2.57 | 120 | 122.57 | 6.8 | 45 | 95 | 24.29 | 0 | 0 | 0 | Normal
2025-11-22 | 326 | 11 | Spring | 0 | 24 | -3.8 | 5.56 | 72.5 | 0 | 0 | 1.22 | 1.22 | 3.8 | 45 | 77.49 | -43.78 | 0 | 0 | 0 | Battery-supported
2025-11-22 01:00 | 326 | 11 | Spring | 1 | 24 | -3.3 | 13.43 | 14.5 | 76.3 | 4.58 | 120 | 124.58 | 3.3 | 45 | 95 | 47.59 | 0 | 0 | 0 | Normal
2025-11-22 02:00 | 326 | 11 | Spring | 2 | 24 | -6.1 | 10.88 | 46.8 | 110.2 | 6.61 | 56.26 | 62.87 | 6.1 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-11-22 03:00 | 326 | 11 | Spring | 3 | 24 | -9.2 | 9.74 | 83.8 | 93.3 | 5.6 | 34.01 | 39.61 | 9.2 | 45 | 92.84 | -5.39 | 0 | 0 | 0 | Battery-supported
2025-11-22 04:00 | 326 | 11 | Spring | 4 | 24 | -9.6 | 16.01 | 19.7 | 279.4 | 16.76 | 120 | 136.76 | 9.6 | 45 | 95 | 5.86 | 0 | 0 | 0 | Normal
2025-11-22 05:00 | 326 | 11 | Spring | 5 | 24 | -5 | 8.89 | 35.5 | 293 | 17.58 | 21.92 | 39.5 | 5 | 45 | 92.8 | -5.5 | 0 | 0 | 0 | Battery-supported
2025-11-22 06:00 | 326 | 11 | Spring | 6 | 24 | -9.9 | 7.6 | 36.4 | 337.1 | 20.23 | 9.65 | 29.88 | 9.9 | 46.05 | 86.33 | -16.17 | 0 | 0 | 0 | Battery-supported
2025-11-22 07:00 | 326 | 11 | Spring | 7 | 24 | -6.4 | 1.63 | 75.6 | 225.3 | 13.52 | 0 | 13.52 | 6.4 | 48.97 | 72.15 | -35.45 | 0 | 0 | 0 | Battery-supported
2025-11-22 08:00 | 326 | 11 | Spring | 8 | 24 | -7.1 | 11.78 | 65.5 | 289.1 | 17.35 | 79.45 | 96.8 | 7.1 | 50.39 | 89.23 | 46.41 | 0 | 0 | 0 | Normal
2025-11-22 09:00 | 326 | 11 | Spring | 9 | 24 | -6.4 | 4.07 | 46.4 | 395.2 | 23.71 | 0.03 | 23.74 | 6.4 | 50.18 | 78.65 | -26.44 | 0 | 0 | 0 | Battery-supported
2025-11-22 10:00 | 326 | 11 | Spring | 10 | 24 | -6.1 | 3.64 | 73.2 | 285.6 | 17.14 | 0 | 17.14 | 6.1 | 55.4 | 63.35 | -38.26 | 0 | 0 | 0 | Battery-supported
2025-11-22 11:00 | 326 | 11 | Spring | 11 | 24 | -8.9 | 7.76 | 80.7 | 256.8 | 15.41 | 10.82 | 26.23 | 8.9 | 53.41 | 52.48 | -27.18 | 0 | 0 | 0 | Battery-supported
2025-11-22 12:00 | 326 | 11 | Spring | 12 | 24 | -8.7 | 3.59 | 28.7 | 514.8 | 30.89 | 0 | 30.89 | 8.7 | 55.92 | 42.47 | -25.03 | 0 | 0 | 0 | Battery-supported
2025-11-22 13:00 | 326 | 11 | Spring | 13 | 24 | -4.6 | 9.33 | 63.1 | 342.6 | 20.56 | 27.73 | 48.29 | 4.6 | 46.49 | 43.13 | 1.8 | 0 | 0 | 0 | Normal
2025-11-22 14:00 | 326 | 11 | Spring | 14 | 24 | -7.2 | 8.4 | 48.7 | 402.2 | 24.13 | 16.47 | 40.6 | 7.2 | 49.95 | 39.39 | -9.35 | 0 | 0 | 0 | Battery-supported
2025-11-22 15:00 | 326 | 11 | Spring | 15 | 24 | -11.5 | 7.96 | 74.6 | 266.7 | 16 | 12.42 | 28.42 | 11.5 | 51.8 | 30.04 | -23.38 | 0 | 0 | 0 | Battery-supported
2025-11-22 16:00 | 326 | 11 | Spring | 16 | 24 | -3.6 | 6.61 | 40.8 | 394.3 | 23.66 | 4.21 | 27.87 | 3.6 | 48.39 | 21.83 | -20.52 | 0 | 0 | 0 | Battery-supported
2025-11-22 17:00 | 326 | 11 | Spring | 17 | 24 | -7 | 11.56 | 32.7 | 392.9 | 23.57 | 73.29 | 96.86 | 7 | 51.9 | 38.37 | 44.96 | 0 | 0 | 0 | Normal
2025-11-22 18:00 | 326 | 11 | Spring | 18 | 24 | -3.5 | 9.36 | 64.5 | 239.5 | 14.37 | 28.16 | 42.53 | 3.5 | 49.33 | 35.65 | -6.8 | 0 | 0 | 0 | Battery-supported
2025-11-22 19:00 | 326 | 11 | Spring | 19 | 24 | -1.3 | 9.26 | 41.6 | 274.7 | 16.48 | 26.75 | 43.23 | 1.3 | 45.99 | 34.55 | -2.76 | 0 | 0 | 0 | Battery-supported
2025-11-22 20:00 | 326 | 11 | Spring | 20 | 24 | -4.3 | 4.35 | 41.1 | 226.8 | 13.61 | 0.09 | 13.7 | 4.3 | 46.71 | 21.35 | -33.01 | 0 | 0 | 0 | Battery-supported
2025-11-22 21:00 | 326 | 11 | Spring | 21 | 24 | -2.2 | 6.99 | 57.9 | 142.1 | 8.53 | 5.95 | 14.48 | 2.2 | 45 | 15 | -15.87 | 14.65 | 5.258 | 0 | Diesel-backup
2025-11-22 22:00 | 326 | 11 | Spring | 22 | 24 | -4.2 | 4.3 | 41.5 | 117 | 7.02 | 0.07 | 7.09 | 4.2 | 45.07 | 15 | 0 | 37.98 | 12.495 | 0 | Diesel-backup
2025-11-22 23:00 | 326 | 11 | Spring | 23 | 24 | -1.3 | 6.93 | 67.5 | 42.3 | 2.54 | 5.65 | 8.19 | 1.3 | 45 | 15 | 0 | 36.81 | 12.165 | 0 | Diesel-backup
2025-11-23 | 327 | 11 | Spring | 0 | 24 | -7.2 | 4.73 | 87.8 | 0 | 0 | 0.26 | 0.26 | 7.2 | 45 | 15 | 0 | 44.74 | 14.332 | 0 | Diesel-backup
2025-11-23 01:00 | 327 | 11 | Spring | 1 | 24 | -5.3 | 6.8 | 26.5 | 68.6 | 4.12 | 5.03 | 9.15 | 5.3 | 45 | 15 | 0 | 35.85 | 11.892 | 0 | Diesel-backup
2025-11-23 02:00 | 327 | 11 | Spring | 2 | 24 | -4.2 | 6.97 | 60.3 | 93 | 5.58 | 5.85 | 11.43 | 4.2 | 45 | 15 | 0 | 33.57 | 11.234 | 0 | Diesel-backup
2025-11-23 03:00 | 327 | 11 | Spring | 3 | 24 | -6.5 | 6.8 | 79.9 | 100.7 | 6.04 | 5.03 | 11.07 | 6.5 | 45 | 15 | 0 | 33.93 | 11.338 | 0 | Diesel-backup
2025-11-23 04:00 | 327 | 11 | Spring | 4 | 24 | -3.9 | 11.67 | 26 | 264 | 15.84 | 76.33 | 92.17 | 3.9 | 45 | 32.36 | 47.17 | 0 | 0 | 0 | Normal
2025-11-23 05:00 | 327 | 11 | Spring | 5 | 24 | -7.7 | 10.06 | 32.6 | 301.6 | 18.1 | 39.51 | 57.61 | 7.7 | 45 | 37 | 12.61 | 0 | 0 | 0 | Normal
2025-11-23 06:00 | 327 | 11 | Spring | 6 | 24 | -2.4 | 2.99 | 47.5 | 298.7 | 17.92 | 0 | 17.92 | 2.4 | 45 | 26.17 | -27.08 | 0 | 0 | 0 | Battery-supported
2025-11-23 07:00 | 327 | 11 | Spring | 7 | 24 | -2.4 | 6.36 | 64.2 | 270 | 16.2 | 3.27 | 19.47 | 2.4 | 45 | 15.96 | -25.53 | 0 | 0 | 0 | Battery-supported
2025-11-23 08:00 | 327 | 11 | Spring | 8 | 24 | -6.5 | 7.92 | 30.4 | 438.6 | 26.32 | 12.09 | 38.41 | 6.5 | 45 | 15 | -2.39 | 4.2 | 1.564 | 0 | Diesel-backup
2025-11-23 09:00 | 327 | 11 | Spring | 9 | 24 | -5.9 | 4.6 | 46.7 | 393.6 | 23.62 | 0.19 | 23.81 | 5.9 | 52.99 | 15 | 0 | 29.18 | 9.928 | 0 | Diesel-backup
2025-11-23 10:00 | 327 | 11 | Spring | 10 | 24 | -4.3 | 8.38 | 64.1 | 329.1 | 19.75 | 16.27 | 36.02 | 4.3 | 51.22 | 15 | 0 | 15.2 | 5.444 | 0 | Diesel-backup
2025-11-23 11:00 | 327 | 11 | Spring | 11 | 24 | -9.3 | 4.96 | 45 | 431.1 | 25.87 | 0.44 | 26.31 | 9.3 | 53.37 | 15 | 0 | 27.06 | 9.281 | 0 | Diesel-backup
2025-11-23 12:00 | 327 | 11 | Spring | 12 | 24 | -9.3 | 7.25 | 40.7 | 455.6 | 27.34 | 7.38 | 34.72 | 9.3 | 51.47 | 15 | 0 | 16.75 | 5.966 | 0 | Diesel-backup
2025-11-23 13:00 | 327 | 11 | Spring | 13 | 24 | -3.3 | 3.99 | 62.1 | 347.4 | 20.84 | 0.02 | 20.86 | 3.3 | 49.35 | 15 | 0 | 28.49 | 9.719 | 0 | Diesel-backup
2025-11-23 14:00 | 327 | 11 | Spring | 14 | 24 | -5.1 | 6.78 | 51.4 | 389.4 | 23.36 | 4.94 | 28.3 | 5.1 | 48.33 | 15 | 0 | 20.03 | 7.05 | 0 | Diesel-backup
2025-11-23 15:00 | 327 | 11 | Spring | 15 | 24 | -5.8 | 10.21 | 58.7 | 339.4 | 20.36 | 42.28 | 62.64 | 5.8 | 48.15 | 20.33 | 14.49 | 0 | 0 | 0 | Normal
2025-11-23 16:00 | 327 | 11 | Spring | 16 | 24 | -4.9 | 11.02 | 28.3 | 447.5 | 26.85 | 59.52 | 86.37 | 4.9 | 45 | 35.56 | 41.37 | 0 | 0 | 0 | Normal
2025-11-23 17:00 | 327 | 11 | Spring | 17 | 24 | -9.8 | 7.33 | 64.8 | 267.3 | 16.04 | 7.86 | 23.9 | 9.8 | 54.64 | 23.26 | -30.74 | 0 | 0 | 0 | Battery-supported
2025-11-23 18:00 | 327 | 11 | Spring | 18 | 24 | -4.8 | 20.75 | 36.9 | 335.5 | 20.13 | 120 | 140.13 | 4.8 | 53.38 | 55.18 | 86.75 | 0 | 0 | 0 | Normal
2025-11-23 19:00 | 327 | 11 | Spring | 19 | 24 | -5.9 | 8.86 | 51.9 | 244 | 14.64 | 21.55 | 36.19 | 5.9 | 45 | 51.66 | -8.81 | 0 | 0 | 0 | Battery-supported
2025-11-23 20:00 | 327 | 11 | Spring | 20 | 24 | -2.1 | 11.21 | 42 | 224.8 | 13.49 | 64.15 | 77.64 | 2.1 | 45 | 63.67 | 32.64 | 0 | 0 | 0 | Normal
2025-11-23 21:00 | 327 | 11 | Spring | 21 | 24 | -2 | 14.58 | 51.2 | 154.6 | 9.28 | 120 | 129.28 | 2 | 45 | 94.69 | 84.28 | 0 | 0 | 0 | Normal
2025-11-23 22:00 | 327 | 11 | Spring | 22 | 24 | -3.1 | 4.65 | 3.6 | 165.2 | 9.91 | 0.21 | 10.12 | 3.1 | 45 | 80.74 | -34.88 | 0 | 0 | 0 | Battery-supported
2025-11-23 23:00 | 327 | 11 | Spring | 23 | 24 | -3.7 | 10.15 | 33.3 | 64.3 | 3.86 | 41.16 | 45.02 | 3.7 | 45 | 80.74 | 0.02 | 0 | 0 | 0 | Normal
2025-11-24 | 328 | 11 | Spring | 0 | 24 | -8 | 8.29 | 61.9 | 0 | 0 | 15.38 | 15.38 | 8 | 48.07 | 67.67 | -32.69 | 0 | 0 | 0 | Battery-supported
2025-11-24 01:00 | 328 | 11 | Spring | 1 | 24 | -3.8 | 10.33 | 65.3 | 43.7 | 2.62 | 44.59 | 47.21 | 3.8 | 46.77 | 67.83 | 0.44 | 0 | 0 | 0 | Normal
2025-11-24 02:00 | 328 | 11 | Spring | 2 | 24 | -4.1 | 12.58 | 64.2 | 88.1 | 5.29 | 104.78 | 110.07 | 4.1 | 45 | 91.77 | 65.07 | 0 | 0 | 0 | Normal
2025-11-24 03:00 | 328 | 11 | Spring | 3 | 24 | -3.1 | 4.15 | 1.2 | 248.7 | 14.92 | 0.04 | 14.96 | 3.1 | 45 | 79.76 | -30.04 | 0 | 0 | 0 | Battery-supported
2025-11-24 04:00 | 328 | 11 | Spring | 4 | 24 | -1.6 | 20.2 | 46.8 | 212.8 | 12.77 | 120 | 132.77 | 1.6 | 45 | 95 | 41.42 | 0 | 0 | 0 | Normal
2025-11-24 05:00 | 328 | 11 | Spring | 5 | 24 | -10.3 | 7.51 | 69.7 | 190.6 | 11.44 | 9.02 | 20.46 | 10.3 | 45 | 85.18 | -24.54 | 0 | 0 | 0 | Battery-supported
2025-11-24 06:00 | 328 | 11 | Spring | 6 | 24 | -7.6 | 5.97 | 47.2 | 299.6 | 17.98 | 2.11 | 20.09 | 7.6 | 45 | 75.22 | -24.91 | 0 | 0 | 0 | Battery-supported
2025-11-24 07:00 | 328 | 11 | Spring | 7 | 24 | -8.6 | 1.24 | 19.7 | 443.6 | 26.62 | 0 | 26.62 | 8.6 | 45.77 | 67.56 | -19.15 | 0 | 0 | 0 | Battery-supported
2025-11-24 08:00 | 328 | 11 | Spring | 8 | 24 | -6.6 | 13.99 | 23.3 | 468.7 | 28.12 | 120 | 148.12 | 6.6 | 52.2 | 95 | 74.57 | 0 | 0 | 0 | Normal
2025-11-24 09:00 | 328 | 11 | Spring | 9 | 24 | -6.9 | 12.1 | 50.8 | 375.2 | 22.51 | 89.02 | 111.53 | 6.9 | 52.12 | 95 | 0 | 0 | 0 | 0 | Normal
2025-11-24 10:00 | 328 | 11 | Spring | 10 | 24 | -7.3 | 6.47 | 23 | 524.1 | 31.45 | 3.67 | 35.12 | 7.3 | 48.41 | 89.68 | -13.29 | 0 | 0 | 0 | Battery-supported
2025-11-24 11:00 | 328 | 11 | Spring | 11 | 24 | -4.3 | 1.96 | 64.7 | 334.9 | 20.09 | 0 | 20.09 | 4.3 | 47.81 | 78.6 | -27.72 | 0 | 0 | 0 | Battery-supported
2025-11-24 12:00 | 328 | 11 | Spring | 12 | 24 | -8.7 | 7.7 | 9.4 | 609.9 | 36.59 | 10.37 | 46.96 | 8.7 | 50.28 | 77.27 | -3.32 | 0 | 0 | 0 | Battery-supported
2025-11-24 13:00 | 328 | 11 | Spring | 13 | 24 | -8.2 | 2.75 | 100 | 162.6 | 9.76 | 0 | 9.76 | 8.2 | 54.7 | 59.29 | -44.94 | 0 | 0 | 0 | Battery-supported
2025-11-24 14:00 | 328 | 11 | Spring | 14 | 24 | -7.7 | 13.2 | 47.4 | 408.4 | 24.5 | 120 | 144.5 | 7.7 | 52.35 | 93.2 | 92.15 | 0 | 0 | 0 | Normal
2025-11-24 15:00 | 328 | 11 | Spring | 15 | 24 | -5.9 | 6.35 | 82 | 233.5 | 14.01 | 3.24 | 17.25 | 5.9 | 55.52 | 77.9 | -38.27 | 0 | 0 | 0 | Battery-supported
2025-11-24 16:00 | 328 | 11 | Spring | 16 | 24 | -7.4 | 3.92 | 79.8 | 228.3 | 13.7 | 0.01 | 13.71 | 7.4 | 51.7 | 62.7 | -37.99 | 0 | 0 | 0 | Battery-supported
2025-11-24 17:00 | 328 | 11 | Spring | 17 | 24 | -4.5 | 8.48 | 41.7 | 357.8 | 21.47 | 17.29 | 38.76 | 4.5 | 45 | 60.2 | -6.24 | 0 | 0 | 0 | Battery-supported
2025-11-24 18:00 | 328 | 11 | Spring | 18 | 24 | -4.6 | 9.21 | 57.1 | 265.2 | 15.91 | 26.06 | 41.97 | 4.6 | 45 | 58.99 | -3.03 | 0 | 0 | 0 | Battery-supported
2025-11-24 19:00 | 328 | 11 | Spring | 19 | 24 | -5.8 | 9.85 | 26.5 | 320 | 19.2 | 35.84 | 55.04 | 5.8 | 49.43 | 61.06 | 5.61 | 0 | 0 | 0 | Normal
2025-11-24 20:00 | 328 | 11 | Spring | 20 | 24 | -2.1 | 4.08 | 53.2 | 197.2 | 11.83 | 0.03 | 11.86 | 2.1 | 45 | 47.8 | -33.14 | 0 | 0 | 0 | Battery-supported
2025-11-24 21:00 | 328 | 11 | Spring | 21 | 24 | -4.2 | 12.53 | 71.7 | 115.9 | 6.95 | 103.06 | 110.01 | 4.2 | 45 | 71.72 | 65.01 | 0 | 0 | 0 | Normal
2025-11-24 22:00 | 328 | 11 | Spring | 22 | 24 | -1.9 | 6.44 | 70 | 80.7 | 4.84 | 3.56 | 8.4 | 1.9 | 45 | 57.08 | -36.6 | 0 | 0 | 0 | Battery-supported
2025-11-24 23:00 | 328 | 11 | Spring | 23 | 24 | -4.9 | 1.55 | 65.6 | 43.5 | 2.61 | 0 | 2.61 | 4.9 | 45 | 40.13 | -42.39 | 0 | 0 | 0 | Battery-supported
2025-11-25 | 329 | 11 | Spring | 0 | 24 | -4.6 | 6.88 | 75.1 | 0 | 0 | 5.4 | 5.4 | 4.6 | 45 | 24.29 | -39.6 | 0 | 0 | 0 | Battery-supported
2025-11-25 01:00 | 329 | 11 | Spring | 1 | 24 | -6.2 | 6.83 | 56.5 | 49.3 | 2.96 | 5.17 | 8.13 | 6.2 | 45 | 15 | -23.22 | 13.65 | 4.916 | 0 | Diesel-backup
2025-11-25 02:00 | 329 | 11 | Spring | 2 | 24 | -5.4 | 6.76 | 28.6 | 133.4 | 8 | 4.85 | 12.85 | 5.4 | 45 | 15 | 0 | 32.15 | 10.817 | 0 | Diesel-backup
2025-11-25 03:00 | 329 | 11 | Spring | 3 | 24 | -4.2 | 8.55 | 77 | 106.1 | 6.37 | 18.03 | 24.4 | 4.2 | 45 | 15 | 0 | 20.6 | 7.235 | 0 | Diesel-backup
2025-11-25 04:00 | 329 | 11 | Spring | 4 | 24 | -7 | 17.74 | 60.8 | 178.4 | 10.7 | 120 | 130.7 | 7 | 45 | 46.54 | 85.7 | 0 | 0 | 0 | Normal
2025-11-25 05:00 | 329 | 11 | Spring | 5 | 24 | -5.3 | 7.01 | 28.2 | 314.9 | 18.89 | 6.05 | 24.94 | 5.3 | 45 | 38.51 | -20.06 | 0 | 0 | 0 | Battery-supported
2025-11-25 06:00 | 329 | 11 | Spring | 6 | 24 | -8.4 | 7.53 | 20.6 | 392.2 | 23.53 | 9.16 | 32.69 | 8.4 | 45 | 33.59 | -12.31 | 0 | 0 | 0 | Battery-supported
2025-11-25 07:00 | 329 | 11 | Spring | 7 | 24 | -5.1 | 5.17 | 34.4 | 386.3 | 23.18 | 0.65 | 23.83 | 5.1 | 45 | 25.12 | -21.17 | 0 | 0 | 0 | Battery-supported
2025-11-25 08:00 | 329 | 11 | Spring | 8 | 24 | -8.1 | 7 | 86.4 | 200 | 12 | 6 | 18 | 8.1 | 51.93 | 15 | -25.3 | 8.63 | 3.162 | 0 | Diesel-backup
2025-11-25 09:00 | 329 | 11 | Spring | 9 | 24 | -4.9 | 9.94 | 43.4 | 408.9 | 24.53 | 37.38 | 61.91 | 4.9 | 50.2 | 19.31 | 11.71 | 0 | 0 | 0 | Normal
2025-11-25 10:00 | 329 | 11 | Spring | 10 | 24 | -6.5 | 10.07 | 37.5 | 455.2 | 27.31 | 39.69 | 67 | 6.5 | 56.25 | 23.27 | 10.75 | 0 | 0 | 0 | Normal
2025-11-25 11:00 | 329 | 11 | Spring | 11 | 24 | -3 | 15.11 | 27.6 | 515.5 | 30.93 | 120 | 150.93 | 3 | 47.3 | 61.4 | 103.63 | 0 | 0 | 0 | Normal
2025-11-25 12:00 | 329 | 11 | Spring | 12 | 24 | -8.6 | 1.85 | 38.3 | 467.5 | 28.05 | 0 | 28.05 | 8.6 | 53.81 | 51.1 | -25.76 | 0 | 0 | 0 | Battery-supported
2025-11-25 13:00 | 329 | 11 | Spring | 13 | 24 | -9 | 11.72 | 41.6 | 447.6 | 26.86 | 77.74 | 104.6 | 9 | 52.42 | 70.3 | 52.18 | 0 | 0 | 0 | Normal
2025-11-25 14:00 | 329 | 11 | Spring | 14 | 24 | -6.7 | 10.75 | 50.4 | 394.2 | 23.65 | 53.34 | 76.99 | 6.7 | 45 | 82.07 | 31.99 | 0 | 0 | 0 | Normal
2025-11-25 15:00 | 329 | 11 | Spring | 15 | 24 | -8 | 2.48 | 27.9 | 479 | 28.74 | 0 | 28.74 | 8 | 50.44 | 73.39 | -21.7 | 0 | 0 | 0 | Battery-supported
2025-11-25 16:00 | 329 | 11 | Spring | 16 | 24 | -7.6 | 14.93 | 67.3 | 281.3 | 16.88 | 120 | 136.88 | 7.6 | 55.96 | 95 | 58.72 | 0 | 0 | 0 | Normal
2025-11-25 17:00 | 329 | 11 | Spring | 17 | 24 | -2.9 | 2.87 | 62.8 | 275.1 | 16.51 | 0 | 16.51 | 2.9 | 47.83 | 82.47 | -31.32 | 0 | 0 | 0 | Battery-supported
2025-11-25 18:00 | 329 | 11 | Spring | 18 | 24 | -4 | 10.09 | 31.9 | 353 | 21.18 | 40.06 | 61.24 | 4 | 45.05 | 88.43 | 16.19 | 0 | 0 | 0 | Normal
2025-11-25 19:00 | 329 | 11 | Spring | 19 | 24 | -4.9 | 1.58 | 66.3 | 200.8 | 12.05 | 0 | 12.05 | 4.9 | 49.37 | 73.5 | -37.32 | 0 | 0 | 0 | Battery-supported
2025-11-25 20:00 | 329 | 11 | Spring | 20 | 24 | -4.7 | 3.88 | 16.7 | 286.8 | 17.21 | 0.01 | 17.22 | 4.7 | 45 | 62.39 | -27.78 | 0 | 0 | 0 | Battery-supported
2025-11-25 21:00 | 329 | 11 | Spring | 21 | 24 | -5.2 | 10.27 | 66 | 126.7 | 7.6 | 43.43 | 51.03 | 5.2 | 45 | 64.61 | 6.03 | 0 | 0 | 0 | Normal
2025-11-25 22:00 | 329 | 11 | Spring | 22 | 24 | -0.4 | 10.52 | 84.5 | 62.2 | 3.73 | 48.42 | 52.15 | 0.4 | 45 | 67.24 | 7.15 | 0 | 0 | 0 | Normal
2025-11-25 23:00 | 329 | 11 | Spring | 23 | 24 | -5.9 | 6.6 | 31.5 | 65.4 | 3.92 | 4.17 | 8.09 | 5.9 | 45 | 52.48 | -36.91 | 0 | 0 | 0 | Battery-supported
2025-11-26 | 330 | 11 | Spring | 0 | 24 | -7.3 | 15.68 | 35.6 | 0 | 0 | 120 | 120 | 7.3 | 45 | 80.08 | 75 | 0 | 0 | 0 | Normal
2025-11-26 01:00 | 330 | 11 | Spring | 1 | 24 | -3 | 10.1 | 34.2 | 63.7 | 3.82 | 40.24 | 44.06 | 3 | 45 | 79.7 | -0.94 | 0 | 0 | 0 | Battery-supported
2025-11-26 02:00 | 330 | 11 | Spring | 2 | 24 | -5.7 | 12.63 | 37.8 | 121.6 | 7.3 | 106.52 | 113.82 | 5.7 | 45 | 95 | 41.58 | 0 | 0 | 0 | Normal
2025-11-26 03:00 | 330 | 11 | Spring | 3 | 24 | -1.1 | 6.76 | 17.6 | 217.8 | 13.07 | 4.85 | 17.92 | 1.1 | 45 | 84.17 | -27.08 | 0 | 0 | 0 | Battery-supported
2025-11-26 04:00 | 330 | 11 | Spring | 4 | 24 | -7.1 | 3.49 | 64.9 | 168.4 | 10.1 | 0 | 10.1 | 7.1 | 45 | 70.21 | -34.9 | 0 | 0 | 0 | Battery-supported
2025-11-26 05:00 | 330 | 11 | Spring | 5 | 24 | -4.4 | 3.47 | 7.6 | 376.5 | 22.59 | 0 | 22.59 | 4.4 | 45 | 61.24 | -22.41 | 0 | 0 | 0 | Battery-supported
2025-11-26 06:00 | 330 | 11 | Spring | 6 | 24 | -4.1 | 5.87 | 95.2 | 132.5 | 7.95 | 1.86 | 9.81 | 4.1 | 45 | 47.17 | -35.19 | 0 | 0 | 0 | Battery-supported
2025-11-26 07:00 | 330 | 11 | Spring | 7 | 24 | -7.8 | 3.99 | 22.6 | 432.1 | 25.93 | 0.02 | 25.95 | 7.8 | 45 | 39.55 | -19.05 | 0 | 0 | 0 | Battery-supported
2025-11-26 08:00 | 330 | 11 | Spring | 8 | 24 | -8.3 | 3.81 | 29.5 | 442.3 | 26.54 | 0 | 26.54 | 8.3 | 52.33 | 29.23 | -25.79 | 0 | 0 | 0 | Battery-supported
2025-11-26 09:00 | 330 | 11 | Spring | 9 | 24 | -5 | 2.16 | 47.4 | 390.5 | 23.43 | 0 | 23.43 | 5 | 45 | 20.6 | -21.57 | 0 | 0 | 0 | Battery-supported
2025-11-26 10:00 | 330 | 11 | Spring | 10 | 24 | -5.2 | 6.11 | 76 | 272.4 | 16.34 | 2.49 | 18.83 | 5.2 | 50.03 | 15 | -14.01 | 17.19 | 6.113 | 0 | Diesel-backup
2025-11-26 11:00 | 330 | 11 | Spring | 11 | 24 | -9.3 | 2.12 | 55.7 | 378.8 | 22.73 | 0 | 22.73 | 9.3 | 55.88 | 15 | 0 | 33.15 | 11.111 | 0 | Diesel-backup
2025-11-26 12:00 | 330 | 11 | Spring | 12 | 24 | -8.4 | 6.03 | 48 | 419.6 | 25.18 | 2.27 | 27.45 | 8.4 | 52.55 | 15 | 0 | 25.1 | 8.671 | 0 | Diesel-backup
2025-11-26 13:00 | 330 | 11 | Spring | 13 | 24 | -11.1 | 1.72 | 51.6 | 398.7 | 23.92 | 0 | 23.92 | 11.1 | 55.61 | 15 | 0 | 31.69 | 10.681 | 0 | Diesel-backup
2025-11-26 14:00 | 330 | 11 | Spring | 14 | 24 | -3.9 | 5.68 | 40.6 | 440.7 | 26.44 | 1.45 | 27.89 | 3.9 | 47.94 | 15 | 0 | 20.05 | 7.056 | 0 | Diesel-backup
2025-11-26 15:00 | 330 | 11 | Spring | 15 | 24 | -5.4 | 9.9 | 74.5 | 267.5 | 16.05 | 36.69 | 52.74 | 5.4 | 50.56 | 15.8 | 2.18 | 0 | 0 | 0 | Normal
2025-11-26 16:00 | 330 | 11 | Spring | 16 | 24 | -4.8 | 3.89 | 80.2 | 226.2 | 13.57 | 0.01 | 13.58 | 4.8 | 45.08 | 15 | -2.01 | 29.49 | 10.024 | 0 | Diesel-backup
2025-11-26 17:00 | 330 | 11 | Spring | 17 | 24 | -7.8 | 8.59 | 25.8 | 419.5 | 25.17 | 18.46 | 43.63 | 7.8 | 47.33 | 15 | 0 | 3.7 | 1.38 | 0 | Diesel-backup
2025-11-26 18:00 | 330 | 11 | Spring | 18 | 24 | -6.3 | 8.26 | 64.9 | 238.2 | 14.29 | 15.09 | 29.38 | 6.3 | 45.94 | 15 | 0 | 16.56 | 5.902 | 0 | Diesel-backup
2025-11-26 19:00 | 330 | 11 | Spring | 19 | 24 | -4.8 | 4.65 | 26 | 321.3 | 19.28 | 0.21 | 19.49 | 4.8 | 50.45 | 15 | 0 | 30.96 | 10.464 | 0 | Diesel-backup
2025-11-26 20:00 | 330 | 11 | Spring | 20 | 24 | -5.2 | 2.04 | 80.2 | 130.8 | 7.85 | 0 | 7.85 | 5.2 | 45 | 15 | 0 | 37.15 | 12.261 | 0 | Diesel-backup
2025-11-26 21:00 | 330 | 11 | Spring | 21 | 24 | -3.5 | 16 | 39.4 | 176.9 | 10.61 | 120 | 130.61 | 3.5 | 45 | 46.5 | 85.61 | 0 | 0 | 0 | Normal
2025-11-26 22:00 | 330 | 11 | Spring | 22 | 24 | -2.6 | 11.73 | 23.3 | 140.1 | 8.41 | 78.02 | 86.43 | 2.6 | 45 | 61.75 | 41.43 | 0 | 0 | 0 | Normal
2025-11-26 23:00 | 330 | 11 | Spring | 23 | 24 | 0.9 | 4.62 | 67.9 | 42 | 2.52 | 0.2 | 2.72 | 0 | 45 | 44.84 | -42.28 | 0 | 0 | 0 | Battery-supported
2025-11-27 | 331 | 11 | Spring | 0 | 24 | -4.3 | 16.8 | 47.1 | 0 | 0 | 120 | 120 | 4.3 | 45 | 72.44 | 75 | 0 | 0 | 0 | Normal
2025-11-27 01:00 | 331 | 11 | Spring | 1 | 24 | -2.2 | 11.35 | 77.5 | 35.8 | 2.15 | 67.7 | 69.85 | 2.2 | 45 | 81.58 | 24.85 | 0 | 0 | 0 | Normal
2025-11-27 02:00 | 331 | 11 | Spring | 2 | 24 | -6.8 | 10.26 | 30 | 131.6 | 7.9 | 43.24 | 51.14 | 6.8 | 45 | 83.84 | 6.14 | 0 | 0 | 0 | Normal
2025-11-27 03:00 | 331 | 11 | Spring | 3 | 24 | -9.1 | 2.82 | 56.8 | 144.1 | 8.65 | 0 | 8.65 | 9.1 | 45.43 | 69.13 | -36.78 | 0 | 0 | 0 | Battery-supported
2025-11-27 04:00 | 331 | 11 | Spring | 4 | 24 | -6.5 | 10.29 | 62.6 | 173.9 | 10.43 | 43.81 | 54.24 | 6.5 | 45 | 72.53 | 9.24 | 0 | 0 | 0 | Normal
2025-11-27 05:00 | 331 | 11 | Spring | 5 | 24 | -9.6 | 13.41 | 96.3 | 110.9 | 6.65 | 120 | 126.65 | 9.6 | 45.24 | 95 | 61.06 | 0 | 0 | 0 | Normal
2025-11-27 06:00 | 331 | 11 | Spring | 6 | 24 | -6.3 | 7.52 | 84.9 | 168.5 | 10.11 | 9.09 | 19.2 | 6.3 | 45 | 84.68 | -25.8 | 0 | 0 | 0 | Battery-supported
2025-11-27 07:00 | 331 | 11 | Spring | 7 | 24 | -8.2 | 8.64 | 56.8 | 298.8 | 17.93 | 19.01 | 36.94 | 8.2 | 45 | 81.46 | -8.06 | 0 | 0 | 0 | Battery-supported
2025-11-27 08:00 | 331 | 11 | Spring | 8 | 24 | -10.8 | 9.9 | 32.8 | 428.5 | 25.71 | 36.69 | 62.4 | 10.8 | 57.61 | 83.22 | 4.79 | 0 | 0 | 0 | Normal
2025-11-27 09:00 | 331 | 11 | Spring | 9 | 24 | -2.7 | 14.29 | 61.5 | 326.5 | 19.59 | 120 | 139.59 | 2.7 | 45 | 95 | 32.01 | 0 | 0 | 0 | Normal
2025-11-27 10:00 | 331 | 11 | Spring | 10 | 24 | -7.5 | 9.11 | 67.3 | 313.9 | 18.83 | 24.71 | 43.54 | 7.5 | 55.33 | 90.28 | -11.79 | 0 | 0 | 0 | Battery-supported
2025-11-27 11:00 | 331 | 11 | Spring | 11 | 24 | -9.7 | 9.72 | 60.8 | 353.8 | 21.23 | 33.68 | 54.91 | 9.7 | 52.52 | 91.16 | 2.39 | 0 | 0 | 0 | Normal
2025-11-27 12:00 | 331 | 11 | Spring | 12 | 24 | -3.8 | 8.39 | 63.8 | 342.3 | 20.54 | 16.37 | 36.91 | 3.8 | 46.72 | 87.24 | -9.81 | 0 | 0 | 0 | Battery-supported
2025-11-27 13:00 | 331 | 11 | Spring | 13 | 24 | -7 | 17.08 | 11.3 | 595.5 | 35.73 | 120 | 155.73 | 7 | 47.17 | 95 | 21.09 | 0 | 0 | 0 | Normal
2025-11-27 14:00 | 331 | 11 | Spring | 14 | 24 | -2.6 | 7.64 | 78.6 | 260.1 | 15.61 | 9.93 | 25.54 | 2.6 | 45.48 | 87.02 | -19.94 | 0 | 0 | 0 | Battery-supported
2025-11-27 15:00 | 331 | 11 | Spring | 15 | 24 | -6.2 | 9.68 | 27.6 | 480.5 | 28.83 | 33.04 | 61.87 | 6.2 | 52.85 | 90.34 | 9.02 | 0 | 0 | 0 | Normal
2025-11-27 16:00 | 331 | 11 | Spring | 16 | 24 | -5.5 | 14.78 | 37.8 | 406.8 | 24.41 | 120 | 144.41 | 5.5 | 47.94 | 95 | 12.65 | 0 | 0 | 0 | Normal
2025-11-27 17:00 | 331 | 11 | Spring | 17 | 24 | -3.2 | 5.43 | 20.5 | 440.6 | 26.44 | 1.01 | 27.45 | 3.2 | 46.99 | 87.18 | -19.54 | 0 | 0 | 0 | Battery-supported
2025-11-27 18:00 | 331 | 11 | Spring | 18 | 24 | -2.4 | 18.86 | 31.4 | 354.4 | 21.26 | 120 | 141.26 | 2.4 | 51.87 | 95 | 21.24 | 0 | 0 | 0 | Normal
2025-11-27 19:00 | 331 | 11 | Spring | 19 | 24 | -1.9 | 5.09 | 11.8 | 364 | 21.84 | 0.56 | 22.4 | 1.9 | 45 | 85.96 | -22.6 | 0 | 0 | 0 | Battery-supported
2025-11-27 20:00 | 331 | 11 | Spring | 20 | 24 | -3.7 | 3.92 | 79.8 | 131.7 | 7.9 | 0.01 | 7.91 | 3.7 | 45 | 71.12 | -37.09 | 0 | 0 | 0 | Battery-supported
2025-11-27 21:00 | 331 | 11 | Spring | 21 | 24 | -2.4 | 9.85 | 97.3 | 67.8 | 4.07 | 35.84 | 39.91 | 2.4 | 45 | 69.09 | -5.09 | 0 | 0 | 0 | Battery-supported
2025-11-27 22:00 | 331 | 11 | Spring | 22 | 24 | -2.1 | 4.92 | 49.5 | 106.8 | 6.41 | 0.4 | 6.81 | 2.1 | 45 | 53.81 | -38.19 | 0 | 0 | 0 | Battery-supported
2025-11-27 23:00 | 331 | 11 | Spring | 23 | 24 | -3.5 | 16.64 | 24.5 | 69.9 | 4.19 | 120 | 124.19 | 3.5 | 45 | 82.95 | 79.19 | 0 | 0 | 0 | Normal
2025-11-28 | 332 | 11 | Spring | 0 | 24 | -4.4 | 22.17 | 43.9 | 0 | 0 | 120 | 120 | 4.4 | 45 | 95 | 32.73 | 0 | 0 | 0 | Normal
2025-11-28 01:00 | 332 | 11 | Spring | 1 | 24 | -7.7 | 4 | 33.2 | 64.3 | 3.86 | 0.02 | 3.88 | 7.7 | 45 | 78.55 | -41.12 | 0 | 0 | 0 | Battery-supported
2025-11-28 02:00 | 332 | 11 | Spring | 2 | 24 | -3.6 | 3.75 | 93.2 | 51.1 | 3.07 | 0 | 3.07 | 3.6 | 45 | 61.78 | -41.93 | 0 | 0 | 0 | Battery-supported
2025-11-28 03:00 | 332 | 11 | Spring | 3 | 24 | -5.2 | 3.63 | 94.5 | 73.1 | 4.39 | 0 | 4.39 | 5.2 | 45 | 45.54 | -40.61 | 0 | 0 | 0 | Battery-supported
2025-11-28 04:00 | 332 | 11 | Spring | 4 | 24 | -6.5 | 1.52 | 58.2 | 184.7 | 11.08 | 0 | 11.08 | 6.5 | 45 | 31.97 | -33.92 | 0 | 0 | 0 | Battery-supported
2025-11-28 05:00 | 332 | 11 | Spring | 5 | 24 | -3.1 | 4.82 | 53 | 240.6 | 14.44 | 0.32 | 14.76 | 3.1 | 45 | 19.87 | -30.24 | 0 | 0 | 0 | Battery-supported
2025-11-28 06:00 | 332 | 11 | Spring | 6 | 24 | -9.3 | 13.05 | 13.4 | 417.2 | 25.03 | 120 | 145.03 | 9.3 | 45.43 | 56.52 | 99.6 | 0 | 0 | 0 | Normal
2025-11-28 07:00 | 332 | 11 | Spring | 7 | 24 | -2.7 | 10.11 | 42.2 | 355.6 | 21.34 | 40.42 | 61.76 | 2.7 | 45 | 62.69 | 16.76 | 0 | 0 | 0 | Normal
2025-11-28 08:00 | 332 | 11 | Spring | 8 | 24 | -6.4 | 6.36 | 90.4 | 183 | 10.98 | 3.27 | 14.25 | 6.4 | 45.1 | 50.35 | -30.85 | 0 | 0 | 0 | Battery-supported
2025-11-28 09:00 | 332 | 11 | Spring | 9 | 24 | -5.6 | 9.44 | 55.7 | 352.6 | 21.16 | 29.33 | 50.49 | 5.6 | 52.84 | 49.41 | -2.35 | 0 | 0 | 0 | Battery-supported
2025-11-28 10:00 | 332 | 11 | Spring | 10 | 24 | -7 | 2.96 | 64.7 | 326.1 | 19.57 | 0 | 19.57 | 7 | 49.72 | 37.35 | -30.15 | 0 | 0 | 0 | Battery-supported
2025-11-28 11:00 | 332 | 11 | Spring | 11 | 24 | -9.6 | 7.6 | 40.1 | 454.8 | 27.29 | 9.65 | 36.94 | 9.6 | 52.73 | 31.04 | -15.79 | 0 | 0 | 0 | Battery-supported
2025-11-28 12:00 | 332 | 11 | Spring | 12 | 24 | -5.9 | 8.45 | 48.5 | 417.3 | 25.04 | 16.98 | 42.02 | 5.9 | 52.57 | 26.82 | -10.55 | 0 | 0 | 0 | Battery-supported
2025-11-28 13:00 | 332 | 11 | Spring | 13 | 24 | -4.5 | 8.14 | 99.6 | 164.7 | 9.88 | 13.98 | 23.86 | 4.5 | 45 | 18.36 | -21.14 | 0 | 0 | 0 | Battery-supported
2025-11-28 14:00 | 332 | 11 | Spring | 14 | 24 | -3.4 | 4.72 | 67.6 | 312.2 | 18.73 | 0.25 | 18.98 | 3.4 | 48.94 | 15 | -8.4 | 21.56 | 7.546 | 0 | Diesel-backup
2025-11-28 15:00 | 332 | 11 | Spring | 15 | 24 | -4.9 | 4.6 | 84.8 | 220.8 | 13.25 | 0.19 | 13.44 | 4.9 | 45 | 15 | 0 | 31.56 | 10.642 | 0 | Diesel-backup
2025-11-28 16:00 | 332 | 11 | Spring | 16 | 24 | -8.9 | 10.66 | 47.8 | 364.3 | 21.86 | 51.37 | 73.23 | 8.9 | 45.33 | 25.27 | 27.9 | 0 | 0 | 0 | Normal
2025-11-28 17:00 | 332 | 11 | Spring | 17 | 24 | -7.2 | 10.27 | 62.2 | 277.6 | 16.66 | 43.43 | 60.09 | 7.2 | 45 | 30.82 | 15.09 | 0 | 0 | 0 | Normal
2025-11-28 18:00 | 332 | 11 | Spring | 18 | 24 | 0.9 | 1.6 | 33.7 | 346.7 | 20.8 | 0 | 20.8 | 0 | 45.24 | 21.04 | -24.44 | 0 | 0 | 0 | Battery-supported
2025-11-28 19:00 | 332 | 11 | Spring | 19 | 24 | -5.8 | 1.57 | 66.2 | 200.9 | 12.05 | 0 | 12.05 | 5.8 | 51.28 | 15 | -15.11 | 24.12 | 8.363 | 0 | Diesel-backup
2025-11-28 20:00 | 332 | 11 | Spring | 20 | 24 | -0.2 | 21.2 | 36.2 | 238.9 | 14.33 | 120 | 134.33 | 0.2 | 46.53 | 47.31 | 87.8 | 0 | 0 | 0 | Normal
2025-11-28 21:00 | 332 | 11 | Spring | 21 | 24 | -5.5 | 8.61 | 100 | 62.8 | 3.77 | 18.68 | 22.45 | 5.5 | 45 | 38.29 | -22.55 | 0 | 0 | 0 | Battery-supported
2025-11-28 22:00 | 332 | 11 | Spring | 22 | 24 | -4 | 8.15 | 85.9 | 60.4 | 3.62 | 14.07 | 17.69 | 4 | 45 | 27.37 | -27.31 | 0 | 0 | 0 | Battery-supported
2025-11-28 23:00 | 332 | 11 | Spring | 23 | 24 | -2.4 | 4.11 | 31.1 | 65.6 | 3.94 | 0.03 | 3.97 | 2.4 | 45 | 15 | -30.92 | 10.11 | 3.688 | 0 | Diesel-backup
2025-11-29 | 333 | 11 | Spring | 0 | 24 | -5.8 | 5.86 | 30 | 0 | 0 | 1.84 | 1.84 | 5.8 | 45 | 15 | 0 | 43.16 | 13.913 | 0 | Diesel-backup
2025-11-29 01:00 | 333 | 11 | Spring | 1 | 24 | -0.8 | 4.96 | 50.5 | 53.2 | 3.19 | 0.44 | 3.63 | 0.8 | 45 | 15 | 0 | 41.37 | 13.431 | 0 | Diesel-backup
2025-11-29 02:00 | 333 | 11 | Spring | 2 | 24 | -4.6 | 13.06 | 53.3 | 101.9 | 6.11 | 120 | 126.11 | 4.6 | 45 | 44.85 | 81.11 | 0 | 0 | 0 | Normal
2025-11-29 03:00 | 333 | 11 | Spring | 3 | 24 | -4.1 | 12.72 | 8.1 | 235.8 | 14.15 | 109.7 | 123.85 | 4.1 | 45 | 73.87 | 78.85 | 0 | 0 | 0 | Normal
2025-11-29 04:00 | 333 | 11 | Spring | 4 | 24 | -6.1 | 8.67 | 23.3 | 270.8 | 16.25 | 19.34 | 35.59 | 6.1 | 48.96 | 68.52 | -13.37 | 0 | 0 | 0 | Battery-supported
2025-11-29 05:00 | 333 | 11 | Spring | 5 | 24 | -4.3 | 7.89 | 62.8 | 211.2 | 12.67 | 11.84 | 24.51 | 4.3 | 45 | 60.32 | -20.49 | 0 | 0 | 0 | Battery-supported
2025-11-29 06:00 | 333 | 11 | Spring | 6 | 24 | -2.5 | 9.57 | 55.8 | 269.7 | 16.18 | 31.3 | 47.48 | 2.5 | 45 | 61.23 | 2.48 | 0 | 0 | 0 | Normal
2025-11-29 07:00 | 333 | 11 | Spring | 7 | 24 | -6.5 | 7.82 | 88.9 | 173.2 | 10.39 | 11.28 | 21.67 | 6.5 | 45 | 51.9 | -23.33 | 0 | 0 | 0 | Battery-supported
2025-11-29 08:00 | 333 | 11 | Spring | 8 | 24 | -2.4 | 10.63 | 100 | 142 | 8.52 | 50.73 | 59.25 | 2.4 | 45.37 | 57.01 | 13.88 | 0 | 0 | 0 | Normal
2025-11-29 09:00 | 333 | 11 | Spring | 9 | 24 | -7.5 | 15.47 | 41.7 | 416.4 | 24.98 | 120 | 144.98 | 7.5 | 54.15 | 90.44 | 90.83 | 0 | 0 | 0 | Normal
2025-11-29 10:00 | 333 | 11 | Spring | 10 | 24 | -4.3 | 6.93 | 44 | 424.7 | 25.48 | 5.65 | 31.13 | 4.3 | 47.76 | 83.78 | -16.63 | 0 | 0 | 0 | Battery-supported
2025-11-29 11:00 | 333 | 11 | Spring | 11 | 24 | -4.7 | 4.14 | 41.2 | 449.1 | 26.95 | 0.04 | 26.99 | 4.7 | 45.82 | 76.25 | -18.83 | 0 | 0 | 0 | Battery-supported
2025-11-29 12:00 | 333 | 11 | Spring | 12 | 24 | -7.8 | 7.94 | 5.2 | 630.4 | 37.82 | 12.25 | 50.07 | 7.8 | 45 | 78.12 | 5.07 | 0 | 0 | 0 | Normal
2025-11-29 13:00 | 333 | 11 | Spring | 13 | 24 | -4.6 | 5.1 | 26 | 523.5 | 31.41 | 0.57 | 31.98 | 4.6 | 45.86 | 72.56 | -13.88 | 0 | 0 | 0 | Battery-supported
2025-11-29 14:00 | 333 | 11 | Spring | 14 | 24 | -4.7 | 2.47 | 17.6 | 550 | 33 | 0 | 33 | 4.7 | 50.17 | 65.7 | -17.17 | 0 | 0 | 0 | Battery-supported
2025-11-29 15:00 | 333 | 11 | Spring | 15 | 24 | -6.2 | 3.43 | 69.1 | 291.8 | 17.51 | 0 | 17.51 | 6.2 | 45 | 54.7 | -27.49 | 0 | 0 | 0 | Battery-supported
2025-11-29 16:00 | 333 | 11 | Spring | 16 | 24 | -3.2 | 14.25 | 41.3 | 392.1 | 23.53 | 120 | 143.53 | 3.2 | 51.79 | 88.46 | 91.74 | 0 | 0 | 0 | Normal
2025-11-29 17:00 | 333 | 11 | Spring | 17 | 24 | -3.3 | 7.68 | 17.4 | 452.6 | 27.16 | 10.22 | 37.38 | 3.3 | 47.02 | 84.61 | -9.64 | 0 | 0 | 0 | Battery-supported
2025-11-29 18:00 | 333 | 11 | Spring | 18 | 24 | -3.6 | 5.83 | 26.6 | 371.4 | 22.28 | 1.77 | 24.05 | 3.6 | 51.94 | 73.45 | -27.89 | 0 | 0 | 0 | Battery-supported
2025-11-29 19:00 | 333 | 11 | Spring | 19 | 24 | -3.4 | 8.38 | 14.6 | 355.5 | 21.33 | 16.27 | 37.6 | 3.4 | 45.81 | 70.17 | -8.21 | 0 | 0 | 0 | Battery-supported
2025-11-29 20:00 | 333 | 11 | Spring | 20 | 24 | -3.4 | 5.35 | 41.8 | 225.2 | 13.51 | 0.89 | 14.4 | 3.4 | 45 | 57.93 | -30.6 | 0 | 0 | 0 | Battery-supported
2025-11-29 21:00 | 333 | 11 | Spring | 21 | 24 | -4.1 | 14.5 | 70.3 | 118.7 | 7.12 | 120 | 127.12 | 4.1 | 45 | 88.15 | 82.12 | 0 | 0 | 0 | Normal
2025-11-29 22:00 | 333 | 11 | Spring | 22 | 24 | -3.1 | 21.01 | 23.7 | 139.6 | 8.38 | 120 | 128.38 | 3.1 | 45 | 95 | 18.63 | 0 | 0 | 0 | Normal
2025-11-29 23:00 | 333 | 11 | Spring | 23 | 24 | -5.1 | 5.54 | 34.1 | 63.8 | 3.83 | 1.19 | 5.02 | 5.1 | 45 | 79.01 | -39.98 | 0 | 0 | 0 | Battery-supported
2025-11-30 | 334 | 11 | Spring | 0 | 24 | 2 | 6.71 | 36 | 0 | 0 | 4.63 | 4.63 | 0 | 45 | 62.86 | -40.37 | 0 | 0 | 0 | Battery-supported
2025-11-30 01:00 | 334 | 11 | Spring | 1 | 24 | -7.3 | 9.02 | 67.5 | 42.3 | 2.54 | 23.54 | 26.08 | 7.3 | 45 | 55.29 | -18.92 | 0 | 0 | 0 | Battery-supported
2025-11-30 02:00 | 334 | 11 | Spring | 2 | 24 | -5.9 | 3.16 | 68.1 | 83.1 | 4.99 | 0 | 4.99 | 5.9 | 45 | 39.29 | -40.01 | 0 | 0 | 0 | Battery-supported
2025-11-30 03:00 | 334 | 11 | Spring | 3 | 24 | -6.1 | 1.76 | 77.1 | 105.9 | 6.35 | 0 | 6.35 | 6.1 | 45 | 23.83 | -38.65 | 0 | 0 | 0 | Battery-supported
2025-11-30 04:00 | 334 | 11 | Spring | 4 | 24 | -0.8 | 13.54 | 74.9 | 143.9 | 8.63 | 120 | 128.63 | 0.8 | 45 | 54.6 | 83.63 | 0 | 0 | 0 | Normal
2025-11-30 05:00 | 334 | 11 | Spring | 5 | 24 | -8.5 | 5.73 | 80.7 | 157.6 | 9.46 | 1.55 | 11.01 | 8.5 | 45 | 41.01 | -33.99 | 0 | 0 | 0 | Battery-supported
2025-11-30 06:00 | 334 | 11 | Spring | 6 | 24 | -4.9 | 5.43 | 50.2 | 289.2 | 17.35 | 1.01 | 18.36 | 4.9 | 45 | 30.35 | -26.64 | 0 | 0 | 0 | Battery-supported
2025-11-30 07:00 | 334 | 11 | Spring | 7 | 24 | -5.5 | 9.38 | 68.3 | 254 | 15.24 | 28.45 | 43.69 | 5.5 | 45 | 29.83 | -1.31 | 0 | 0 | 0 | Battery-supported
2025-11-30 08:00 | 334 | 11 | Spring | 8 | 24 | -5.3 | 4.12 | 50.1 | 354.6 | 21.28 | 0.03 | 21.31 | 5.3 | 52.28 | 17.44 | -30.97 | 0 | 0 | 0 | Battery-supported
2025-11-30 09:00 | 334 | 11 | Spring | 9 | 24 | -3.3 | 5.35 | 75.6 | 262.2 | 15.73 | 0.89 | 16.62 | 3.3 | 47.84 | 15 | -6.1 | 25.12 | 8.678 | 0 | Diesel-backup
2025-11-30 10:00 | 334 | 11 | Spring | 10 | 24 | -3.2 | 3.2 | 71.7 | 292.7 | 17.56 | 0 | 17.56 | 3.2 | 47.93 | 15 | 0 | 30.37 | 10.287 | 0 | Diesel-backup
2025-11-30 11:00 | 334 | 11 | Spring | 11 | 24 | -6.6 | 2.02 | 23.9 | 533.6 | 32.02 | 0 | 32.02 | 6.6 | 51.08 | 15 | 0 | 19.06 | 6.732 | 0 | Diesel-backup
2025-11-30 12:00 | 334 | 11 | Spring | 12 | 24 | -4.9 | 5.3 | 39.2 | 463.1 | 27.79 | 0.82 | 28.61 | 4.9 | 45 | 15 | 0 | 16.39 | 5.845 | 0 | Diesel-backup
2025-11-30 13:00 | 334 | 11 | Spring | 13 | 24 | -9.1 | 4.09 | 15.5 | 574.9 | 34.49 | 0.03 | 34.52 | 9.1 | 51.2 | 15 | 0 | 16.68 | 5.942 | 0 | Diesel-backup
2025-11-30 14:00 | 334 | 11 | Spring | 14 | 24 | -4.4 | 3.75 | 66.9 | 315.7 | 18.94 | 0 | 18.94 | 4.4 | 51.01 | 15 | 0 | 32.07 | 10.793 | 0 | Diesel-backup
2025-11-30 15:00 | 334 | 11 | Spring | 15 | 24 | -5.9 | 7.39 | 75.9 | 261.1 | 15.67 | 8.24 | 23.91 | 5.9 | 45 | 15 | 0 | 21.09 | 7.394 | 0 | Diesel-backup
2025-11-30 16:00 | 334 | 11 | Spring | 16 | 24 | -4.2 | 11.27 | 57.6 | 322.7 | 19.36 | 65.66 | 85.02 | 4.2 | 45 | 29.73 | 40.02 | 0 | 0 | 0 | Normal
2025-11-30 17:00 | 334 | 11 | Spring | 17 | 24 | -7.2 | 11.39 | 30.2 | 402.5 | 24.15 | 68.75 | 92.9 | 7.2 | 45.46 | 47.19 | 47.44 | 0 | 0 | 0 | Normal
2025-11-30 18:00 | 334 | 11 | Spring | 18 | 24 | -2.4 | 11.13 | 10.2 | 428.4 | 25.7 | 62.17 | 87.87 | 2.4 | 45 | 62.96 | 42.87 | 0 | 0 | 0 | Normal
2025-11-30 19:00 | 334 | 11 | Spring | 19 | 24 | -6.9 | 4.5 | 23.9 | 327.7 | 19.66 | 0.14 | 19.8 | 6.9 | 49.62 | 51.03 | -29.82 | 0 | 0 | 0 | Battery-supported
2025-11-30 20:00 | 334 | 11 | Spring | 20 | 24 | -2.7 | 6.95 | 96.1 | 91.6 | 5.5 | 5.75 | 11.25 | 2.7 | 45 | 37.53 | -33.75 | 0 | 0 | 0 | Battery-supported
2025-11-30 21:00 | 334 | 11 | Spring | 21 | 24 | -5.8 | 5.16 | 56.9 | 144 | 8.64 | 0.64 | 9.28 | 5.8 | 45 | 23.25 | -35.72 | 0 | 0 | 0 | Battery-supported
2025-11-30 22:00 | 334 | 11 | Spring | 22 | 24 | -5.1 | 4.54 | 68 | 83.2 | 4.99 | 0.16 | 5.15 | 5.1 | 48.58 | 15 | -20.61 | 22.82 | 7.949 | 0 | Diesel-backup
2025-11-30 23:00 | 334 | 11 | Spring | 23 | 24 | -1 | 4.72 | 29.9 | 66.4 | 3.98 | 0.25 | 4.23 | 1 | 45 | 15 | 0 | 40.77 | 13.267 | 0 | Diesel-backup
2025-12-01 | 335 | 12 | Summer | 0 | 24 | -2.4 | 3.53 | 32.5 | 0 | 0 | 0 | 0 | 2.4 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-12-01 01:00 | 335 | 12 | Summer | 1 | 24 | -1.5 | 8.39 | 91 | 27.2 | 1.63 | 16.37 | 18 | 1.5 | 45 | 15 | 0 | 27 | 9.262 | 0 | Diesel-backup
2025-12-01 02:00 | 335 | 12 | Summer | 2 | 24 | -1 | 13.1 | 18.4 | 146.3 | 8.78 | 120 | 128.78 | 1 | 45 | 45.83 | 83.78 | 0 | 0 | 0 | Normal
2025-12-01 03:00 | 335 | 12 | Summer | 3 | 24 | -6.5 | 5.06 | 24.8 | 204.3 | 12.26 | 0.53 | 12.79 | 6.5 | 45 | 32.95 | -32.21 | 0 | 0 | 0 | Battery-supported
2025-12-01 04:00 | 335 | 12 | Summer | 4 | 24 | -1.9 | 4.72 | 60.1 | 180 | 10.8 | 0.25 | 11.05 | 1.9 | 45 | 19.37 | -33.95 | 0 | 0 | 0 | Battery-supported
2025-12-01 05:00 | 335 | 12 | Summer | 5 | 24 | -8.7 | 1.71 | 55.2 | 233.9 | 14.03 | 0 | 14.03 | 8.7 | 45 | 15 | -10.92 | 20.05 | 7.057 | 0 | Diesel-backup
2025-12-01 06:00 | 335 | 12 | Summer | 6 | 24 | -4.1 | 10.12 | 46.6 | 301.6 | 18.1 | 40.61 | 58.71 | 4.1 | 45 | 20.05 | 13.71 | 0 | 0 | 0 | Normal
2025-12-01 07:00 | 335 | 12 | Summer | 7 | 24 | -7 | 1.43 | 45.3 | 343.6 | 20.62 | 0 | 20.62 | 7 | 51.83 | 15 | -12.61 | 18.6 | 6.579 | 0 | Diesel-backup
2025-12-01 08:00 | 335 | 12 | Summer | 8 | 24 | -8 | 7.57 | 19.3 | 485.8 | 29.15 | 9.44 | 38.59 | 8 | 48.96 | 15 | 0 | 10.37 | 3.778 | 0 | Diesel-backup
2025-12-01 09:00 | 335 | 12 | Summer | 9 | 24 | -4.5 | 4.24 | 5.1 | 582.9 | 34.97 | 0.06 | 35.03 | 4.5 | 47.02 | 15 | 0 | 11.99 | 4.343 | 0 | Diesel-backup
2025-12-01 10:00 | 335 | 12 | Summer | 10 | 24 | -3.6 | 6.13 | 37.9 | 453.4 | 27.2 | 2.55 | 29.75 | 3.6 | 47.97 | 15 | 0 | 18.22 | 6.455 | 0 | Diesel-backup
2025-12-01 11:00 | 335 | 12 | Summer | 11 | 24 | -3.5 | 7.83 | 15.9 | 573 | 34.38 | 11.36 | 45.74 | 3.5 | 56.06 | 15 | 0 | 10.32 | 3.761 | 0 | Diesel-backup
2025-12-01 12:00 | 335 | 12 | Summer | 12 | 24 | -4.7 | 7.55 | 43.2 | 443.3 | 26.6 | 9.3 | 35.9 | 4.7 | 50.69 | 15 | 0 | 14.79 | 5.305 | 0 | Diesel-backup
2025-12-01 13:00 | 335 | 12 | Summer | 13 | 24 | -4.5 | 12.21 | 17.6 | 564.2 | 33.85 | 92.48 | 126.33 | 4.5 | 47.49 | 44.01 | 78.84 | 0 | 0 | 0 | Normal
2025-12-01 14:00 | 335 | 12 | Summer | 14 | 24 | -3.3 | 1.48 | 39.2 | 447.4 | 26.84 | 0 | 26.84 | 3.3 | 45 | 36.75 | -18.16 | 0 | 0 | 0 | Battery-supported
2025-12-01 15:00 | 335 | 12 | Summer | 15 | 24 | -3.4 | 11.39 | 2.9 | 592.7 | 35.56 | 68.75 | 104.31 | 3.4 | 51.35 | 56.24 | 52.96 | 0 | 0 | 0 | Normal
2025-12-01 16:00 | 335 | 12 | Summer | 16 | 24 | -2.5 | 8.02 | 52.1 | 345.9 | 20.75 | 12.92 | 33.67 | 2.5 | 45 | 51.71 | -11.33 | 0 | 0 | 0 | Battery-supported
2025-12-01 17:00 | 335 | 12 | Summer | 17 | 24 | -2.9 | 12.93 | 32 | 395.3 | 23.72 | 117.37 | 141.09 | 2.9 | 51.57 | 84.65 | 89.52 | 0 | 0 | 0 | Normal
2025-12-01 18:00 | 335 | 12 | Summer | 18 | 24 | -1.3 | 7.26 | 40.3 | 323.6 | 19.42 | 7.44 | 26.86 | 1.3 | 45 | 77.39 | -18.14 | 0 | 0 | 0 | Battery-supported
2025-12-01 19:00 | 335 | 12 | Summer | 19 | 24 | -6.6 | 2.63 | 71 | 186.6 | 11.2 | 0 | 11.2 | 6.6 | 46.78 | 63.16 | -35.58 | 0 | 0 | 0 | Battery-supported
2025-12-01 20:00 | 335 | 12 | Summer | 20 | 24 | -3.2 | 6.65 | 21 | 276.3 | 16.58 | 4.37 | 20.95 | 3.2 | 45 | 53.54 | -24.05 | 0 | 0 | 0 | Battery-supported
2025-12-01 21:00 | 335 | 12 | Summer | 21 | 24 | -6 | 9.95 | 23.8 | 206.3 | 12.38 | 37.56 | 49.94 | 6 | 45 | 55.36 | 4.94 | 0 | 0 | 0 | Normal
2025-12-01 22:00 | 335 | 12 | Summer | 22 | 24 | -2.5 | 10.97 | 38.7 | 120.5 | 7.23 | 58.34 | 65.57 | 2.5 | 45 | 62.93 | 20.57 | 0 | 0 | 0 | Normal
2025-12-01 23:00 | 335 | 12 | Summer | 23 | 24 | 0.2 | 6.79 | 37.5 | 61.6 | 3.7 | 4.98 | 8.68 | 0 | 45 | 48.4 | -36.32 | 0 | 0 | 0 | Battery-supported
2025-12-02 | 336 | 12 | Summer | 0 | 24 | -4.6 | 6.28 | 40.7 | 0 | 0 | 3.01 | 3.01 | 4.6 | 45 | 31.61 | -41.99 | 0 | 0 | 0 | Battery-supported
2025-12-02 01:00 | 336 | 12 | Summer | 1 | 24 | -3.6 | 7.92 | 100 | 21.4 | 1.28 | 12.09 | 13.37 | 3.6 | 45 | 18.95 | -31.63 | 0 | 0 | 0 | Battery-supported
2025-12-02 02:00 | 336 | 12 | Summer | 2 | 24 | -2.6 | 11.96 | 49.4 | 106.9 | 6.41 | 84.75 | 91.16 | 2.6 | 45 | 35.94 | 46.16 | 0 | 0 | 0 | Normal
2025-12-02 03:00 | 336 | 12 | Summer | 3 | 24 | -9.2 | 5.34 | 41.4 | 173.1 | 10.39 | 0.87 | 11.26 | 9.2 | 47.59 | 21.41 | -36.33 | 0 | 0 | 0 | Battery-supported
2025-12-02 04:00 | 336 | 12 | Summer | 4 | 24 | -6.2 | 9 | 86.4 | 115.4 | 6.92 | 23.29 | 30.21 | 6.2 | 45 | 15.49 | -14.79 | 0 | 0 | 0 | Battery-supported
2025-12-02 05:00 | 336 | 12 | Summer | 5 | 24 | -4.5 | 17.67 | 56.4 | 230.3 | 13.82 | 120 | 133.82 | 4.5 | 45 | 48.18 | 88.82 | 0 | 0 | 0 | Normal
2025-12-02 06:00 | 336 | 12 | Summer | 6 | 24 | -12 | 24.11 | 76.3 | 198.4 | 11.9 | 120 | 131.9 | 12 | 47.84 | 79.11 | 84.06 | 0 | 0 | 0 | Normal
2025-12-02 07:00 | 336 | 12 | Summer | 7 | 24 | -7.9 | 11.92 | 87 | 181 | 10.86 | 83.55 | 94.41 | 7.9 | 45.2 | 95 | 43.17 | 0 | 0 | 0 | Normal
2025-12-02 08:00 | 336 | 12 | Summer | 8 | 24 | -3.4 | 6.16 | 41.5 | 391.1 | 23.47 | 2.63 | 26.1 | 3.4 | 52.27 | 84.53 | -26.17 | 0 | 0 | 0 | Battery-supported
2025-12-02 09:00 | 336 | 12 | Summer | 9 | 24 | -3.5 | 3.14 | 25.8 | 488.7 | 29.32 | 0 | 29.32 | 3.5 | 45 | 78.26 | -15.68 | 0 | 0 | 0 | Battery-supported
2025-12-02 10:00 | 336 | 12 | Summer | 10 | 24 | -4.8 | 8.73 | 42.2 | 433 | 25.98 | 20.02 | 46 | 4.8 | 47.99 | 77.46 | -1.99 | 0 | 0 | 0 | Battery-supported
2025-12-02 11:00 | 336 | 12 | Summer | 11 | 24 | -3.4 | 15.51 | 49.3 | 410 | 24.6 | 120 | 144.6 | 3.4 | 45 | 95 | 47.65 | 0 | 0 | 0 | Normal
2025-12-02 12:00 | 336 | 12 | Summer | 12 | 24 | -4.6 | 6.78 | 24.2 | 536.9 | 32.21 | 4.94 | 37.15 | 4.6 | 52.64 | 88.8 | -15.49 | 0 | 0 | 0 | Battery-supported
2025-12-02 13:00 | 336 | 12 | Summer | 13 | 24 | -3.4 | 12.7 | 86.2 | 230 | 13.8 | 108.99 | 122.79 | 3.4 | 45 | 95 | 16.84 | 0 | 0 | 0 | Normal
2025-12-02 14:00 | 336 | 12 | Summer | 14 | 24 | -5 | 12.14 | 63.3 | 332.6 | 19.96 | 90.27 | 110.23 | 5 | 47.79 | 95 | 0 | 0 | 0 | 0 | Normal
2025-12-02 15:00 | 336 | 12 | Summer | 15 | 24 | -3.6 | 7.23 | 35.3 | 445.5 | 26.73 | 7.26 | 33.99 | 3.6 | 45 | 90.6 | -11.01 | 0 | 0 | 0 | Battery-supported
2025-12-02 16:00 | 336 | 12 | Summer | 16 | 24 | -4.9 | 11.53 | 46.6 | 369.4 | 22.16 | 72.47 | 94.63 | 4.9 | 45 | 95 | 11.97 | 0 | 0 | 0 | Normal
2025-12-02 17:00 | 336 | 12 | Summer | 17 | 24 | -0.4 | 3.39 | 53.2 | 312.8 | 18.77 | 0 | 18.77 | 0.4 | 45.99 | 84.11 | -27.22 | 0 | 0 | 0 | Battery-supported
2025-12-02 18:00 | 336 | 12 | Summer | 18 | 24 | 0.4 | 6.36 | 31.7 | 353.6 | 21.22 | 3.27 | 24.49 | 0 | 45 | 75.91 | -20.51 | 0 | 0 | 0 | Battery-supported
2025-12-02 19:00 | 336 | 12 | Summer | 19 | 24 | 0.2 | 9.31 | 52.2 | 242.9 | 14.57 | 27.45 | 42.02 | 0 | 45 | 74.72 | -2.98 | 0 | 0 | 0 | Battery-supported
2025-12-02 20:00 | 336 | 12 | Summer | 20 | 24 | -3.7 | 7.12 | 98.5 | 85.7 | 5.14 | 6.64 | 11.78 | 3.7 | 53.21 | 58.14 | -41.43 | 0 | 0 | 0 | Battery-supported
2025-12-02 21:00 | 336 | 12 | Summer | 21 | 24 | -4.9 | 3.62 | 31.3 | 192.1 | 11.53 | 0 | 11.53 | 4.9 | 45 | 44.76 | -33.47 | 0 | 0 | 0 | Battery-supported
2025-12-02 22:00 | 336 | 12 | Summer | 22 | 24 | -0.2 | 11.54 | 37.5 | 122.1 | 7.33 | 72.74 | 80.07 | 0.2 | 45 | 57.66 | 35.07 | 0 | 0 | 0 | Normal
2025-12-02 23:00 | 336 | 12 | Summer | 23 | 24 | -2 | 9.24 | 70.5 | 40.3 | 2.42 | 26.47 | 28.89 | 2 | 45 | 51.22 | -16.11 | 0 | 0 | 0 | Battery-supported
2025-12-03 | 337 | 12 | Summer | 0 | 24 | -2.7 | 7.95 | 51.6 | 0 | 0 | 12.33 | 12.33 | 2.7 | 45 | 38.15 | -32.67 | 0 | 0 | 0 | Battery-supported
2025-12-03 01:00 | 337 | 12 | Summer | 1 | 24 | -5.1 | 14.17 | 3.5 | 83.4 | 5 | 120 | 125 | 5.1 | 45 | 67.59 | 80 | 0 | 0 | 0 | Normal
2025-12-03 02:00 | 337 | 12 | Summer | 2 | 24 | -3.2 | 11.64 | 4.6 | 163.9 | 9.83 | 75.49 | 85.32 | 3.2 | 45 | 82.43 | 40.32 | 0 | 0 | 0 | Normal
2025-12-03 03:00 | 337 | 12 | Summer | 3 | 24 | -6.9 | 1.08 | 42 | 172 | 10.32 | 0 | 10.32 | 6.9 | 45 | 68.56 | -34.68 | 0 | 0 | 0 | Battery-supported
2025-12-03 04:00 | 337 | 12 | Summer | 4 | 24 | -3.5 | 8.03 | 71.2 | 152.9 | 9.17 | 13.01 | 22.18 | 3.5 | 45 | 59.43 | -22.82 | 0 | 0 | 0 | Battery-supported
2025-12-03 05:00 | 337 | 12 | Summer | 5 | 24 | -2.2 | 7.88 | 43.8 | 268.1 | 16.09 | 11.76 | 27.85 | 2.2 | 45 | 52.57 | -17.15 | 0 | 0 | 0 | Battery-supported
2025-12-03 06:00 | 337 | 12 | Summer | 6 | 24 | -1.9 | 5.81 | 30.5 | 357.9 | 21.47 | 1.73 | 23.2 | 1.9 | 45 | 43.85 | -21.8 | 0 | 0 | 0 | Battery-supported
2025-12-03 07:00 | 337 | 12 | Summer | 7 | 24 | -4 | 1.48 | 14.1 | 465.5 | 27.93 | 0 | 27.93 | 4 | 45 | 37.02 | -17.07 | 0 | 0 | 0 | Battery-supported
2025-12-03 08:00 | 337 | 12 | Summer | 8 | 24 | -8.7 | 4.35 | 37.7 | 407.4 | 24.44 | 0.09 | 24.53 | 8.7 | 58.24 | 23.54 | -33.71 | 0 | 0 | 0 | Battery-supported
2025-12-03 09:00 | 337 | 12 | Summer | 9 | 24 | -5.2 | 1.22 | 26.6 | 485.2 | 29.11 | 0 | 29.11 | 5.2 | 50.42 | 15.01 | -21.31 | 0 | 0 | 0 | Battery-supported
2025-12-03 10:00 | 337 | 12 | Summer | 10 | 24 | -0.7 | 20.99 | 24.1 | 519.1 | 31.15 | 120 | 151.15 | 0.7 | 45.84 | 53.77 | 105.31 | 0 | 0 | 0 | Normal
2025-12-03 11:00 | 337 | 12 | Summer | 11 | 24 | -7.1 | 7.12 | 67.4 | 321.6 | 19.3 | 6.64 | 25.94 | 7.1 | 50.51 | 43.94 | -24.57 | 0 | 0 | 0 | Battery-supported
2025-12-03 12:00 | 337 | 12 | Summer | 12 | 24 | -5 | 9.57 | 8.1 | 616.2 | 36.97 | 31.3 | 68.27 | 5 | 51.05 | 50.27 | 17.22 | 0 | 0 | 0 | Normal
2025-12-03 13:00 | 337 | 12 | Summer | 13 | 24 | -1.4 | 3.57 | 47.5 | 418.7 | 25.12 | 0 | 25.12 | 1.4 | 46.25 | 41.82 | -21.13 | 0 | 0 | 0 | Battery-supported
2025-12-03 14:00 | 337 | 12 | Summer | 14 | 24 | -2.8 | 1.62 | 36.9 | 458.3 | 27.5 | 0 | 27.5 | 2.8 | 45 | 34.82 | -17.5 | 0 | 0 | 0 | Battery-supported
2025-12-03 15:00 | 337 | 12 | Summer | 15 | 24 | 1.7 | 5.55 | 21.5 | 508.5 | 30.51 | 1.21 | 31.72 | 0 | 50.46 | 27.33 | -18.74 | 0 | 0 | 0 | Battery-supported
2025-12-03 16:00 | 337 | 12 | Summer | 16 | 24 | -5 | 5.07 | 57.7 | 322.3 | 19.34 | 0.54 | 19.88 | 5 | 54.8 | 15 | -30.82 | 4.1 | 1.528 | 0 | Diesel-backup
2025-12-03 17:00 | 337 | 12 | Summer | 17 | 24 | -5.3 | 8.28 | 32.8 | 392.5 | 23.55 | 15.29 | 38.84 | 5.3 | 46.28 | 15 | 0 | 7.44 | 2.738 | 0 | Diesel-backup
2025-12-03 18:00 | 337 | 12 | Summer | 18 | 24 | -0.1 | 5.71 | 43.6 | 312 | 18.72 | 1.51 | 20.23 | 0.1 | 45 | 15 | 0 | 24.77 | 8.568 | 0 | Diesel-backup
2025-12-03 19:00 | 337 | 12 | Summer | 19 | 24 | -5.3 | 23.56 | 55.6 | 232.9 | 13.97 | 120 | 133.97 | 5.3 | 45 | 47.74 | 88.97 | 0 | 0 | 0 | Normal
2025-12-03 20:00 | 337 | 12 | Summer | 20 | 24 | -3.1 | 12.98 | 19.4 | 280.2 | 16.81 | 119.24 | 136.05 | 3.1 | 45 | 81.25 | 91.05 | 0 | 0 | 0 | Normal
2025-12-03 21:00 | 337 | 12 | Summer | 21 | 24 | -2.8 | 16.19 | 70.4 | 118.5 | 7.11 | 120 | 127.11 | 2.8 | 45 | 95 | 37.37 | 0 | 0 | 0 | Normal
2025-12-03 22:00 | 337 | 12 | Summer | 22 | 24 | -0.6 | 7.15 | 16.2 | 149.1 | 8.95 | 6.81 | 15.76 | 0.6 | 45 | 83.3 | -29.24 | 0 | 0 | 0 | Battery-supported
2025-12-03 23:00 | 337 | 12 | Summer | 23 | 24 | -1.7 | 8.18 | 86.6 | 30 | 1.8 | 14.35 | 16.15 | 1.7 | 45 | 71.76 | -28.85 | 0 | 0 | 0 | Battery-supported
2025-12-04 | 338 | 12 | Summer | 0 | 24 | -2.2 | 15.32 | 0 | 0 | 0 | 120 | 120 | 2.2 | 45 | 95 | 63.14 | 0 | 0 | 0 | Normal
2025-12-04 01:00 | 338 | 12 | Summer | 1 | 24 | -4.5 | 5.42 | 21.1 | 72.1 | 4.33 | 0.99 | 5.32 | 4.5 | 45 | 79.13 | -39.68 | 0 | 0 | 0 | Battery-supported
2025-12-04 02:00 | 338 | 12 | Summer | 2 | 24 | -1.3 | 9.26 | 16.7 | 148.6 | 8.92 | 26.75 | 35.67 | 1.3 | 45 | 75.4 | -9.33 | 0 | 0 | 0 | Battery-supported
2025-12-04 03:00 | 338 | 12 | Summer | 3 | 24 | 4.5 | 5.69 | 80.6 | 99.2 | 5.95 | 1.47 | 7.42 | 0 | 45 | 60.36 | -37.58 | 0 | 0 | 0 | Battery-supported
2025-12-04 04:00 | 338 | 12 | Summer | 4 | 24 | -3.2 | 9.56 | 44.6 | 218.3 | 13.1 | 31.15 | 44.25 | 3.2 | 45 | 60.06 | -0.75 | 0 | 0 | 0 | Battery-supported
2025-12-04 05:00 | 338 | 12 | Summer | 5 | 24 | -4.8 | 2.85 | 15.7 | 352.3 | 21.14 | 0 | 21.14 | 4.8 | 48.67 | 49.05 | -27.53 | 0 | 0 | 0 | Battery-supported
2025-12-04 06:00 | 338 | 12 | Summer | 6 | 24 | -8.2 | 4.9 | 28.5 | 364.5 | 21.87 | 0.38 | 22.25 | 8.2 | 45 | 39.95 | -22.75 | 0 | 0 | 0 | Battery-supported
2025-12-04 07:00 | 338 | 12 | Summer | 7 | 24 | -6.9 | 8.26 | 56.6 | 299.5 | 17.97 | 15.09 | 33.06 | 6.9 | 45 | 35.18 | -11.94 | 0 | 0 | 0 | Battery-supported
2025-12-04 08:00 | 338 | 12 | Summer | 8 | 24 | -6 | 8.85 | 82.9 | 215 | 12.9 | 21.43 | 34.33 | 6 | 48.65 | 29.45 | -14.32 | 0 | 0 | 0 | Battery-supported
2025-12-04 09:00 | 338 | 12 | Summer | 9 | 24 | -6.6 | 10.85 | 63.6 | 317 | 19.02 | 55.57 | 74.59 | 6.6 | 53.75 | 37.12 | 20.84 | 0 | 0 | 0 | Normal
2025-12-04 10:00 | 338 | 12 | Summer | 10 | 24 | -5.3 | 3.25 | 75 | 277.1 | 16.63 | 0 | 16.63 | 5.3 | 51.7 | 23.09 | -35.07 | 0 | 0 | 0 | Battery-supported
2025-12-04 11:00 | 338 | 12 | Summer | 11 | 24 | -1.2 | 8.07 | 16 | 572.5 | 34.35 | 13.36 | 47.71 | 1.2 | 45 | 24.09 | 2.71 | 0 | 0 | 0 | Normal
2025-12-04 12:00 | 338 | 12 | Summer | 12 | 24 | -2 | 2.28 | 52.5 | 397.5 | 23.85 | 0 | 23.85 | 2 | 47.14 | 15 | -22.72 | 0.57 | 0.216 | 0 | Diesel-backup
2025-12-04 13:00 | 338 | 12 | Summer | 13 | 24 | -4.7 | 5.9 | 82.3 | 249 | 14.94 | 1.93 | 16.87 | 4.7 | 46.06 | 15 | 0 | 29.19 | 9.932 | 0 | Diesel-backup
2025-12-04 14:00 | 338 | 12 | Summer | 14 | 24 | -6.7 | 7.27 | 80.5 | 250.8 | 15.05 | 7.5 | 22.55 | 6.7 | 50.72 | 15 | 0 | 28.17 | 9.621 | 0 | Diesel-backup
2025-12-04 15:00 | 338 | 12 | Summer | 15 | 24 | -0.7 | 6.62 | 58.5 | 339.9 | 20.39 | 4.25 | 24.64 | 0.7 | 45 | 15 | 0 | 20.36 | 7.157 | 0 | Diesel-backup
2025-12-04 16:00 | 338 | 12 | Summer | 16 | 24 | -3.4 | 17.31 | 63.5 | 297.7 | 17.86 | 120 | 137.86 | 3.4 | 45 | 49.17 | 92.86 | 0 | 0 | 0 | Normal
2025-12-04 17:00 | 338 | 12 | Summer | 17 | 24 | -6.7 | 7.31 | 30.1 | 403 | 24.18 | 7.74 | 31.92 | 6.7 | 45 | 43.94 | -13.08 | 0 | 0 | 0 | Battery-supported
2025-12-04 18:00 | 338 | 12 | Summer | 18 | 24 | -1.1 | 9.98 | 61 | 251.5 | 15.09 | 38.08 | 53.17 | 1.1 | 45 | 46.95 | 8.17 | 0 | 0 | 0 | Normal
2025-12-04 19:00 | 338 | 12 | Summer | 19 | 24 | -0.3 | 8.28 | 88.2 | 135.2 | 8.11 | 15.29 | 23.4 | 0.3 | 45 | 38.31 | -21.6 | 0 | 0 | 0 | Battery-supported
2025-12-04 20:00 | 338 | 12 | Summer | 20 | 24 | -7.8 | 7.03 | 61.5 | 176.7 | 10.6 | 6.16 | 16.76 | 7.8 | 50.17 | 24.94 | -33.41 | 0 | 0 | 0 | Battery-supported
2025-12-04 21:00 | 338 | 12 | Summer | 21 | 24 | -4.4 | 9.56 | 74.6 | 110.5 | 6.63 | 31.15 | 37.78 | 4.4 | 45 | 22.06 | -7.22 | 0 | 0 | 0 | Battery-supported
2025-12-04 22:00 | 338 | 12 | Summer | 22 | 24 | -2.9 | 7.85 | 41.9 | 116.4 | 6.98 | 11.52 | 18.5 | 2.9 | 45 | 15 | -17.64 | 8.86 | 3.246 | 0 | Diesel-backup
2025-12-04 23:00 | 338 | 12 | Summer | 23 | 24 | -1.3 | 7.45 | 13.3 | 77.1 | 4.63 | 8.63 | 13.26 | 1.3 | 45 | 15 | 0 | 31.74 | 10.696 | 0 | Diesel-backup
2025-12-05 | 339 | 12 | Summer | 0 | 24 | -4.3 | 6.22 | 64.4 | 0 | 0 | 2.82 | 2.82 | 4.3 | 45 | 15 | 0 | 42.18 | 13.65 | 0 | Diesel-backup
2025-12-05 01:00 | 339 | 12 | Summer | 1 | 24 | -5.3 | 5.4 | 27.2 | 68.1 | 4.09 | 0.96 | 5.05 | 5.3 | 45 | 15 | 0 | 39.95 | 13.042 | 0 | Diesel-backup
2025-12-05 02:00 | 339 | 12 | Summer | 2 | 24 | -2.3 | 4.94 | 68.3 | 82.8 | 4.97 | 0.42 | 5.39 | 2.3 | 45 | 15 | 0 | 39.61 | 12.948 | 0 | Diesel-backup
2025-12-05 03:00 | 339 | 12 | Summer | 3 | 24 | -5.3 | 7.43 | 62 | 134.3 | 8.06 | 8.5 | 16.56 | 5.3 | 45 | 15 | 0 | 28.44 | 9.704 | 0 | Diesel-backup
2025-12-05 04:00 | 339 | 12 | Summer | 4 | 24 | -3.4 | 7.12 | 13.8 | 294.1 | 17.65 | 6.64 | 24.29 | 3.4 | 45 | 15 | 0 | 20.71 | 7.271 | 0 | Diesel-backup
2025-12-05 05:00 | 339 | 12 | Summer | 5 | 24 | -7.4 | 15.02 | 54 | 237.7 | 14.26 | 120 | 134.26 | 7.4 | 45 | 47.85 | 89.26 | 0 | 0 | 0 | Normal
2025-12-05 06:00 | 339 | 12 | Summer | 6 | 24 | -8.1 | 2.62 | 45.4 | 305.9 | 18.35 | 0 | 18.35 | 8.1 | 45 | 37.19 | -26.65 | 0 | 0 | 0 | Battery-supported
2025-12-05 07:00 | 339 | 12 | Summer | 7 | 24 | -3.7 | 18.02 | 81.8 | 201 | 12.06 | 120 | 132.06 | 3.7 | 45 | 69.23 | 87.06 | 0 | 0 | 0 | Normal
2025-12-05 08:00 | 339 | 12 | Summer | 8 | 24 | -4.8 | 3.3 | 58.6 | 318.4 | 19.1 | 0 | 19.1 | 4.8 | 45.19 | 58.79 | -26.09 | 0 | 0 | 0 | Battery-supported
2025-12-05 09:00 | 339 | 12 | Summer | 9 | 24 | -3.3 | 6.96 | 79.1 | 246.6 | 14.8 | 5.8 | 20.6 | 3.3 | 48.21 | 47.75 | -27.61 | 0 | 0 | 0 | Battery-supported
2025-12-05 10:00 | 339 | 12 | Summer | 10 | 24 | -6.3 | 8.88 | 26.7 | 506.5 | 30.39 | 21.8 | 52.19 | 6.3 | 45 | 50.39 | 7.19 | 0 | 0 | 0 | Normal
2025-12-05 11:00 | 339 | 12 | Summer | 11 | 24 | -6.7 | 3.81 | 64.4 | 336.3 | 20.18 | 0 | 20.18 | 6.7 | 49.53 | 38.65 | -29.35 | 0 | 0 | 0 | Battery-supported
2025-12-05 12:00 | 339 | 12 | Summer | 12 | 24 | -1.6 | 3.25 | 58.7 | 367.1 | 22.03 | 0 | 22.03 | 1.6 | 45 | 29.46 | -22.97 | 0 | 0 | 0 | Battery-supported
2025-12-05 13:00 | 339 | 12 | Summer | 13 | 24 | -7.6 | 6.49 | 62.5 | 345.3 | 20.72 | 3.74 | 24.46 | 7.6 | 46.12 | 20.8 | -21.66 | 0 | 0 | 0 | Battery-supported
2025-12-05 14:00 | 339 | 12 | Summer | 14 | 24 | -1.1 | 10.1 | 32.7 | 478.3 | 28.7 | 40.24 | 68.94 | 1.1 | 46.58 | 29.03 | 22.36 | 0 | 0 | 0 | Normal
2025-12-05 15:00 | 339 | 12 | Summer | 15 | 24 | -0.6 | 11.66 | 5.5 | 581 | 34.86 | 76.05 | 110.91 | 0.6 | 48.05 | 52.16 | 62.86 | 0 | 0 | 0 | Normal
2025-12-05 16:00 | 339 | 12 | Summer | 16 | 24 | -1.2 | 2.92 | 64.8 | 291.8 | 17.51 | 0 | 17.51 | 1.2 | 45 | 41.16 | -27.49 | 0 | 0 | 0 | Battery-supported
2025-12-05 17:00 | 339 | 12 | Summer | 17 | 24 | -4.3 | 6.33 | 47.9 | 333.4 | 20 | 3.17 | 23.17 | 4.3 | 47.58 | 31.4 | -24.41 | 0 | 0 | 0 | Battery-supported
2025-12-05 18:00 | 339 | 12 | Summer | 18 | 24 | -4.4 | 2.01 | 57 | 265.5 | 15.93 | 0 | 15.93 | 4.4 | 46.23 | 19.28 | -30.3 | 0 | 0 | 0 | Battery-supported
2025-12-05 19:00 | 339 | 12 | Summer | 19 | 24 | -2.9 | 3.87 | 93.7 | 118.6 | 7.12 | 0.01 | 7.13 | 2.9 | 45.48 | 15 | -10.7 | 27.65 | 9.462 | 0 | Diesel-backup
2025-12-05 20:00 | 339 | 12 | Summer | 20 | 24 | -5.2 | 13.51 | 69.9 | 156.1 | 9.37 | 120 | 129.37 | 5.2 | 46.1 | 45.64 | 83.27 | 0 | 0 | 0 | Normal
2025-12-05 21:00 | 339 | 12 | Summer | 21 | 24 | -4.5 | 8.59 | 48.1 | 160.5 | 9.63 | 18.46 | 28.09 | 4.5 | 45 | 38.88 | -16.91 | 0 | 0 | 0 | Battery-supported
2025-12-05 22:00 | 339 | 12 | Summer | 22 | 24 | -1.1 | 4.1 | 45.6 | 111.7 | 6.7 | 0.03 | 6.73 | 1.1 | 45 | 23.57 | -38.27 | 0 | 0 | 0 | Battery-supported
2025-12-05 23:00 | 339 | 12 | Summer | 23 | 24 | -1.4 | 12.79 | 59.8 | 47.2 | 2.83 | 112.22 | 115.05 | 1.4 | 45 | 49.35 | 70.05 | 0 | 0 | 0 | Normal
2025-12-06 | 340 | 12 | Summer | 0 | 24 | -5.3 | 4.48 | 57.6 | 0 | 0 | 0.13 | 0.13 | 5.3 | 45 | 31.4 | -44.87 | 0 | 0 | 0 | Battery-supported
2025-12-06 01:00 | 340 | 12 | Summer | 1 | 24 | -1.9 | 6.85 | 69.6 | 40.9 | 2.45 | 5.26 | 7.71 | 1.9 | 45 | 16.49 | -37.29 | 0 | 0 | 0 | Battery-supported
2025-12-06 02:00 | 340 | 12 | Summer | 2 | 24 | -2.7 | 1.7 | 12.3 | 154.1 | 9.25 | 0 | 9.25 | 2.7 | 45 | 15 | -3.71 | 32.04 | 10.783 | 0 | Diesel-backup
2025-12-06 03:00 | 340 | 12 | Summer | 3 | 24 | -0.8 | 4.1 | 34 | 187 | 11.22 | 0.03 | 11.25 | 0.8 | 45 | 15 | 0 | 33.75 | 11.286 | 0 | Diesel-backup
2025-12-06 04:00 | 340 | 12 | Summer | 4 | 24 | -3.2 | 8.1 | 74.3 | 145.2 | 8.71 | 13.62 | 22.33 | 3.2 | 45 | 15 | 0 | 22.67 | 7.902 | 0 | Diesel-backup
2025-12-06 05:00 | 340 | 12 | Summer | 5 | 24 | -2.5 | 7.88 | 68.4 | 194.5 | 11.67 | 11.76 | 23.43 | 2.5 | 45 | 15 | 0 | 21.57 | 7.549 | 0 | Diesel-backup
2025-12-06 06:00 | 340 | 12 | Summer | 6 | 24 | -4 | 5.38 | 81.8 | 179.1 | 10.75 | 0.93 | 11.68 | 4 | 45 | 15 | 0 | 33.32 | 11.161 | 0 | Diesel-backup
2025-12-06 07:00 | 340 | 12 | Summer | 7 | 24 | -3 | 6.44 | 28.1 | 410.9 | 24.65 | 3.56 | 28.21 | 3 | 45 | 15 | 0 | 16.79 | 5.979 | 0 | Diesel-backup
2025-12-06 08:00 | 340 | 12 | Summer | 8 | 24 | -8.1 | 10.5 | 57.5 | 323.1 | 19.39 | 48.01 | 67.4 | 8.1 | 51.03 | 21.02 | 16.37 | 0 | 0 | 0 | Normal
2025-12-06 09:00 | 340 | 12 | Summer | 9 | 24 | -5.5 | 6.13 | 47.9 | 388.2 | 23.29 | 2.55 | 25.84 | 5.5 | 45 | 15 | -15.06 | 4.1 | 1.526 | 0 | Diesel-backup
2025-12-06 10:00 | 340 | 12 | Summer | 10 | 24 | -5.1 | 8.86 | 44.7 | 421.3 | 25.28 | 21.55 | 46.83 | 5.1 | 49.99 | 15 | 0 | 3.16 | 1.18 | 0 | Diesel-backup
2025-12-06 11:00 | 340 | 12 | Summer | 11 | 24 | -5.3 | 4.83 | 81.1 | 254.9 | 15.29 | 0.33 | 15.62 | 5.3 | 53.44 | 15 | 0 | 37.82 | 12.45 | 0 | Diesel-backup
2025-12-06 12:00 | 340 | 12 | Summer | 12 | 24 | -3.5 | 6.79 | 24.1 | 537.2 | 32.23 | 4.98 | 37.21 | 3.5 | 52 | 15 | 0 | 14.79 | 5.305 | 0 | Diesel-backup
2025-12-06 13:00 | 340 | 12 | Summer | 13 | 24 | -2.7 | 1.6 | 72 | 299 | 17.94 | 0 | 17.94 | 2.7 | 47.65 | 15 | 0 | 29.71 | 10.089 | 0 | Diesel-backup
2025-12-06 14:00 | 340 | 12 | Summer | 14 | 24 | -2.9 | 5.06 | 81.9 | 244.4 | 14.66 | 0.53 | 15.19 | 2.9 | 49.26 | 15 | 0 | 34.07 | 11.379 | 0 | Diesel-backup
2025-12-06 15:00 | 340 | 12 | Summer | 15 | 24 | -3.7 | 7.26 | 31 | 465 | 27.9 | 7.44 | 35.34 | 3.7 | 45 | 15 | 0 | 9.66 | 3.528 | 0 | Diesel-backup
2025-12-06 16:00 | 340 | 12 | Summer | 16 | 24 | -4.6 | 6.56 | 29.7 | 441.4 | 26.48 | 4.01 | 30.49 | 4.6 | 49.91 | 15 | 0 | 19.42 | 6.85 | 0 | Diesel-backup
2025-12-06 17:00 | 340 | 12 | Summer | 17 | 24 | -0.3 | 4.83 | 14.8 | 462.4 | 27.74 | 0.33 | 28.07 | 0.3 | 45.67 | 15 | 0 | 17.6 | 6.249 | 0 | Diesel-backup
2025-12-06 18:00 | 340 | 12 | Summer | 18 | 24 | -1.7 | 3.56 | 30.5 | 357.9 | 21.47 | 0 | 21.47 | 1.7 | 45 | 15 | 0 | 23.53 | 8.176 | 0 | Diesel-backup
2025-12-06 19:00 | 340 | 12 | Summer | 19 | 24 | -4.5 | 7.41 | 37 | 288.4 | 17.3 | 8.37 | 25.67 | 4.5 | 47.76 | 15 | 0 | 22.09 | 7.717 | 0 | Diesel-backup
2025-12-06 20:00 | 340 | 12 | Summer | 20 | 24 | -2.7 | 6.42 | 30.5 | 252.8 | 15.17 | 3.48 | 18.65 | 2.7 | 45 | 15 | 0 | 26.35 | 9.061 | 0 | Diesel-backup
2025-12-06 21:00 | 340 | 12 | Summer | 21 | 24 | -6.1 | 8.36 | 68.2 | 122.7 | 7.36 | 16.07 | 23.43 | 6.1 | 45 | 15 | 0 | 21.57 | 7.549 | 0 | Diesel-backup
2025-12-06 22:00 | 340 | 12 | Summer | 22 | 24 | -2.4 | 4.39 | 74.6 | 74.8 | 4.49 | 0.1 | 4.59 | 2.4 | 45 | 15 | 0 | 40.41 | 13.169 | 0 | Diesel-backup
2025-12-06 23:00 | 340 | 12 | Summer | 23 | 24 | -3.1 | 9.59 | 16.7 | 74.9 | 4.49 | 31.61 | 36.1 | 3.1 | 45.57 | 15 | 0 | 9.47 | 3.461 | 0 | Diesel-backup
2025-12-07 | 341 | 12 | Summer | 0 | 24 | -4.1 | 3.18 | 21.4 | 0 | 0 | 0 | 0 | 4.1 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-12-07 01:00 | 341 | 12 | Summer | 1 | 24 | 0.3 | 2.41 | 83.3 | 32.1 | 1.93 | 0 | 1.93 | 0 | 45 | 15 | 0 | 43.07 | 13.889 | 0 | Diesel-backup
2025-12-07 02:00 | 341 | 12 | Summer | 2 | 24 | -6.1 | 13.5 | 48 | 108.6 | 6.52 | 120 | 126.52 | 6.1 | 45 | 45 | 81.52 | 0 | 0 | 0 | Normal
2025-12-07 03:00 | 341 | 12 | Summer | 3 | 24 | -2.4 | 3.32 | 38.2 | 179.1 | 10.75 | 0 | 10.75 | 2.4 | 45 | 31.3 | -34.25 | 0 | 0 | 0 | Battery-supported
2025-12-07 04:00 | 341 | 12 | Summer | 4 | 24 | 0.5 | 7.42 | 39.7 | 230.4 | 13.82 | 8.43 | 22.25 | 0 | 45 | 22.2 | -22.75 | 0 | 0 | 0 | Battery-supported
2025-12-07 05:00 | 341 | 12 | Summer | 5 | 24 | -2.3 | 5.71 | 49 | 252.4 | 15.14 | 1.51 | 16.65 | 2.3 | 45 | 15 | -18 | 10.35 | 3.772 | 0 | Diesel-backup
2025-12-07 06:00 | 341 | 12 | Summer | 6 | 24 | -5 | 13.68 | 84.8 | 169 | 10.14 | 120 | 130.14 | 5 | 45 | 46.33 | 85.14 | 0 | 0 | 0 | Normal
2025-12-07 07:00 | 341 | 12 | Summer | 7 | 24 | -7.5 | 9.77 | 11.7 | 474.6 | 28.48 | 34.5 | 62.98 | 7.5 | 45 | 52.95 | 17.98 | 0 | 0 | 0 | Normal
2025-12-07 08:00 | 341 | 12 | Summer | 8 | 24 | -8.1 | 2.47 | 80.4 | 225.6 | 13.54 | 0 | 13.54 | 8.1 | 50.57 | 38.14 | -37.03 | 0 | 0 | 0 | Battery-supported
2025-12-07 09:00 | 341 | 12 | Summer | 9 | 24 | -6 | 15.95 | 83.6 | 225.9 | 13.55 | 120 | 133.55 | 6 | 45.23 | 70.64 | 88.32 | 0 | 0 | 0 | Normal
2025-12-07 10:00 | 341 | 12 | Summer | 10 | 24 | -6.4 | 11.73 | 39.8 | 444.2 | 26.65 | 78.02 | 104.67 | 6.4 | 52.13 | 89.97 | 52.54 | 0 | 0 | 0 | Normal
2025-12-07 11:00 | 341 | 12 | Summer | 11 | 24 | -6.2 | 5.29 | 73 | 294.1 | 17.65 | 0.8 | 18.45 | 6.2 | 45 | 79.35 | -26.55 | 0 | 0 | 0 | Battery-supported
2025-12-07 12:00 | 341 | 12 | Summer | 12 | 24 | -5.1 | 3.16 | 70.9 | 306.9 | 18.41 | 0 | 18.41 | 5.1 | 53.38 | 65.36 | -34.97 | 0 | 0 | 0 | Battery-supported
2025-12-07 13:00 | 341 | 12 | Summer | 13 | 24 | -4.2 | 7.73 | 43.5 | 438.3 | 26.3 | 10.59 | 36.89 | 4.2 | 47.62 | 61.07 | -10.73 | 0 | 0 | 0 | Battery-supported
2025-12-07 14:00 | 341 | 12 | Summer | 14 | 24 | -2.5 | 7.98 | 94 | 186.8 | 11.21 | 12.58 | 23.79 | 2.5 | 45 | 52.59 | -21.21 | 0 | 0 | 0 | Battery-supported
2025-12-07 15:00 | 341 | 12 | Summer | 15 | 24 | -5.9 | 1.81 | 59.3 | 336.4 | 20.18 | 0 | 20.18 | 5.9 | 45 | 42.66 | -24.82 | 0 | 0 | 0 | Battery-supported
2025-12-07 16:00 | 341 | 12 | Summer | 16 | 24 | -4.4 | 7.41 | 32.2 | 430.9 | 25.85 | 8.37 | 34.22 | 4.4 | 46.07 | 37.92 | -11.85 | 0 | 0 | 0 | Battery-supported
2025-12-07 17:00 | 341 | 12 | Summer | 17 | 24 | -2.9 | 11.2 | 17.2 | 453.3 | 27.2 | 63.9 | 91.1 | 2.9 | 45 | 54.89 | 46.1 | 0 | 0 | 0 | Normal
2025-12-07 18:00 | 341 | 12 | Summer | 18 | 24 | -2.7 | 7.18 | 90.2 | 150.1 | 9.01 | 6.98 | 15.99 | 2.7 | 47.52 | 42.27 | -31.53 | 0 | 0 | 0 | Battery-supported
2025-12-07 19:00 | 341 | 12 | Summer | 19 | 24 | 1.9 | 6.5 | 67.3 | 197.9 | 11.87 | 3.78 | 15.65 | 0 | 45 | 30.53 | -29.35 | 0 | 0 | 0 | Battery-supported
2025-12-07 20:00 | 341 | 12 | Summer | 20 | 24 | -1.6 | 6.04 | 77.5 | 137.4 | 8.24 | 2.29 | 10.53 | 1.6 | 47.74 | 15.65 | -37.21 | 0 | 0 | 0 | Battery-supported
2025-12-07 21:00 | 341 | 12 | Summer | 21 | 24 | -5.7 | 4.04 | 53 | 151.2 | 9.07 | 0.02 | 9.09 | 5.7 | 45 | 15 | -1.62 | 34.29 | 11.442 | 0 | Diesel-backup
2025-12-07 22:00 | 341 | 12 | Summer | 22 | 24 | -1.4 | 12.48 | 59.8 | 93.6 | 5.62 | 101.35 | 106.97 | 1.4 | 45 | 37.8 | 61.97 | 0 | 0 | 0 | Normal
2025-12-07 23:00 | 341 | 12 | Summer | 23 | 24 | -1.3 | 5.47 | 50.9 | 52.9 | 3.17 | 1.07 | 4.24 | 1.3 | 45 | 21.5 | -40.76 | 0 | 0 | 0 | Battery-supported
2025-12-08 | 342 | 12 | Summer | 0 | 24 | -3 | 7.7 | 53.2 | 0 | 0 | 10.37 | 10.37 | 3 | 45 | 15 | -16.25 | 18.38 | 6.507 | 0 | Diesel-backup
2025-12-08 01:00 | 342 | 12 | Summer | 1 | 24 | -5.8 | 2.74 | 52.6 | 51.9 | 3.11 | 0 | 3.11 | 5.8 | 45.62 | 15 | 0 | 42.51 | 13.739 | 0 | Diesel-backup
2025-12-08 02:00 | 342 | 12 | Summer | 2 | 24 | 0.4 | 6.34 | 32.1 | 128.9 | 7.73 | 3.21 | 10.94 | 0 | 45 | 15 | 0 | 34.06 | 11.376 | 0 | Diesel-backup
2025-12-08 03:00 | 342 | 12 | Summer | 3 | 24 | -6.2 | 9.06 | 22.1 | 209.5 | 12.57 | 24.06 | 36.63 | 6.2 | 45 | 15 | 0 | 8.37 | 3.071 | 0 | Diesel-backup
2025-12-08 04:00 | 342 | 12 | Summer | 4 | 24 | -2.8 | 5.38 | 74.3 | 145.3 | 8.72 | 0.93 | 9.65 | 2.8 | 45 | 15 | 0 | 35.35 | 11.749 | 0 | Diesel-backup
2025-12-08 05:00 | 342 | 12 | Summer | 5 | 24 | -4.1 | 5.48 | 86.3 | 140.8 | 8.45 | 1.09 | 9.54 | 4.1 | 45 | 15 | 0 | 35.46 | 11.78 | 0 | Diesel-backup
2025-12-08 06:00 | 342 | 12 | Summer | 6 | 24 | -3.5 | 6.74 | 75.2 | 202.3 | 12.14 | 4.76 | 16.9 | 3.5 | 45 | 15 | 0 | 28.1 | 9.6 | 0 | Diesel-backup
2025-12-08 07:00 | 342 | 12 | Summer | 7 | 24 | -1.2 | 8.86 | 79.4 | 210.6 | 12.64 | 21.55 | 34.19 | 1.2 | 45 | 15 | 0 | 10.81 | 3.932 | 0 | Diesel-backup
2025-12-08 08:00 | 342 | 12 | Summer | 8 | 24 | -3.7 | 7.36 | 53.3 | 340.8 | 20.45 | 8.05 | 28.5 | 3.7 | 49.68 | 15 | 0 | 21.18 | 7.423 | 0 | Diesel-backup
2025-12-08 09:00 | 342 | 12 | Summer | 9 | 24 | -6.2 | 19.16 | 60.2 | 332.3 | 19.94 | 120 | 139.94 | 6.2 | 52.27 | 47.26 | 87.67 | 0 | 0 | 0 | Normal
2025-12-08 10:00 | 342 | 12 | Summer | 10 | 24 | -2.3 | 13.47 | 22.7 | 525.6 | 31.54 | 120 | 151.54 | 2.3 | 45.33 | 86.35 | 106.21 | 0 | 0 | 0 | Normal
2025-12-08 11:00 | 342 | 12 | Summer | 11 | 24 | -5.9 | 4.75 | 54.1 | 386.5 | 23.19 | 0.27 | 23.46 | 5.9 | 53.03 | 74.52 | -29.57 | 0 | 0 | 0 | Battery-supported
2025-12-08 12:00 | 342 | 12 | Summer | 12 | 24 | -3.9 | 12.06 | 90 | 213 | 12.78 | 87.79 | 100.57 | 3.9 | 47.04 | 94.22 | 53.53 | 0 | 0 | 0 | Normal
2025-12-08 13:00 | 342 | 12 | Summer | 13 | 24 | -6.7 | 1.78 | 63.9 | 338.5 | 20.31 | 0 | 20.31 | 6.7 | 45 | 84.34 | -24.69 | 0 | 0 | 0 | Battery-supported
2025-12-08 14:00 | 342 | 12 | Summer | 14 | 24 | -5.8 | 5.68 | 40.4 | 441.6 | 26.5 | 1.45 | 27.95 | 5.8 | 53.88 | 73.97 | -25.93 | 0 | 0 | 0 | Battery-supported
2025-12-08 15:00 | 342 | 12 | Summer | 15 | 24 | -3 | 2.32 | 32.4 | 458.7 | 27.52 | 0 | 27.52 | 3 | 45 | 66.98 | -17.48 | 0 | 0 | 0 | Battery-supported
2025-12-08 16:00 | 342 | 12 | Summer | 16 | 24 | -1.9 | 9.42 | 47.9 | 363.8 | 21.83 | 29.04 | 50.87 | 1.9 | 45 | 69.14 | 5.87 | 0 | 0 | 0 | Normal
2025-12-08 17:00 | 342 | 12 | Summer | 17 | 24 | -6.2 | 5.38 | 63.5 | 272.7 | 16.36 | 0.93 | 17.29 | 6.2 | 61.96 | 51.27 | -44.67 | 0 | 0 | 0 | Battery-supported
2025-12-08 18:00 | 342 | 12 | Summer | 18 | 24 | -1.1 | 3.02 | 75.5 | 201.3 | 12.08 | 0 | 12.08 | 1.1 | 45 | 38.1 | -32.92 | 0 | 0 | 0 | Battery-supported
2025-12-08 19:00 | 342 | 12 | Summer | 19 | 24 | -3.8 | 10.55 | 62.2 | 212.9 | 12.77 | 49.04 | 61.81 | 3.8 | 49.36 | 42.68 | 12.45 | 0 | 0 | 0 | Normal
2025-12-08 20:00 | 342 | 12 | Summer | 20 | 24 | 0.8 | 3.31 | 79.2 | 133.2 | 7.99 | 0 | 7.99 | 0 | 45 | 27.88 | -37.01 | 0 | 0 | 0 | Battery-supported
2025-12-08 21:00 | 342 | 12 | Summer | 21 | 24 | -2.8 | 9.98 | 37.6 | 180.2 | 10.81 | 38.08 | 48.89 | 2.8 | 45 | 29.31 | 3.89 | 0 | 0 | 0 | Normal
2025-12-08 22:00 | 342 | 12 | Summer | 22 | 24 | -4.7 | 7.85 | 53 | 102.3 | 6.14 | 11.52 | 17.66 | 4.7 | 45 | 18.38 | -27.34 | 0 | 0 | 0 | Battery-supported
2025-12-08 23:00 | 342 | 12 | Summer | 23 | 24 | -2.2 | 6 | 62.5 | 45.5 | 2.73 | 2.19 | 4.92 | 2.2 | 45 | 15 | -8.44 | 31.64 | 10.666 | 0 | Diesel-backup
2025-12-09 | 343 | 12 | Summer | 0 | 24 | -4.6 | 11.31 | 7.5 | 0 | 0 | 66.68 | 66.68 | 4.6 | 45 | 22.98 | 21.68 | 0 | 0 | 0 | Normal
2025-12-09 01:00 | 343 | 12 | Summer | 1 | 24 | -0.2 | 3.74 | 50.4 | 53.2 | 3.19 | 0 | 3.19 | 0.2 | 45 | 15 | -19.95 | 21.86 | 7.644 | 0 | Diesel-backup
2025-12-09 02:00 | 343 | 12 | Summer | 2 | 24 | -3.4 | 1.99 | 67.1 | 84.4 | 5.06 | 0 | 5.06 | 3.4 | 45 | 15 | 0 | 39.94 | 13.039 | 0 | Diesel-backup
2025-12-09 03:00 | 343 | 12 | Summer | 3 | 24 | -4.1 | 3.16 | 88.5 | 84.5 | 5.07 | 0 | 5.07 | 4.1 | 45 | 15 | 0 | 39.93 | 13.037 | 0 | Diesel-backup
2025-12-09 04:00 | 343 | 12 | Summer | 4 | 24 | -2.8 | 18.97 | 65.8 | 166 | 9.96 | 120 | 129.96 | 2.8 | 45 | 46.27 | 84.96 | 0 | 0 | 0 | Normal
2025-12-09 05:00 | 343 | 12 | Summer | 5 | 24 | -6.6 | 4.05 | 30.3 | 308.6 | 18.52 | 0.02 | 18.54 | 6.6 | 45 | 35.68 | -26.46 | 0 | 0 | 0 | Battery-supported
2025-12-09 06:00 | 343 | 12 | Summer | 6 | 24 | -7.5 | 5.18 | 31 | 355.9 | 21.35 | 0.66 | 22.01 | 7.5 | 45 | 26.49 | -22.99 | 0 | 0 | 0 | Battery-supported
2025-12-09 07:00 | 343 | 12 | Summer | 7 | 24 | -3.9 | 15.12 | 43.7 | 349.8 | 20.99 | 120 | 140.99 | 3.9 | 45 | 61.81 | 95.99 | 0 | 0 | 0 | Normal
2025-12-09 08:00 | 343 | 12 | Summer | 8 | 24 | -7.3 | 5.19 | 52.2 | 345.6 | 20.74 | 0.68 | 21.42 | 7.3 | 58.76 | 46.87 | -37.34 | 0 | 0 | 0 | Battery-supported
2025-12-09 09:00 | 343 | 12 | Summer | 9 | 24 | -7.2 | 9.55 | 24.9 | 492.6 | 29.56 | 30.99 | 60.55 | 7.2 | 49.81 | 50.83 | 10.74 | 0 | 0 | 0 | Normal
2025-12-09 10:00 | 343 | 12 | Summer | 10 | 24 | -2.8 | 16.09 | 46.1 | 414.5 | 24.87 | 120 | 144.87 | 2.8 | 49.03 | 86.1 | 95.84 | 0 | 0 | 0 | Normal
2025-12-09 11:00 | 343 | 12 | Summer | 11 | 24 | -3.3 | 8.68 | 49.7 | 407.9 | 24.47 | 19.45 | 43.92 | 3.3 | 45.62 | 85.42 | -1.7 | 0 | 0 | 0 | Battery-supported
2025-12-09 12:00 | 343 | 12 | Summer | 12 | 24 | -6.9 | 6.63 | 64.2 | 340 | 20.4 | 4.29 | 24.69 | 6.9 | 49.74 | 75.4 | -25.05 | 0 | 0 | 0 | Battery-supported
2025-12-09 13:00 | 343 | 12 | Summer | 13 | 24 | -5.1 | 10.71 | 16.9 | 568 | 34.08 | 52.46 | 86.54 | 5.1 | 46.66 | 90.07 | 39.88 | 0 | 0 | 0 | Normal
2025-12-09 14:00 | 343 | 12 | Summer | 14 | 24 | -5.3 | 1.34 | 11.8 | 577.4 | 34.64 | 0 | 34.64 | 5.3 | 48.28 | 84.61 | -13.64 | 0 | 0 | 0 | Battery-supported
2025-12-09 15:00 | 343 | 12 | Summer | 15 | 24 | 0.9 | 5.15 | 36.3 | 440.9 | 26.45 | 0.63 | 27.08 | 0 | 45 | 77.45 | -17.92 | 0 | 0 | 0 | Battery-supported
2025-12-09 16:00 | 343 | 12 | Summer | 16 | 24 | -0.6 | 13.56 | 52.9 | 342.9 | 20.57 | 120 | 140.57 | 0.6 | 45 | 95 | 47.7 | 0 | 0 | 0 | Normal
2025-12-09 17:00 | 343 | 12 | Summer | 17 | 24 | -3.2 | 4.09 | 9.3 | 484 | 29.04 | 0.03 | 29.07 | 3.2 | 45 | 88.63 | -15.93 | 0 | 0 | 0 | Battery-supported
2025-12-09 18:00 | 343 | 12 | Summer | 18 | 24 | -0.8 | 0.87 | 46.7 | 301.5 | 18.09 | 0 | 18.09 | 0.8 | 52.87 | 74.72 | -34.78 | 0 | 0 | 0 | Battery-supported
2025-12-09 19:00 | 343 | 12 | Summer | 19 | 24 | -4.9 | 7.32 | 53.1 | 240.4 | 14.42 | 7.8 | 22.22 | 4.9 | 49.47 | 63.82 | -27.25 | 0 | 0 | 0 | Battery-supported
2025-12-09 20:00 | 343 | 12 | Summer | 20 | 24 | -3.3 | 9.62 | 29.4 | 255.6 | 15.34 | 32.08 | 47.42 | 3.3 | 48.62 | 63.34 | -1.2 | 0 | 0 | 0 | Battery-supported
2025-12-09 21:00 | 343 | 12 | Summer | 21 | 24 | -1.7 | 5.57 | 94.1 | 73.8 | 4.43 | 1.24 | 5.67 | 1.7 | 45 | 47.6 | -39.33 | 0 | 0 | 0 | Battery-supported
2025-12-09 22:00 | 343 | 12 | Summer | 22 | 24 | -1.1 | 9.69 | 63.5 | 88.9 | 5.33 | 33.2 | 38.53 | 1.1 | 45 | 45.02 | -6.47 | 0 | 0 | 0 | Battery-supported
2025-12-09 23:00 | 343 | 12 | Summer | 23 | 24 | -2.5 | 7.86 | 46.8 | 55.5 | 3.33 | 11.6 | 14.93 | 2.5 | 45 | 32.99 | -30.07 | 0 | 0 | 0 | Battery-supported
2025-12-10 | 344 | 12 | Summer | 0 | 24 | -1.9 | 27.36 | 58.5 | 0 | 0 | 120 | 120 | 1.9 | 45 | 60.59 | 75 | 0 | 0 | 0 | Normal
2025-12-10 01:00 | 344 | 12 | Summer | 1 | 24 | -2.7 | 10.8 | 7.4 | 80.9 | 4.85 | 54.45 | 59.3 | 2.7 | 45 | 65.85 | 14.3 | 0 | 0 | 0 | Normal
2025-12-10 02:00 | 344 | 12 | Summer | 2 | 24 | -3.6 | 7.84 | 15.7 | 149.8 | 8.99 | 11.44 | 20.43 | 3.6 | 45 | 56.02 | -24.57 | 0 | 0 | 0 | Battery-supported
2025-12-10 03:00 | 344 | 12 | Summer | 3 | 24 | -4.3 | 1.59 | 42 | 172 | 10.32 | 0 | 10.32 | 4.3 | 45 | 42.15 | -34.68 | 0 | 0 | 0 | Battery-supported
2025-12-10 04:00 | 344 | 12 | Summer | 4 | 24 | -4.9 | 4.3 | 75.3 | 142.9 | 8.57 | 0.07 | 8.64 | 4.9 | 45 | 27.61 | -36.36 | 0 | 0 | 0 | Battery-supported
2025-12-10 05:00 | 344 | 12 | Summer | 5 | 24 | -3.8 | 3.34 | 71.6 | 184.9 | 11.09 | 0 | 11.09 | 3.8 | 49.4 | 15 | -31.52 | 6.79 | 2.506 | 0 | Diesel-backup
2025-12-10 06:00 | 344 | 12 | Summer | 6 | 24 | -3.6 | 14.86 | 67 | 230.6 | 13.84 | 120 | 133.84 | 3.6 | 45 | 47.69 | 88.84 | 0 | 0 | 0 | Normal
2025-12-10 07:00 | 344 | 12 | Summer | 7 | 24 | -4.2 | 3.06 | 84.7 | 189.7 | 11.38 | 0 | 11.38 | 4.2 | 45 | 34.25 | -33.62 | 0 | 0 | 0 | Battery-supported
2025-12-10 08:00 | 344 | 12 | Summer | 8 | 24 | -7.3 | 5.5 | 19.4 | 485.2 | 29.11 | 1.12 | 30.23 | 7.3 | 48.8 | 26.82 | -18.57 | 0 | 0 | 0 | Battery-supported
2025-12-10 09:00 | 344 | 12 | Summer | 9 | 24 | -6.9 | 8.38 | 20.4 | 513.3 | 30.8 | 16.27 | 47.07 | 6.9 | 52.79 | 24.53 | -5.72 | 0 | 0 | 0 | Battery-supported
2025-12-10 10:00 | 344 | 12 | Summer | 10 | 24 | -3.7 | 4.81 | 0 | 633.6 | 38.02 | 0.31 | 38.33 | 3.7 | 45.8 | 21.54 | -7.47 | 0 | 0 | 0 | Battery-supported
2025-12-10 11:00 | 344 | 12 | Summer | 11 | 24 | -1.1 | 5.32 | 58.8 | 363.6 | 21.82 | 0.84 | 22.66 | 1.1 | 47.91 | 15 | -16.35 | 8.9 | 3.258 | 0 | Diesel-backup
2025-12-10 12:00 | 344 | 12 | Summer | 12 | 24 | -3.6 | 7.84 | 45.5 | 432.1 | 25.93 | 11.44 | 37.37 | 3.6 | 46.26 | 15 | 0 | 8.89 | 3.256 | 0 | Diesel-backup
2025-12-10 13:00 | 344 | 12 | Summer | 13 | 24 | -4.5 | 4.07 | 60.5 | 355.3 | 21.32 | 0.03 | 21.35 | 4.5 | 45.96 | 15 | 0 | 24.61 | 8.518 | 0 | Diesel-backup
2025-12-10 14:00 | 344 | 12 | Summer | 14 | 24 | -2.7 | 7.28 | 54.9 | 372.7 | 22.36 | 7.56 | 29.92 | 2.7 | 45 | 15 | 0 | 15.08 | 5.403 | 0 | Diesel-backup
2025-12-10 15:00 | 344 | 12 | Summer | 15 | 24 | -5.3 | 10.49 | 22.6 | 503.3 | 30.2 | 47.8 | 78 | 5.3 | 52.46 | 24.4 | 25.54 | 0 | 0 | 0 | Normal
2025-12-10 16:00 | 344 | 12 | Summer | 16 | 24 | 0.4 | 4.49 | 76.5 | 242.1 | 14.53 | 0.14 | 14.67 | 0 | 45 | 15 | -23.5 | 6.83 | 2.52 | 0 | Diesel-backup
2025-12-10 17:00 | 344 | 12 | Summer | 17 | 24 | -1.8 | 3.26 | 45.7 | 342.1 | 20.53 | 0 | 20.53 | 1.8 | 47.8 | 15 | 0 | 27.27 | 9.345 | 0 | Diesel-backup
2025-12-10 18:00 | 344 | 12 | Summer | 18 | 24 | -3.4 | 16.67 | 52 | 283.1 | 16.99 | 120 | 136.99 | 3.4 | 45 | 48.85 | 91.99 | 0 | 0 | 0 | Normal
2025-12-10 19:00 | 344 | 12 | Summer | 19 | 24 | -2.1 | 16.81 | 29.8 | 310 | 18.6 | 120 | 138.6 | 2.1 | 48.54 | 81.99 | 90.06 | 0 | 0 | 0 | Normal
2025-12-10 20:00 | 344 | 12 | Summer | 20 | 24 | -2.9 | 6.44 | 40.5 | 228.3 | 13.7 | 3.56 | 17.26 | 2.9 | 51.03 | 68.49 | -33.77 | 0 | 0 | 0 | Battery-supported
2025-12-10 21:00 | 344 | 12 | Summer | 21 | 24 | 1.1 | 7.15 | 73.1 | 113.5 | 6.81 | 6.81 | 13.62 | 0 | 45 | 55.93 | -31.38 | 0 | 0 | 0 | Battery-supported
2025-12-10 22:00 | 344 | 12 | Summer | 22 | 24 | -2.4 | 7.11 | 39 | 120.1 | 7.21 | 6.58 | 13.79 | 2.4 | 45 | 43.45 | -31.21 | 0 | 0 | 0 | Battery-supported
2025-12-10 23:00 | 344 | 12 | Summer | 23 | 24 | -1.8 | 5.1 | 40.9 | 59.3 | 3.56 | 0.57 | 4.13 | 1.8 | 45.67 | 26.83 | -41.54 | 0 | 0 | 0 | Battery-supported
2025-12-11 | 345 | 12 | Summer | 0 | 24 | -1.1 | 6.32 | 0 | 0 | 0 | 3.14 | 3.14 | 1.1 | 45 | 15 | -29.59 | 12.27 | 4.442 | 0 | Diesel-backup
2025-12-11 01:00 | 345 | 12 | Summer | 1 | 24 | -4.4 | 1.61 | 60 | 47.1 | 2.83 | 0 | 2.83 | 4.4 | 45 | 15 | 0 | 42.17 | 13.647 | 0 | Diesel-backup
2025-12-11 02:00 | 345 | 12 | Summer | 2 | 24 | -2.7 | 2.58 | 33.7 | 126.9 | 7.61 | 0 | 7.61 | 2.7 | 45 | 15 | 0 | 37.39 | 12.329 | 0 | Diesel-backup
2025-12-11 03:00 | 345 | 12 | Summer | 3 | 24 | -2.9 | 5.32 | 15.7 | 221.5 | 13.29 | 0.84 | 14.13 | 2.9 | 45 | 15 | 0 | 30.87 | 10.437 | 0 | Diesel-backup
2025-12-11 04:00 | 345 | 12 | Summer | 4 | 24 | -7.3 | 4.5 | 65.7 | 166.4 | 9.98 | 0.14 | 10.12 | 7.3 | 45 | 15 | 0 | 34.88 | 11.613 | 0 | Diesel-backup
2025-12-11 05:00 | 345 | 12 | Summer | 5 | 24 | -3.6 | 2.86 | 64.5 | 206.1 | 12.37 | 0 | 12.37 | 3.6 | 45 | 15 | 0 | 32.63 | 10.958 | 0 | Diesel-backup
2025-12-11 06:00 | 345 | 12 | Summer | 6 | 24 | -4.5 | 6.31 | 24 | 380.5 | 22.83 | 3.11 | 25.94 | 4.5 | 45 | 15 | 0 | 19.06 | 6.732 | 0 | Diesel-backup
2025-12-11 07:00 | 345 | 12 | Summer | 7 | 24 | -4.3 | 9.8 | 75 | 227.8 | 13.67 | 35 | 48.67 | 4.3 | 45 | 16.35 | 3.67 | 0 | 0 | 0 | Normal
2025-12-11 08:00 | 345 | 12 | Summer | 8 | 24 | -4.5 | 4.07 | 54.8 | 334.5 | 20.07 | 0.03 | 20.1 | 4.5 | 45 | 15 | -3.38 | 21.52 | 7.534 | 0 | Diesel-backup
2025-12-11 09:00 | 345 | 12 | Summer | 9 | 24 | -4 | 1.17 | 60.5 | 331.1 | 19.87 | 0 | 19.87 | 4 | 48.21 | 15 | 0 | 28.34 | 9.673 | 0 | Diesel-backup
2025-12-11 10:00 | 345 | 12 | Summer | 10 | 24 | -1.5 | 7.82 | 54.8 | 373.4 | 22.4 | 11.28 | 33.68 | 1.5 | 45 | 15 | 0 | 11.32 | 4.11 | 0 | Diesel-backup
2025-12-11 11:00 | 345 | 12 | Summer | 11 | 24 | -6.8 | 5.41 | 50 | 406.3 | 24.38 | 0.98 | 25.36 | 6.8 | 52.63 | 15 | 0 | 27.27 | 9.345 | 0 | Diesel-backup
2025-12-11 12:00 | 345 | 12 | Summer | 12 | 24 | -4.6 | 10.75 | 56.2 | 379.4 | 22.76 | 53.34 | 76.1 | 4.6 | 48 | 25.34 | 28.1 | 0 | 0 | 0 | Normal
2025-12-11 13:00 | 345 | 12 | Summer | 13 | 24 | -2 | 2.43 | 70.9 | 304.5 | 18.27 | 0 | 18.27 | 2 | 47.11 | 15 | -25.85 | 2.99 | 1.117 | 0 | Diesel-backup
2025-12-11 14:00 | 345 | 12 | Summer | 14 | 24 | -2.1 | 3.14 | 72.1 | 291.1 | 17.47 | 0 | 17.47 | 2.1 | 50.46 | 15 | 0 | 32.99 | 11.064 | 0 | Diesel-backup
2025-12-11 15:00 | 345 | 12 | Summer | 15 | 24 | -1.7 | 5.21 | 59.4 | 335.8 | 20.15 | 0.7 | 20.85 | 1.7 | 45 | 15 | 0 | 24.15 | 8.373 | 0 | Diesel-backup
2025-12-11 16:00 | 345 | 12 | Summer | 16 | 24 | 3.7 | 3.62 | 28.3 | 447.5 | 26.85 | 0 | 26.85 | 0 | 45 | 15 | 0 | 18.15 | 6.432 | 0 | Diesel-backup
2025-12-11 17:00 | 345 | 12 | Summer | 17 | 24 | -0.7 | 12.65 | 40.4 | 362.7 | 21.76 | 107.22 | 128.98 | 0.7 | 48.51 | 44.61 | 80.47 | 0 | 0 | 0 | Normal
2025-12-11 18:00 | 345 | 12 | Summer | 18 | 24 | 0.7 | 2.53 | 30.7 | 356.9 | 21.41 | 0 | 21.41 | 0 | 49.77 | 33.27 | -28.36 | 0 | 0 | 0 | Battery-supported
2025-12-11 19:00 | 345 | 12 | Summer | 19 | 24 | -2.3 | 5.1 | 30 | 309.5 | 18.57 | 0.57 | 19.14 | 2.3 | 50.43 | 20.75 | -31.29 | 0 | 0 | 0 | Battery-supported
2025-12-11 20:00 | 345 | 12 | Summer | 20 | 24 | -3.8 | 18.73 | 87.3 | 113.2 | 6.79 | 120 | 126.79 | 3.8 | 45 | 50.85 | 81.79 | 0 | 0 | 0 | Normal
2025-12-11 21:00 | 345 | 12 | Summer | 21 | 24 | -2.4 | 2.39 | 39 | 177.5 | 10.65 | 0 | 10.65 | 2.4 | 45 | 37.11 | -34.35 | 0 | 0 | 0 | Battery-supported
2025-12-11 22:00 | 345 | 12 | Summer | 22 | 24 | -0.2 | 6.69 | 41.3 | 117.2 | 7.03 | 4.54 | 11.57 | 0.2 | 45 | 23.74 | -33.43 | 0 | 0 | 0 | Battery-supported
2025-12-11 23:00 | 345 | 12 | Summer | 23 | 24 | -1.2 | 5.48 | 38.2 | 61.1 | 3.67 | 1.09 | 4.76 | 1.2 | 45 | 15 | -21.85 | 18.39 | 6.511 | 0 | Diesel-backup
2025-12-12 | 346 | 12 | Summer | 0 | 24 | -1.4 | 8.49 | 95.7 | 0 | 0 | 17.39 | 17.39 | 1.4 | 45 | 15 | 0 | 27.61 | 9.45 | 0 | Diesel-backup
2025-12-12 01:00 | 346 | 12 | Summer | 1 | 24 | -3.1 | 7.99 | 41.1 | 59.2 | 3.55 | 12.67 | 16.22 | 3.1 | 45 | 15 | 0 | 28.78 | 9.807 | 0 | Diesel-backup
2025-12-12 02:00 | 346 | 12 | Summer | 2 | 24 | -3.8 | 7.69 | 22.9 | 140.6 | 8.44 | 10.3 | 18.74 | 3.8 | 45 | 15 | 0 | 26.26 | 9.033 | 0 | Diesel-backup
2025-12-12 03:00 | 346 | 12 | Summer | 3 | 24 | -3.8 | 11.15 | 56.4 | 144.9 | 8.69 | 62.66 | 71.35 | 3.8 | 45 | 24.7 | 26.35 | 0 | 0 | 0 | Normal
2025-12-12 04:00 | 346 | 12 | Summer | 4 | 24 | -2.2 | 10.99 | 33.7 | 245 | 14.7 | 58.81 | 73.51 | 2.2 | 45 | 35.19 | 28.51 | 0 | 0 | 0 | Normal
2025-12-12 05:00 | 346 | 12 | Summer | 5 | 24 | -2.2 | 4.45 | 16.2 | 350.8 | 21.05 | 0.12 | 21.17 | 2.2 | 45 | 25.66 | -23.83 | 0 | 0 | 0 | Battery-supported
2025-12-12 06:00 | 346 | 12 | Summer | 6 | 24 | -6.5 | 4.34 | 50.4 | 288.6 | 17.32 | 0.08 | 17.4 | 6.5 | 45 | 15 | -26.64 | 0.96 | 0.361 | 0 | Diesel-backup
2025-12-12 07:00 | 346 | 12 | Summer | 7 | 24 | -2.8 | 9.53 | 37.9 | 372.5 | 22.35 | 30.69 | 53.04 | 2.8 | 45 | 17.96 | 8.04 | 0 | 0 | 0 | Normal
2025-12-12 08:00 | 346 | 12 | Summer | 8 | 24 | -5.9 | 7.27 | 50.7 | 352.3 | 21.14 | 7.5 | 28.64 | 5.9 | 50.95 | 15 | -7.4 | 14.91 | 5.347 | 0 | Diesel-backup
2025-12-12 09:00 | 346 | 12 | Summer | 9 | 24 | -3.4 | 8.1 | 52.4 | 367.8 | 22.07 | 13.62 | 35.69 | 3.4 | 45.24 | 15 | 0 | 9.55 | 3.489 | 0 | Diesel-backup
2025-12-12 10:00 | 346 | 12 | Summer | 10 | 24 | -4.7 | 6.74 | 94 | 186.7 | 11.2 | 4.76 | 15.96 | 4.7 | 46.25 | 15 | 0 | 30.29 | 10.263 | 0 | Diesel-backup
2025-12-12 11:00 | 346 | 12 | Summer | 11 | 24 | -0.6 | 4.87 | 53 | 391.9 | 23.51 | 0.36 | 23.87 | 0.6 | 45 | 15 | 0 | 21.13 | 7.407 | 0 | Diesel-backup
2025-12-12 12:00 | 346 | 12 | Summer | 12 | 24 | -4.7 | 9.25 | 71.2 | 305.5 | 18.33 | 26.61 | 44.94 | 4.7 | 46.13 | 15 | 0 | 1.19 | 0.448 | 0 | Diesel-backup
2025-12-12 13:00 | 346 | 12 | Summer | 13 | 24 | -3 | 3.93 | 62 | 347.7 | 20.86 | 0.01 | 20.87 | 3 | 46.54 | 15 | 0 | 25.67 | 8.85 | 0 | Diesel-backup
2025-12-12 14:00 | 346 | 12 | Summer | 14 | 24 | -1.7 | 18.92 | 70.1 | 300.7 | 18.04 | 120 | 138.04 | 1.7 | 45 | 49.24 | 93.04 | 0 | 0 | 0 | Normal
2025-12-12 15:00 | 346 | 12 | Summer | 15 | 24 | -4.5 | 17.89 | 10 | 560.7 | 33.64 | 120 | 153.64 | 4.5 | 45.39 | 89.07 | 108.25 | 0 | 0 | 0 | Normal
2025-12-12 16:00 | 346 | 12 | Summer | 16 | 24 | -2.4 | 21.35 | 15.7 | 501.1 | 30.07 | 120 | 150.07 | 2.4 | 45 | 95 | 16.1 | 0 | 0 | 0 | Normal
2025-12-12 17:00 | 346 | 12 | Summer | 17 | 24 | -2.5 | 7.56 | 61.7 | 279.6 | 16.78 | 9.37 | 26.15 | 2.5 | 45 | 87.46 | -18.85 | 0 | 0 | 0 | Battery-supported
2025-12-12 18:00 | 346 | 12 | Summer | 18 | 24 | -2.8 | 5.27 | 50.7 | 287.6 | 17.26 | 0.78 | 18.04 | 2.8 | 45 | 76.68 | -26.96 | 0 | 0 | 0 | Battery-supported
2025-12-12 19:00 | 346 | 12 | Summer | 19 | 24 | -2.5 | 14.32 | 52.8 | 241.1 | 14.47 | 120 | 134.47 | 2.5 | 45 | 95 | 49.79 | 0 | 0 | 0 | Normal
2025-12-12 20:00 | 346 | 12 | Summer | 20 | 24 | 0.9 | 6.83 | 67.6 | 161.7 | 9.7 | 5.17 | 14.87 | 0 | 45 | 82.95 | -30.13 | 0 | 0 | 0 | Battery-supported
2025-12-12 21:00 | 346 | 12 | Summer | 21 | 24 | -2.9 | 10.72 | 41.5 | 172.9 | 10.37 | 52.68 | 63.05 | 2.9 | 45 | 89.59 | 18.05 | 0 | 0 | 0 | Normal
2025-12-12 22:00 | 346 | 12 | Summer | 22 | 24 | -0.5 | 10.68 | 77.3 | 71.3 | 4.28 | 51.81 | 56.09 | 0.5 | 45 | 93.67 | 11.09 | 0 | 0 | 0 | Normal
2025-12-12 23:00 | 346 | 12 | Summer | 23 | 24 | -1.2 | 4.01 | 26.1 | 68.9 | 4.13 | 0.02 | 4.15 | 1.2 | 45 | 77.33 | -40.85 | 0 | 0 | 0 | Battery-supported
2025-12-13 | 347 | 12 | Summer | 0 | 24 | -5.2 | 9.1 | 31.4 | 0 | 0 | 24.58 | 24.58 | 5.2 | 45 | 69.16 | -20.42 | 0 | 0 | 0 | Battery-supported
2025-12-13 01:00 | 347 | 12 | Summer | 1 | 24 | -1.4 | 10.38 | 24.8 | 69.7 | 4.18 | 45.58 | 49.76 | 1.4 | 45 | 70.92 | 4.76 | 0 | 0 | 0 | Normal
2025-12-13 02:00 | 347 | 12 | Summer | 2 | 24 | -6 | 6.32 | 82.7 | 64.5 | 3.87 | 3.14 | 7.01 | 6 | 48.14 | 54.46 | -41.13 | 0 | 0 | 0 | Battery-supported
2025-12-13 03:00 | 347 | 12 | Summer | 3 | 24 | -1.9 | 2.55 | 78.5 | 103.3 | 6.2 | 0 | 6.2 | 1.9 | 45 | 38.94 | -38.8 | 0 | 0 | 0 | Battery-supported
2025-12-13 04:00 | 347 | 12 | Summer | 4 | 24 | -4.8 | 14.47 | 71.8 | 151.3 | 9.08 | 120 | 129.08 | 4.8 | 45 | 69.88 | 84.08 | 0 | 0 | 0 | Normal
2025-12-13 05:00 | 347 | 12 | Summer | 5 | 24 | -3.9 | 18.63 | 73.8 | 178.3 | 10.7 | 120 | 130.7 | 3.9 | 45 | 95 | 68.25 | 0 | 0 | 0 | Normal
2025-12-13 06:00 | 347 | 12 | Summer | 6 | 24 | -7 | 7.08 | 47.1 | 300 | 18 | 6.42 | 24.42 | 7 | 45 | 86.77 | -20.58 | 0 | 0 | 0 | Battery-supported
2025-12-13 07:00 | 347 | 12 | Summer | 7 | 24 | -4.1 | 5.57 | 33.7 | 389 | 23.34 | 1.24 | 24.58 | 4.1 | 45 | 78.6 | -20.42 | 0 | 0 | 0 | Battery-supported
2025-12-13 08:00 | 347 | 12 | Summer | 8 | 24 | -2.3 | 2.23 | 23.5 | 468 | 28.08 | 0 | 28.08 | 2.3 | 52.05 | 69.01 | -23.97 | 0 | 0 | 0 | Battery-supported
2025-12-13 09:00 | 347 | 12 | Summer | 9 | 24 | -6.1 | 7.31 | 19.1 | 519 | 31.14 | 7.74 | 38.88 | 6.1 | 45.33 | 66.43 | -6.45 | 0 | 0 | 0 | Battery-supported
2025-12-13 10:00 | 347 | 12 | Summer | 10 | 24 | -5.5 | 5.03 | 47.1 | 410 | 24.6 | 0.5 | 25.1 | 5.5 | 47.52 | 57.46 | -22.42 | 0 | 0 | 0 | Battery-supported
2025-12-13 11:00 | 347 | 12 | Summer | 11 | 24 | -2.9 | 2.22 | 51.3 | 400.3 | 24.02 | 0 | 24.02 | 2.9 | 48.57 | 47.64 | -24.55 | 0 | 0 | 0 | Battery-supported
2025-12-13 12:00 | 347 | 12 | Summer | 12 | 24 | -2.6 | 11.21 | 79.2 | 266.1 | 15.97 | 64.15 | 80.12 | 2.6 | 51.34 | 58.24 | 28.78 | 0 | 0 | 0 | Normal
2025-12-13 13:00 | 347 | 12 | Summer | 13 | 24 | -8.6 | 9.38 | 11.2 | 595.8 | 35.75 | 28.45 | 64.2 | 8.6 | 47.62 | 64.34 | 16.58 | 0 | 0 | 0 | Normal
2025-12-13 14:00 | 347 | 12 | Summer | 14 | 24 | 1.5 | 4.62 | 44.5 | 422.3 | 25.34 | 0.2 | 25.54 | 0 | 45.96 | 56.17 | -20.42 | 0 | 0 | 0 | Battery-supported
2025-12-13 15:00 | 347 | 12 | Summer | 15 | 24 | -1.3 | 16.62 | 16.3 | 532.1 | 31.93 | 120 | 151.93 | 1.3 | 45 | 95 | 105.52 | 0 | 0 | 0 | Normal
2025-12-13 16:00 | 347 | 12 | Summer | 16 | 24 | -0.6 | 6.5 | 44.6 | 378 | 22.68 | 3.78 | 26.46 | 0.6 | 45 | 87.58 | -18.54 | 0 | 0 | 0 | Battery-supported
2025-12-13 17:00 | 347 | 12 | Summer | 17 | 24 | -2.1 | 7.16 | 54.2 | 308.8 | 18.53 | 6.86 | 25.39 | 2.1 | 45 | 79.74 | -19.61 | 0 | 0 | 0 | Battery-supported
2025-12-13 18:00 | 347 | 12 | Summer | 18 | 24 | -5.7 | 5.95 | 60.5 | 253.5 | 15.21 | 2.06 | 17.27 | 5.7 | 45 | 68.65 | -27.73 | 0 | 0 | 0 | Battery-supported
2025-12-13 19:00 | 347 | 12 | Summer | 19 | 24 | 0 | 12.1 | 33.4 | 299.4 | 17.96 | 89.02 | 106.98 | 0 | 45.73 | 91.19 | 61.25 | 0 | 0 | 0 | Normal
2025-12-13 20:00 | 347 | 12 | Summer | 20 | 24 | -2.6 | 9.19 | 63.1 | 172.7 | 10.36 | 25.78 | 36.14 | 2.6 | 45 | 87.64 | -8.86 | 0 | 0 | 0 | Battery-supported
2025-12-13 21:00 | 347 | 12 | Summer | 21 | 24 | -0.2 | 1.59 | 52.1 | 153 | 9.18 | 0 | 9.18 | 0.2 | 45 | 73.32 | -35.82 | 0 | 0 | 0 | Battery-supported
2025-12-13 22:00 | 347 | 12 | Summer | 22 | 24 | -2.1 | 6.79 | 55.8 | 98.7 | 5.92 | 4.98 | 10.9 | 2.1 | 45 | 59.68 | -34.1 | 0 | 0 | 0 | Battery-supported
2025-12-13 23:00 | 347 | 12 | Summer | 23 | 24 | -1.3 | 10.59 | 24.3 | 70 | 4.2 | 49.88 | 54.08 | 1.3 | 45 | 63.02 | 9.08 | 0 | 0 | 0 | Normal
2025-12-14 | 348 | 12 | Summer | 0 | 24 | -3.7 | 2.22 | 28.1 | 0 | 0 | 0 | 0 | 3.7 | 45 | 45.02 | -45 | 0 | 0 | 0 | Battery-supported
2025-12-14 01:00 | 348 | 12 | Summer | 1 | 24 | -0.5 | 10.5 | 57.8 | 48.5 | 2.91 | 48.01 | 50.92 | 0.5 | 45 | 47.2 | 5.92 | 0 | 0 | 0 | Normal
2025-12-14 02:00 | 348 | 12 | Summer | 2 | 24 | -5.4 | 9.29 | 51.5 | 104.2 | 6.25 | 27.17 | 33.42 | 5.4 | 45 | 42.56 | -11.58 | 0 | 0 | 0 | Battery-supported
2025-12-14 03:00 | 348 | 12 | Summer | 3 | 24 | 1.8 | 3.52 | 41.8 | 172.3 | 10.34 | 0 | 10.34 | 0 | 45 | 28.7 | -34.66 | 0 | 0 | 0 | Battery-supported
2025-12-14 04:00 | 348 | 12 | Summer | 4 | 24 | 1.4 | 5.81 | 49.4 | 206.4 | 12.38 | 1.73 | 14.11 | 0 | 45 | 16.34 | -30.89 | 0 | 0 | 0 | Battery-supported
2025-12-14 05:00 | 348 | 12 | Summer | 5 | 24 | -0.2 | 2.8 | 33.7 | 298.4 | 17.9 | 0 | 17.9 | 0.2 | 45.42 | 15 | -3.36 | 24.16 | 8.376 | 0 | Diesel-backup
2025-12-14 06:00 | 348 | 12 | Summer | 6 | 24 | -1.3 | 4.65 | 62.1 | 247.9 | 14.87 | 0.21 | 15.08 | 1.3 | 45 | 15 | 0 | 29.92 | 10.152 | 0 | Diesel-backup
2025-12-14 07:00 | 348 | 12 | Summer | 7 | 24 | -4.4 | 5.75 | 56.8 | 298.7 | 17.92 | 1.59 | 19.51 | 4.4 | 45 | 15 | 0 | 25.49 | 8.793 | 0 | Diesel-backup
2025-12-14 08:00 | 348 | 12 | Summer | 8 | 24 | -1.7 | 9.78 | 53.3 | 341 | 20.46 | 34.66 | 55.12 | 1.7 | 47.05 | 17.97 | 8.07 | 0 | 0 | 0 | Normal
2025-12-14 09:00 | 348 | 12 | Summer | 9 | 24 | -4.4 | 10.92 | 34.9 | 447.6 | 26.86 | 57.18 | 84.04 | 4.4 | 46.23 | 31.88 | 37.81 | 0 | 0 | 0 | Normal
2025-12-14 10:00 | 348 | 12 | Summer | 10 | 24 | -7.5 | 7.71 | 27.4 | 503.6 | 30.22 | 10.44 | 40.66 | 7.5 | 51.47 | 27.56 | -10.81 | 0 | 0 | 0 | Battery-supported
2025-12-14 11:00 | 348 | 12 | Summer | 11 | 24 | -0.5 | 5.59 | 79.3 | 263.6 | 15.82 | 1.28 | 17.1 | 0.5 | 45.27 | 16.29 | -28.17 | 0 | 0 | 0 | Battery-supported
2025-12-14 12:00 | 348 | 12 | Summer | 12 | 24 | -1 | 10.32 | 78.1 | 271.6 | 16.3 | 44.4 | 60.7 | 1 | 45 | 22.07 | 15.7 | 0 | 0 | 0 | Normal
2025-12-14 13:00 | 348 | 12 | Summer | 13 | 24 | -3.2 | 7.16 | 31.3 | 497.6 | 29.86 | 6.86 | 36.72 | 3.2 | 45 | 18.76 | -8.28 | 0 | 0 | 0 | Battery-supported
2025-12-14 14:00 | 348 | 12 | Summer | 14 | 24 | -5.5 | 8.23 | 50.3 | 394.7 | 23.68 | 14.81 | 38.49 | 5.5 | 48.16 | 15 | -9.39 | 0.28 | 0.104 | 0 | Diesel-backup
2025-12-14 15:00 | 348 | 12 | Summer | 15 | 24 | -3.7 | 11.23 | 69.2 | 291.5 | 17.49 | 64.65 | 82.14 | 3.7 | 45 | 28.67 | 37.14 | 0 | 0 | 0 | Normal
2025-12-14 16:00 | 348 | 12 | Summer | 16 | 24 | -6 | 9.96 | 68 | 278.4 | 16.7 | 37.73 | 54.43 | 6 | 54.47 | 28.65 | -0.04 | 0 | 0 | 0 | Battery-supported
2025-12-14 17:00 | 348 | 12 | Summer | 17 | 24 | 0.4 | 8.19 | 80.6 | 205.9 | 12.35 | 14.44 | 26.79 | 0 | 46.49 | 20.77 | -19.7 | 0 | 0 | 0 | Battery-supported
2025-12-14 18:00 | 348 | 12 | Summer | 18 | 24 | -5 | 9.16 | 44.4 | 309.4 | 18.56 | 25.38 | 43.94 | 5 | 48.29 | 19.03 | -4.35 | 0 | 0 | 0 | Battery-supported
2025-12-14 19:00 | 348 | 12 | Summer | 19 | 24 | -0.7 | 4.59 | 81.2 | 156.3 | 9.38 | 0.18 | 9.56 | 0.7 | 45 | 15 | -10.08 | 25.36 | 8.753 | 0 | Diesel-backup
2025-12-14 20:00 | 348 | 12 | Summer | 20 | 24 | -3.1 | 4.2 | 27.5 | 260.3 | 15.62 | 0.05 | 15.67 | 3.1 | 45 | 15 | 0 | 29.33 | 9.974 | 0 | Diesel-backup
2025-12-14 21:00 | 348 | 12 | Summer | 21 | 24 | -4.5 | 18.45 | 66 | 126.8 | 7.61 | 120 | 127.61 | 4.5 | 45 | 45.4 | 82.61 | 0 | 0 | 0 | Normal
2025-12-14 22:00 | 348 | 12 | Summer | 22 | 24 | -1 | 4.05 | 54.6 | 100.3 | 6.02 | 0.02 | 6.04 | 1 | 45 | 29.82 | -38.96 | 0 | 0 | 0 | Battery-supported
2025-12-14 23:00 | 348 | 12 | Summer | 23 | 24 | -2.4 | 11.29 | 67.1 | 42.5 | 2.55 | 66.16 | 68.71 | 2.4 | 45 | 38.54 | 23.71 | 0 | 0 | 0 | Normal
2025-12-15 | 349 | 12 | Summer | 0 | 24 | -0.1 | 5.53 | 85.2 | 0 | 0 | 1.17 | 1.17 | 0.1 | 45 | 21.01 | -43.83 | 0 | 0 | 0 | Battery-supported
2025-12-15 01:00 | 349 | 12 | Summer | 1 | 24 | -5.1 | 9.71 | 54.7 | 50.5 | 3.03 | 33.52 | 36.55 | 5.1 | 45 | 17.63 | -8.45 | 0 | 0 | 0 | Battery-supported
2025-12-15 02:00 | 349 | 12 | Summer | 2 | 24 | -4.3 | 1.45 | 14.2 | 151.7 | 9.1 | 0 | 9.1 | 4.3 | 45 | 15 | -6.57 | 29.33 | 9.973 | 0 | Diesel-backup
2025-12-15 03:00 | 349 | 12 | Summer | 3 | 24 | -8.3 | 2.64 | 88.2 | 85.1 | 5.11 | 0 | 5.11 | 8.3 | 50.6 | 15 | 0 | 45.49 | 14.557 | 0 | Diesel-backup
2025-12-15 04:00 | 349 | 12 | Summer | 4 | 24 | -8.2 | 11.65 | 13.8 | 293.9 | 17.63 | 75.77 | 93.4 | 8.2 | 45 | 32.81 | 48.4 | 0 | 0 | 0 | Normal
2025-12-15 05:00 | 349 | 12 | Summer | 5 | 24 | 0.2 | 2.04 | 54.6 | 235.9 | 14.15 | 0 | 14.15 | 0 | 45 | 20.47 | -30.85 | 0 | 0 | 0 | Battery-supported
2025-12-15 06:00 | 349 | 12 | Summer | 6 | 24 | 0.6 | 4.62 | 53.1 | 279 | 16.74 | 0.2 | 16.94 | 0 | 45 | 15 | -13.68 | 14.38 | 5.166 | 0 | Diesel-backup
2025-12-15 07:00 | 349 | 12 | Summer | 7 | 24 | -3.9 | 14.58 | 55.1 | 305.3 | 18.32 | 120 | 138.32 | 3.9 | 45 | 49.34 | 93.32 | 0 | 0 | 0 | Normal
2025-12-15 08:00 | 349 | 12 | Summer | 8 | 24 | -6 | 10.9 | 27.7 | 450.1 | 27.01 | 56.72 | 83.73 | 6 | 47.42 | 62.7 | 36.31 | 0 | 0 | 0 | Normal
2025-12-15 09:00 | 349 | 12 | Summer | 9 | 24 | -4.8 | 5.35 | 60.4 | 331.7 | 19.9 | 0.89 | 20.79 | 4.8 | 45.58 | 52.79 | -24.79 | 0 | 0 | 0 | Battery-supported
2025-12-15 10:00 | 349 | 12 | Summer | 10 | 24 | -2 | 4.05 | 60.5 | 346 | 20.76 | 0.02 | 20.78 | 2 | 45 | 43.1 | -24.22 | 0 | 0 | 0 | Battery-supported
2025-12-15 11:00 | 349 | 12 | Summer | 11 | 24 | -4.9 | 15.85 | 60.7 | 354.3 | 21.26 | 120 | 141.26 | 4.9 | 45 | 78.52 | 96.26 | 0 | 0 | 0 | Normal
2025-12-15 12:00 | 349 | 12 | Summer | 12 | 24 | -2.9 | 4.28 | 70.1 | 310.8 | 18.65 | 0.07 | 18.72 | 2.9 | 51.91 | 65.25 | -33.19 | 0 | 0 | 0 | Battery-supported
2025-12-15 13:00 | 349 | 12 | Summer | 13 | 24 | -3.1 | 8 | 31.7 | 495.5 | 29.73 | 12.75 | 42.48 | 3.1 | 47.62 | 63.19 | -5.14 | 0 | 0 | 0 | Battery-supported
2025-12-15 14:00 | 349 | 12 | Summer | 14 | 24 | -3.9 | 13.87 | 87.5 | 217.6 | 13.06 | 120 | 133.06 | 3.9 | 45 | 95 | 86.44 | 0 | 0 | 0 | Normal
2025-12-15 15:00 | 349 | 12 | Summer | 15 | 24 | -3.4 | 8.83 | 70.3 | 286.5 | 17.19 | 21.19 | 38.38 | 3.4 | 49.75 | 90.45 | -11.37 | 0 | 0 | 0 | Battery-supported
2025-12-15 16:00 | 349 | 12 | Summer | 16 | 24 | -1.3 | 13.89 | 37.4 | 408.6 | 24.52 | 120 | 144.52 | 1.3 | 48.89 | 95 | 12.36 | 0 | 0 | 0 | Normal
2025-12-15 17:00 | 349 | 12 | Summer | 17 | 24 | -3.8 | 5.21 | 70.7 | 244.6 | 14.68 | 0.7 | 15.38 | 3.8 | 45 | 83.15 | -29.62 | 0 | 0 | 0 | Battery-supported
2025-12-15 18:00 | 349 | 12 | Summer | 18 | 24 | -0.4 | 3.29 | 9.9 | 429.5 | 25.77 | 0 | 25.77 | 0.4 | 45 | 75.46 | -19.23 | 0 | 0 | 0 | Battery-supported
2025-12-15 19:00 | 349 | 12 | Summer | 19 | 24 | -2.3 | 9.95 | 44.8 | 265.2 | 15.91 | 37.56 | 53.47 | 2.3 | 45.33 | 78.46 | 8.14 | 0 | 0 | 0 | Normal
2025-12-15 20:00 | 349 | 12 | Summer | 20 | 24 | -0.9 | 13.01 | 83.5 | 122.5 | 7.35 | 120 | 127.35 | 0.9 | 45 | 95 | 44.96 | 0 | 0 | 0 | Normal
2025-12-15 21:00 | 349 | 12 | Summer | 21 | 24 | 1.8 | 9.15 | 23.4 | 206.9 | 12.41 | 25.24 | 37.65 | 0 | 45 | 92.06 | -7.35 | 0 | 0 | 0 | Battery-supported
2025-12-15 22:00 | 349 | 12 | Summer | 22 | 24 | -1.7 | 3.68 | 63.3 | 89.2 | 5.35 | 0 | 5.35 | 1.7 | 45 | 76.2 | -39.65 | 0 | 0 | 0 | Battery-supported
2025-12-15 23:00 | 349 | 12 | Summer | 23 | 24 | 0.4 | 22.91 | 65.6 | 43.5 | 2.61 | 120 | 122.61 | 0 | 45 | 95 | 51.09 | 0 | 0 | 0 | Normal
2025-12-16 | 350 | 12 | Summer | 0 | 24 | -5.8 | 2.79 | 17.3 | 0 | 0 | 0 | 0 | 5.8 | 53.04 | 73.78 | -53.04 | 0 | 0 | 0 | Battery-supported
2025-12-16 01:00 | 350 | 12 | Summer | 1 | 24 | -3.2 | 7.49 | 28.5 | 67.3 | 4.04 | 8.89 | 12.93 | 3.2 | 45 | 60.96 | -32.07 | 0 | 0 | 0 | Battery-supported
2025-12-16 02:00 | 350 | 12 | Summer | 2 | 24 | -2.5 | 13.8 | 35.8 | 124.2 | 7.45 | 120 | 127.45 | 2.5 | 45 | 91.3 | 82.45 | 0 | 0 | 0 | Normal
2025-12-16 03:00 | 350 | 12 | Summer | 3 | 24 | 1.3 | 7.06 | 18.8 | 215.6 | 12.94 | 6.31 | 19.25 | 0 | 45 | 81 | -25.75 | 0 | 0 | 0 | Battery-supported
2025-12-16 04:00 | 350 | 12 | Summer | 4 | 24 | -7.6 | 10.02 | 60.3 | 179.7 | 10.78 | 38.79 | 49.57 | 7.6 | 45 | 82.68 | 4.57 | 0 | 0 | 0 | Normal
2025-12-16 05:00 | 350 | 12 | Summer | 5 | 24 | -3.8 | 1.92 | 36.5 | 290 | 17.4 | 0 | 17.4 | 3.8 | 45 | 71.64 | -27.6 | 0 | 0 | 0 | Battery-supported
2025-12-16 06:00 | 350 | 12 | Summer | 6 | 24 | -0.7 | 9.78 | 46.6 | 301.7 | 18.1 | 34.66 | 52.76 | 0.7 | 45 | 74.5 | 7.76 | 0 | 0 | 0 | Normal
2025-12-16 07:00 | 350 | 12 | Summer | 7 | 24 | -5.7 | 3.53 | 10.7 | 478.5 | 28.71 | 0 | 28.71 | 5.7 | 45 | 67.98 | -16.29 | 0 | 0 | 0 | Battery-supported
2025-12-16 08:00 | 350 | 12 | Summer | 8 | 24 | -4.5 | 7.56 | 52.7 | 343.3 | 20.6 | 9.37 | 29.97 | 4.5 | 48.76 | 60.46 | -18.79 | 0 | 0 | 0 | Battery-supported
2025-12-16 09:00 | 350 | 12 | Summer | 9 | 24 | -3.3 | 2.73 | 18.4 | 522.3 | 31.34 | 0 | 31.34 | 3.3 | 45.55 | 54.78 | -14.21 | 0 | 0 | 0 | Battery-supported
2025-12-16 10:00 | 350 | 12 | Summer | 10 | 24 | -3.5 | 10.34 | 92.5 | 194.2 | 11.65 | 44.79 | 56.44 | 3.5 | 46.64 | 58.39 | 9.8 | 0 | 0 | 0 | Normal
2025-12-16 11:00 | 350 | 12 | Summer | 11 | 24 | -0.2 | 9.04 | 31.7 | 495.9 | 29.75 | 23.8 | 53.55 | 0.2 | 45 | 61.53 | 8.55 | 0 | 0 | 0 | Normal
2025-12-16 12:00 | 350 | 12 | Summer | 12 | 24 | -2.3 | 7.51 | 66.7 | 328 | 19.68 | 9.02 | 28.7 | 2.3 | 54.84 | 51.08 | -26.14 | 0 | 0 | 0 | Battery-supported
2025-12-16 13:00 | 350 | 12 | Summer | 13 | 24 | 0 | 11.81 | 56 | 377.1 | 22.63 | 80.32 | 102.95 | 0 | 45 | 72.4 | 57.95 | 0 | 0 | 0 | Normal
2025-12-16 14:00 | 350 | 12 | Summer | 14 | 24 | -3.4 | 9.59 | 78.9 | 258.9 | 15.53 | 31.61 | 47.14 | 3.4 | 45 | 73.19 | 2.14 | 0 | 0 | 0 | Normal
2025-12-16 15:00 | 350 | 12 | Summer | 15 | 24 | -3.8 | 2.66 | 89.7 | 198.4 | 11.9 | 0 | 11.9 | 3.8 | 48.94 | 58.37 | -37.04 | 0 | 0 | 0 | Battery-supported
2025-12-16 16:00 | 350 | 12 | Summer | 16 | 24 | -2.3 | 11.62 | 8.5 | 531.7 | 31.9 | 74.93 | 106.83 | 2.3 | 49.39 | 79.51 | 57.44 | 0 | 0 | 0 | Normal
2025-12-16 17:00 | 350 | 12 | Summer | 17 | 24 | -4.1 | 9.67 | 23 | 430.7 | 25.84 | 32.88 | 58.72 | 4.1 | 45 | 84.56 | 13.72 | 0 | 0 | 0 | Normal
2025-12-16 18:00 | 350 | 12 | Summer | 18 | 24 | -0.2 | 4.03 | 36.4 | 337.3 | 20.24 | 0.02 | 20.26 | 0.2 | 45 | 74.66 | -24.74 | 0 | 0 | 0 | Battery-supported
2025-12-16 19:00 | 350 | 12 | Summer | 19 | 24 | -2 | 6.87 | 29.1 | 312.2 | 18.73 | 5.36 | 24.09 | 2 | 45 | 66.3 | -20.91 | 0 | 0 | 0 | Battery-supported
2025-12-16 20:00 | 350 | 12 | Summer | 20 | 24 | -2.5 | 5.06 | 60.7 | 178.6 | 10.72 | 0.53 | 11.25 | 2.5 | 45 | 52.8 | -33.75 | 0 | 0 | 0 | Battery-supported
2025-12-16 21:00 | 350 | 12 | Summer | 21 | 24 | 0 | 19.73 | 64.2 | 130.1 | 7.81 | 120 | 127.81 | 0 | 45 | 83.27 | 82.81 | 0 | 0 | 0 | Normal
2025-12-16 22:00 | 350 | 12 | Summer | 22 | 24 | -3.8 | 3.24 | 64.2 | 88 | 5.28 | 0 | 5.28 | 3.8 | 45 | 67.39 | -39.72 | 0 | 0 | 0 | Battery-supported
2025-12-16 23:00 | 350 | 12 | Summer | 23 | 24 | 0.2 | 5.22 | 89.4 | 28.2 | 1.69 | 0.71 | 2.4 | 0 | 45 | 50.35 | -42.6 | 0 | 0 | 0 | Battery-supported
2025-12-17 | 351 | 12 | Summer | 0 | 24 | -2.8 | 6.56 | 51.1 | 0 | 0 | 4.01 | 4.01 | 2.8 | 45 | 33.95 | -40.99 | 0 | 0 | 0 | Battery-supported
2025-12-17 01:00 | 351 | 12 | Summer | 1 | 24 | 0.5 | 7.34 | 6.7 | 81.3 | 4.88 | 7.93 | 12.81 | 0 | 45 | 21.07 | -32.19 | 0 | 0 | 0 | Battery-supported
2025-12-17 02:00 | 351 | 12 | Summer | 2 | 24 | -3.3 | 5.32 | 48.7 | 107.8 | 6.47 | 0.84 | 7.31 | 3.3 | 45 | 15 | -15.18 | 22.51 | 7.85 | 0 | Diesel-backup
2025-12-17 03:00 | 351 | 12 | Summer | 3 | 24 | -1.5 | 7.22 | 68.5 | 122 | 7.32 | 7.21 | 14.53 | 1.5 | 45 | 15 | 0 | 30.47 | 10.317 | 0 | Diesel-backup
2025-12-17 04:00 | 351 | 12 | Summer | 4 | 24 | -2.8 | 9.13 | 27.8 | 259.7 | 15.58 | 24.98 | 40.56 | 2.8 | 45 | 15 | 0 | 4.44 | 1.651 | 0 | Diesel-backup
2025-12-17 05:00 | 351 | 12 | Summer | 5 | 24 | -1.9 | 4.29 | 52.6 | 241.8 | 14.51 | 0.07 | 14.58 | 1.9 | 45 | 15 | 0 | 30.42 | 10.302 | 0 | Diesel-backup
2025-12-17 06:00 | 351 | 12 | Summer | 6 | 24 | -3.5 | 5.33 | 37.1 | 334.9 | 20.09 | 0.86 | 20.95 | 3.5 | 45 | 15 | 0 | 24.05 | 8.341 | 0 | Diesel-backup
2025-12-17 07:00 | 351 | 12 | Summer | 7 | 24 | -7.6 | 17.28 | 58.2 | 293.1 | 17.59 | 120 | 137.59 | 7.6 | 45.54 | 48.87 | 92.05 | 0 | 0 | 0 | Normal
2025-12-17 08:00 | 351 | 12 | Summer | 8 | 24 | -1.7 | 0.6 | 69.5 | 272 | 16.32 | 0 | 16.32 | 1.7 | 45 | 37.4 | -28.68 | 0 | 0 | 0 | Battery-supported
2025-12-17 09:00 | 351 | 12 | Summer | 9 | 24 | -4.1 | 11.74 | 59.7 | 334.8 | 20.09 | 78.31 | 98.4 | 4.1 | 49.24 | 55.49 | 49.16 | 0 | 0 | 0 | Normal
2025-12-17 10:00 | 351 | 12 | Summer | 10 | 24 | -2 | 11.58 | 81.9 | 244.3 | 14.66 | 73.83 | 88.49 | 2 | 45 | 71.5 | 43.49 | 0 | 0 | 0 | Normal
2025-12-17 11:00 | 351 | 12 | Summer | 11 | 24 | -2 | 2.57 | 34.3 | 483.1 | 28.99 | 0 | 28.99 | 2 | 45 | 65.09 | -16.01 | 0 | 0 | 0 | Battery-supported
2025-12-17 12:00 | 351 | 12 | Summer | 12 | 24 | -4.9 | 18.87 | 73.8 | 292.9 | 17.57 | 120 | 137.57 | 4.9 | 50.15 | 95 | 81.27 | 0 | 0 | 0 | Normal
2025-12-17 13:00 | 351 | 12 | Summer | 13 | 24 | -4.9 | 6.41 | 12.7 | 588.3 | 35.3 | 3.45 | 38.75 | 4.9 | 50.43 | 90.33 | -11.68 | 0 | 0 | 0 | Battery-supported
2025-12-17 14:00 | 351 | 12 | Summer | 14 | 24 | -1 | 12.34 | 37.2 | 456.6 | 27.4 | 96.69 | 124.09 | 1 | 51.47 | 95 | 12.7 | 0 | 0 | 0 | Normal
2025-12-17 15:00 | 351 | 12 | Summer | 15 | 24 | -2.7 | 7.59 | 13.1 | 546.2 | 32.77 | 9.58 | 42.35 | 2.7 | 48.52 | 92.53 | -6.17 | 0 | 0 | 0 | Battery-supported
2025-12-17 16:00 | 351 | 12 | Summer | 16 | 24 | 0.3 | 1.88 | 32.3 | 430.3 | 25.82 | 0 | 25.82 | 0 | 47.64 | 83.8 | -21.82 | 0 | 0 | 0 | Battery-supported
2025-12-17 17:00 | 351 | 12 | Summer | 17 | 24 | -1.8 | 5.5 | 21 | 438.5 | 26.31 | 1.12 | 27.43 | 1.8 | 45 | 76.78 | -17.57 | 0 | 0 | 0 | Battery-supported
2025-12-17 18:00 | 351 | 12 | Summer | 18 | 24 | 1.1 | 11.85 | 83.8 | 172.4 | 10.34 | 81.48 | 91.82 | 0 | 45 | 94.01 | 46.82 | 0 | 0 | 0 | Normal
2025-12-17 19:00 | 351 | 12 | Summer | 19 | 24 | -0.1 | 12.04 | 53.2 | 240.1 | 14.41 | 87.17 | 101.58 | 0.1 | 45 | 95 | 2.7 | 0 | 0 | 0 | Normal
2025-12-17 20:00 | 351 | 12 | Summer | 20 | 24 | -0.3 | 7.78 | 60.5 | 179.2 | 10.75 | 10.97 | 21.72 | 0.3 | 47.64 | 84.63 | -25.92 | 0 | 0 | 0 | Battery-supported
2025-12-17 21:00 | 351 | 12 | Summer | 21 | 24 | -1.8 | 3.15 | 21.8 | 209.9 | 12.59 | 0 | 12.59 | 1.8 | 45 | 71.67 | -32.41 | 0 | 0 | 0 | Battery-supported
2025-12-17 22:00 | 351 | 12 | Summer | 22 | 24 | -0.7 | 12.54 | 68.1 | 83 | 4.98 | 103.4 | 108.38 | 0.7 | 45 | 94.99 | 63.38 | 0 | 0 | 0 | Normal
2025-12-17 23:00 | 351 | 12 | Summer | 23 | 24 | 1.2 | 4.29 | 44 | 57.4 | 3.44 | 0.07 | 3.51 | 0 | 45 | 78.4 | -41.49 | 0 | 0 | 0 | Battery-supported
2025-12-18 | 352 | 12 | Summer | 0 | 24 | -1.7 | 7.53 | 83 | 0 | 0 | 9.16 | 9.16 | 1.7 | 45 | 64.06 | -35.84 | 0 | 0 | 0 | Battery-supported
2025-12-18 01:00 | 352 | 12 | Summer | 1 | 24 | -0.8 | 9.44 | 49.5 | 53.8 | 3.23 | 29.33 | 32.56 | 0.8 | 45 | 59.08 | -12.44 | 0 | 0 | 0 | Battery-supported
2025-12-18 02:00 | 352 | 12 | Summer | 2 | 24 | -2.3 | 9.97 | 45.9 | 111.3 | 6.68 | 37.91 | 44.59 | 2.3 | 51.13 | 56.47 | -6.54 | 0 | 0 | 0 | Battery-supported
2025-12-18 03:00 | 352 | 12 | Summer | 3 | 24 | -2.5 | 9.24 | 58.1 | 141.6 | 8.5 | 26.47 | 34.97 | 2.5 | 45 | 52.46 | -10.03 | 0 | 0 | 0 | Battery-supported
2025-12-18 04:00 | 352 | 12 | Summer | 4 | 24 | 0.7 | 3.85 | 21.9 | 274.1 | 16.45 | 0.01 | 16.46 | 0 | 45 | 41.04 | -28.54 | 0 | 0 | 0 | Battery-supported
2025-12-18 05:00 | 352 | 12 | Summer | 5 | 24 | -0.8 | 5.17 | 56.1 | 231.4 | 13.88 | 0.65 | 14.53 | 0.8 | 45 | 28.85 | -30.47 | 0 | 0 | 0 | Battery-supported
2025-12-18 06:00 | 352 | 12 | Summer | 6 | 24 | -3.5 | 3.78 | 61 | 251.5 | 15.09 | 0 | 15.09 | 3.5 | 45 | 16.89 | -29.91 | 0 | 0 | 0 | Battery-supported
2025-12-18 07:00 | 352 | 12 | Summer | 7 | 24 | -3.3 | 10.43 | 51.1 | 321.1 | 19.27 | 46.58 | 65.85 | 3.3 | 45 | 24.56 | 20.85 | 0 | 0 | 0 | Normal
2025-12-18 08:00 | 352 | 12 | Summer | 8 | 24 | -5.4 | 9.61 | 42.4 | 387.3 | 23.24 | 31.93 | 55.17 | 5.4 | 47.86 | 27.25 | 7.31 | 0 | 0 | 0 | Normal
2025-12-18 09:00 | 352 | 12 | Summer | 9 | 24 | -4.2 | 4.2 | 40.4 | 422.5 | 25.35 | 0.05 | 25.4 | 4.2 | 46.35 | 18.87 | -20.95 | 0 | 0 | 0 | Battery-supported
2025-12-18 10:00 | 352 | 12 | Summer | 10 | 24 | -3 | 11.34 | 54.6 | 374 | 22.44 | 67.45 | 89.89 | 3 | 52.66 | 32.57 | 37.23 | 0 | 0 | 0 | Normal
2025-12-18 11:00 | 352 | 12 | Summer | 11 | 24 | -1.6 | 11.3 | 66.4 | 326.4 | 19.58 | 66.42 | 86 | 1.6 | 45 | 47.66 | 41 | 0 | 0 | 0 | Normal
2025-12-18 12:00 | 352 | 12 | Summer | 12 | 24 | -1.5 | 13.5 | 32.9 | 494.1 | 29.65 | 120 | 149.65 | 1.5 | 45 | 86.17 | 104.65 | 0 | 0 | 0 | Normal
2025-12-18 13:00 | 352 | 12 | Summer | 13 | 24 | -5.2 | 9.41 | 20.6 | 549.6 | 32.98 | 28.89 | 61.87 | 5.2 | 45 | 92.38 | 16.87 | 0 | 0 | 0 | Normal
2025-12-18 14:00 | 352 | 12 | Summer | 14 | 24 | -0.2 | 9.77 | 49.5 | 398.5 | 23.91 | 34.5 | 58.41 | 0.2 | 45 | 95 | 7.12 | 0 | 0 | 0 | Normal
2025-12-18 15:00 | 352 | 12 | Summer | 15 | 24 | -2.2 | 5.42 | 25.8 | 488.7 | 29.32 | 0.99 | 30.31 | 2.2 | 48.69 | 87.65 | -18.38 | 0 | 0 | 0 | Battery-supported
2025-12-18 16:00 | 352 | 12 | Summer | 16 | 24 | -3.8 | 6.25 | 49.6 | 356.8 | 21.41 | 2.91 | 24.32 | 3.8 | 45.65 | 79.12 | -21.33 | 0 | 0 | 0 | Battery-supported
2025-12-18 17:00 | 352 | 12 | Summer | 17 | 24 | 1.6 | 12.77 | 88.9 | 173.6 | 10.42 | 111.49 | 121.91 | 0 | 45 | 95 | 43.16 | 0 | 0 | 0 | Normal
2025-12-18 18:00 | 352 | 12 | Summer | 18 | 24 | 2.2 | 4.71 | 47.5 | 298.5 | 17.91 | 0.25 | 18.16 | 0 | 45 | 84.26 | -26.84 | 0 | 0 | 0 | Battery-supported
2025-12-18 19:00 | 352 | 12 | Summer | 19 | 24 | -0.3 | 3.96 | 62.4 | 212.4 | 12.74 | 0.01 | 12.75 | 0.3 | 45 | 71.36 | -32.25 | 0 | 0 | 0 | Battery-supported
2025-12-18 20:00 | 352 | 12 | Summer | 20 | 24 | 0.7 | 9.83 | 92.9 | 99.5 | 5.97 | 35.5 | 41.47 | 0 | 49.28 | 68.24 | -7.81 | 0 | 0 | 0 | Battery-supported
2025-12-18 21:00 | 352 | 12 | Summer | 21 | 24 | 0.8 | 1.64 | 43.7 | 168.8 | 10.13 | 0 | 10.13 | 0 | 45 | 54.29 | -34.87 | 0 | 0 | 0 | Battery-supported
2025-12-18 22:00 | 352 | 12 | Summer | 22 | 24 | 2 | 4.53 | 65.9 | 85.9 | 5.15 | 0.15 | 5.3 | 0 | 45 | 38.41 | -39.7 | 0 | 0 | 0 | Battery-supported
2025-12-18 23:00 | 352 | 12 | Summer | 23 | 24 | 0.3 | 13.8 | 65 | 43.9 | 2.63 | 120 | 122.63 | 0 | 45 | 66.98 | 77.63 | 0 | 0 | 0 | Normal
2025-12-19 | 353 | 12 | Summer | 0 | 24 | -4.4 | 15.35 | 51.1 | 0 | 0 | 120 | 120 | 4.4 | 45 | 94.58 | 75 | 0 | 0 | 0 | Normal
2025-12-19 01:00 | 353 | 12 | Summer | 1 | 24 | 2.5 | 12.01 | 72.3 | 39.2 | 2.35 | 86.26 | 88.61 | 0 | 45 | 95 | 1.14 | 0 | 0 | 0 | Normal
2025-12-19 02:00 | 353 | 12 | Summer | 2 | 24 | 0.1 | 7.32 | 100 | 42.4 | 2.54 | 7.8 | 10.34 | 0 | 45 | 81.14 | -34.66 | 0 | 0 | 0 | Battery-supported
2025-12-19 03:00 | 353 | 12 | Summer | 3 | 24 | -3.8 | 3.97 | 40.9 | 174 | 10.44 | 0.01 | 10.45 | 3.8 | 45 | 67.32 | -34.55 | 0 | 0 | 0 | Battery-supported
2025-12-19 04:00 | 353 | 12 | Summer | 4 | 24 | -5.3 | 2.65 | 65.6 | 166.6 | 10 | 0 | 10 | 5.3 | 45 | 53.32 | -35 | 0 | 0 | 0 | Battery-supported
2025-12-19 05:00 | 353 | 12 | Summer | 5 | 24 | -2.2 | 5.66 | 37.9 | 285.8 | 17.15 | 1.41 | 18.56 | 2.2 | 45 | 42.74 | -26.44 | 0 | 0 | 0 | Battery-supported
2025-12-19 06:00 | 353 | 12 | Summer | 6 | 24 | -4.2 | 2.69 | 6.5 | 441.2 | 26.47 | 0 | 26.47 | 4.2 | 45 | 35.33 | -18.53 | 0 | 0 | 0 | Battery-supported
2025-12-19 07:00 | 353 | 12 | Summer | 7 | 24 | -3 | 18.36 | 55 | 305.7 | 18.34 | 120 | 138.34 | 3 | 45 | 69.68 | 93.34 | 0 | 0 | 0 | Normal
2025-12-19 08:00 | 353 | 12 | Summer | 8 | 24 | -2.1 | 5.48 | 53.9 | 338.5 | 20.31 | 1.09 | 21.4 | 2.1 | 45 | 60.24 | -23.6 | 0 | 0 | 0 | Battery-supported
2025-12-19 09:00 | 353 | 12 | Summer | 9 | 24 | -5 | 5.9 | 17 | 528.7 | 31.72 | 1.93 | 33.65 | 5 | 49.09 | 54.06 | -15.44 | 0 | 0 | 0 | Battery-supported
2025-12-19 10:00 | 353 | 12 | Summer | 10 | 24 | -6 | 10.9 | 72.1 | 291.2 | 17.47 | 56.72 | 74.19 | 6 | 46.88 | 64.11 | 27.31 | 0 | 0 | 0 | Normal
2025-12-19 11:00 | 353 | 12 | Summer | 11 | 24 | -2.5 | 2.36 | 75.1 | 284.1 | 17.05 | 0 | 17.05 | 2.5 | 49.19 | 51.26 | -32.14 | 0 | 0 | 0 | Battery-supported
2025-12-19 12:00 | 353 | 12 | Summer | 12 | 24 | -4.2 | 6 | 23.1 | 542.5 | 32.55 | 2.19 | 34.74 | 4.2 | 53.26 | 43.85 | -18.52 | 0 | 0 | 0 | Battery-supported
2025-12-19 13:00 | 353 | 12 | Summer | 13 | 24 | -2.3 | 6.96 | 69.5 | 311.5 | 18.69 | 5.8 | 24.49 | 2.3 | 50.13 | 33.59 | -25.64 | 0 | 0 | 0 | Battery-supported
2025-12-19 14:00 | 353 | 12 | Summer | 14 | 24 | -5.2 | 2.74 | 57.9 | 358.6 | 21.52 | 0 | 21.52 | 5.2 | 48.44 | 22.82 | -26.92 | 0 | 0 | 0 | Battery-supported
2025-12-19 15:00 | 353 | 12 | Summer | 15 | 24 | -2.4 | 3.79 | 69.7 | 289.2 | 17.35 | 0 | 17.35 | 2.4 | 45.2 | 15 | -19.56 | 8.29 | 3.043 | 0 | Diesel-backup
2025-12-19 16:00 | 353 | 12 | Summer | 16 | 24 | 0 | 4.76 | 48.1 | 363 | 21.78 | 0.28 | 22.06 | 0 | 45 | 15 | 0 | 22.94 | 7.989 | 0 | Diesel-backup
2025-12-19 17:00 | 353 | 12 | Summer | 17 | 24 | 0.1 | 12.27 | 52.2 | 316.7 | 19 | 94.41 | 113.41 | 0 | 45 | 40.17 | 68.41 | 0 | 0 | 0 | Normal
2025-12-19 18:00 | 353 | 12 | Summer | 18 | 24 | -2.7 | 15.08 | 36 | 338.7 | 20.32 | 120 | 140.32 | 2.7 | 49.24 | 73.69 | 91.08 | 0 | 0 | 0 | Normal
2025-12-19 19:00 | 353 | 12 | Summer | 19 | 24 | -3.4 | 9.09 | 13.7 | 358.3 | 21.5 | 24.45 | 45.95 | 3.4 | 45 | 74.04 | 0.95 | 0 | 0 | 0 | Normal
2025-12-19 20:00 | 353 | 12 | Summer | 20 | 24 | -0.7 | 6.64 | 20.8 | 276.8 | 16.61 | 4.33 | 20.94 | 0.7 | 45 | 64.42 | -24.06 | 0 | 0 | 0 | Battery-supported
2025-12-19 21:00 | 353 | 12 | Summer | 21 | 24 | 0.4 | 13.79 | 65.1 | 128.4 | 7.7 | 120 | 127.7 | 0 | 45 | 94.85 | 82.7 | 0 | 0 | 0 | Normal
2025-12-19 22:00 | 353 | 12 | Summer | 22 | 24 | -0.1 | 11.35 | 42.3 | 116 | 6.96 | 67.7 | 74.66 | 0.1 | 45 | 95 | 0.4 | 0 | 0 | 0 | Normal
2025-12-19 23:00 | 353 | 12 | Summer | 23 | 24 | -2.3 | 21.49 | 82.8 | 32.4 | 1.94 | 120 | 121.94 | 2.3 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-12-20 | 354 | 12 | Summer | 0 | 24 | -0.8 | 2.06 | 63 | 0 | 0 | 0 | 0 | 0.8 | 45 | 77 | -45 | 0 | 0 | 0 | Battery-supported
2025-12-20 01:00 | 354 | 12 | Summer | 1 | 24 | 1.5 | 7.09 | 33.7 | 64 | 3.84 | 6.48 | 10.32 | 0 | 45 | 63.13 | -34.68 | 0 | 0 | 0 | Battery-supported
2025-12-20 02:00 | 354 | 12 | Summer | 2 | 24 | -1.7 | 4.92 | 44.7 | 112.9 | 6.77 | 0.4 | 7.17 | 1.7 | 45 | 48 | -37.83 | 0 | 0 | 0 | Battery-supported
2025-12-20 03:00 | 354 | 12 | Summer | 3 | 24 | -6.2 | 2.33 | 47.4 | 161.8 | 9.71 | 0 | 9.71 | 6.2 | 45 | 33.88 | -35.29 | 0 | 0 | 0 | Battery-supported
2025-12-20 04:00 | 354 | 12 | Summer | 4 | 24 | -2.5 | 7.13 | 38.9 | 232.2 | 13.93 | 6.69 | 20.62 | 2.5 | 45 | 24.13 | -24.38 | 0 | 0 | 0 | Battery-supported
2025-12-20 05:00 | 354 | 12 | Summer | 5 | 24 | 1.3 | 20.22 | 45.2 | 264 | 15.84 | 120 | 135.84 | 0 | 45 | 57.56 | 90.84 | 0 | 0 | 0 | Normal
2025-12-20 06:00 | 354 | 12 | Summer | 6 | 24 | -6.3 | 3.34 | 57.7 | 263.1 | 15.79 | 0 | 15.79 | 6.3 | 45 | 45.87 | -29.21 | 0 | 0 | 0 | Battery-supported
2025-12-20 07:00 | 354 | 12 | Summer | 7 | 24 | -3.6 | 25.9 | 20.4 | 440.7 | 26.44 | 120 | 146.44 | 3.6 | 45 | 83.2 | 101.44 | 0 | 0 | 0 | Normal
2025-12-20 08:00 | 354 | 12 | Summer | 8 | 24 | -4.2 | 11.48 | 64.9 | 291.4 | 17.48 | 71.12 | 88.6 | 4.2 | 45 | 95 | 32.06 | 0 | 0 | 0 | Normal
2025-12-20 09:00 | 354 | 12 | Summer | 9 | 24 | -3.4 | 14.08 | 69.7 | 289.2 | 17.35 | 120 | 137.35 | 3.4 | 48.13 | 95 | 0 | 0 | 0 | 0 | Normal
2025-12-20 10:00 | 354 | 12 | Summer | 10 | 24 | -3.1 | 14.02 | 39.8 | 444.4 | 26.66 | 120 | 146.66 | 3.1 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-12-20 11:00 | 354 | 12 | Summer | 11 | 24 | -0.7 | 9.1 | 80.6 | 257.3 | 15.44 | 24.58 | 40.02 | 0.7 | 45.75 | 92.71 | -5.73 | 0 | 0 | 0 | Battery-supported
2025-12-20 12:00 | 354 | 12 | Summer | 12 | 24 | -2.7 | 5.43 | 33.3 | 492.1 | 29.53 | 1.01 | 30.54 | 2.7 | 46.44 | 86.35 | -15.9 | 0 | 0 | 0 | Battery-supported
2025-12-20 13:00 | 354 | 12 | Summer | 13 | 24 | 0.2 | 2.67 | 35.2 | 478.5 | 28.71 | 0 | 28.71 | 0 | 47.06 | 79.01 | -18.35 | 0 | 0 | 0 | Battery-supported
2025-12-20 14:00 | 354 | 12 | Summer | 14 | 24 | -2.4 | 3.38 | 43.9 | 425.1 | 25.51 | 0 | 25.51 | 2.4 | 45 | 71.21 | -19.49 | 0 | 0 | 0 | Battery-supported
2025-12-20 15:00 | 354 | 12 | Summer | 15 | 24 | -2.6 | 9.81 | 30.2 | 468.7 | 28.12 | 35.16 | 63.28 | 2.6 | 45 | 77.94 | 18.28 | 0 | 0 | 0 | Normal
2025-12-20 16:00 | 354 | 12 | Summer | 16 | 24 | -2.9 | 5.57 | 65.5 | 289.1 | 17.35 | 1.24 | 18.59 | 2.9 | 49.5 | 65.58 | -30.91 | 0 | 0 | 0 | Battery-supported
2025-12-20 17:00 | 354 | 12 | Summer | 17 | 24 | -5.1 | 3.66 | 93.4 | 155.8 | 9.35 | 0 | 9.35 | 5.1 | 45.41 | 51.15 | -36.06 | 0 | 0 | 0 | Battery-supported
2025-12-20 18:00 | 354 | 12 | Summer | 18 | 24 | -0.3 | 8.22 | 35.5 | 340.2 | 20.41 | 14.72 | 35.13 | 0.3 | 45 | 47.2 | -9.87 | 0 | 0 | 0 | Battery-supported
2025-12-20 19:00 | 354 | 12 | Summer | 19 | 24 | 3.8 | 8.79 | 45.3 | 263.7 | 15.82 | 20.72 | 36.54 | 0 | 45.1 | 43.78 | -8.56 | 0 | 0 | 0 | Battery-supported
2025-12-20 20:00 | 354 | 12 | Summer | 20 | 24 | 0.3 | 10.91 | 52.7 | 198.3 | 11.9 | 56.95 | 68.85 | 0 | 45 | 52.56 | 23.85 | 0 | 0 | 0 | Normal
2025-12-20 21:00 | 354 | 12 | Summer | 21 | 24 | 0.8 | 4.19 | 38.9 | 177.8 | 10.67 | 0.05 | 10.72 | 0 | 45 | 38.84 | -34.28 | 0 | 0 | 0 | Battery-supported
2025-12-20 22:00 | 354 | 12 | Summer | 22 | 24 | -1.8 | 6.61 | 34.9 | 125.3 | 7.52 | 4.21 | 11.73 | 1.8 | 45 | 25.54 | -33.27 | 0 | 0 | 0 | Battery-supported
2025-12-20 23:00 | 354 | 12 | Summer | 23 | 24 | -1.7 | 4.27 | 36.6 | 62.1 | 3.73 | 0.06 | 3.79 | 1.7 | 45 | 15 | -26.34 | 14.87 | 5.332 | 0 | Diesel-backup
2025-12-21 | 355 | 12 | Summer | 0 | 24 | 0.8 | 2.99 | 64.2 | 0 | 0 | 0 | 0 | 0 | 45 | 15 | 0 | 45 | 14.4 | 0 | Diesel-backup
2025-12-21 01:00 | 355 | 12 | Summer | 1 | 24 | 2.7 | 12.72 | 43.7 | 57.5 | 3.45 | 109.7 | 113.15 | 0 | 45 | 40.08 | 68.15 | 0 | 0 | 0 | Normal
2025-12-21 02:00 | 355 | 12 | Summer | 2 | 24 | 1.2 | 12.23 | 42.5 | 115.6 | 6.94 | 93.12 | 100.06 | 0 | 45 | 60.34 | 55.06 | 0 | 0 | 0 | Normal
2025-12-21 03:00 | 355 | 12 | Summer | 3 | 24 | -0.7 | 2.11 | 73.8 | 112.1 | 6.73 | 0 | 6.73 | 0.7 | 45 | 45.03 | -38.27 | 0 | 0 | 0 | Battery-supported
2025-12-21 04:00 | 355 | 12 | Summer | 4 | 24 | -2.8 | 7.33 | 16.9 | 286.4 | 17.18 | 7.86 | 25.04 | 2.8 | 45 | 37.05 | -19.96 | 0 | 0 | 0 | Battery-supported
2025-12-21 05:00 | 355 | 12 | Summer | 5 | 24 | -2.7 | 13.79 | 16.5 | 349.9 | 20.99 | 120 | 140.99 | 2.7 | 45 | 72.37 | 95.99 | 0 | 0 | 0 | Normal
2025-12-21 06:00 | 355 | 12 | Summer | 6 | 24 | -5.1 | 11.11 | 7.8 | 436.6 | 26.2 | 61.68 | 87.88 | 5.1 | 45 | 88.15 | 42.88 | 0 | 0 | 0 | Normal
2025-12-21 07:00 | 355 | 12 | Summer | 7 | 24 | -6.7 | 3.88 | 32.7 | 392.7 | 23.56 | 0.01 | 23.57 | 6.7 | 45 | 79.58 | -21.43 | 0 | 0 | 0 | Battery-supported
2025-12-21 08:00 | 355 | 12 | Summer | 8 | 24 | -6.1 | 14.66 | 87.5 | 195.2 | 11.71 | 120 | 131.71 | 6.1 | 45 | 95 | 41.9 | 0 | 0 | 0 | Normal
2025-12-21 09:00 | 355 | 12 | Summer | 9 | 24 | -3.4 | 13.8 | 75.6 | 262.2 | 15.73 | 120 | 135.73 | 3.4 | 49.78 | 95 | 0 | 0 | 0 | 0 | Normal
2025-12-21 10:00 | 355 | 12 | Summer | 10 | 24 | -4 | 8.59 | 57.3 | 361.3 | 21.68 | 18.46 | 40.14 | 4 | 45 | 93.06 | -4.86 | 0 | 0 | 0 | Battery-supported
2025-12-21 11:00 | 355 | 12 | Summer | 11 | 24 | -6.4 | 6.01 | 65.4 | 331.3 | 19.88 | 2.21 | 22.09 | 6.4 | 46.54 | 83.28 | -24.45 | 0 | 0 | 0 | Battery-supported
2025-12-21 12:00 | 355 | 12 | Summer | 12 | 24 | -2.9 | 3.84 | 12.6 | 593.8 | 35.63 | 0.01 | 35.64 | 2.9 | 45.85 | 79.19 | -10.21 | 0 | 0 | 0 | Battery-supported
2025-12-21 13:00 | 355 | 12 | Summer | 13 | 24 | -3.2 | 7.09 | 86.2 | 229.7 | 13.78 | 6.48 | 20.26 | 3.2 | 45 | 69.3 | -24.74 | 0 | 0 | 0 | Battery-supported
2025-12-21 14:00 | 355 | 12 | Summer | 14 | 24 | -4.7 | 15.87 | 76.1 | 271.8 | 16.31 | 120 | 136.31 | 4.7 | 45.32 | 95 | 69.85 | 0 | 0 | 0 | Normal
2025-12-21 15:00 | 355 | 12 | Summer | 15 | 24 | -2.5 | 3.95 | 33.2 | 455.2 | 27.31 | 0.01 | 27.32 | 2.5 | 45 | 87.93 | -17.68 | 0 | 0 | 0 | Battery-supported
2025-12-21 16:00 | 355 | 12 | Summer | 16 | 24 | -2.1 | 16.68 | 80.6 | 224.7 | 13.48 | 120 | 133.48 | 2.1 | 45 | 95 | 19.22 | 0 | 0 | 0 | Normal
2025-12-21 17:00 | 355 | 12 | Summer | 17 | 24 | -2.4 | 10.8 | 28.5 | 409.3 | 24.56 | 54.45 | 79.01 | 2.4 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-12-21 18:00 | 355 | 12 | Summer | 18 | 24 | 1.2 | 7.08 | 78.2 | 191.8 | 11.51 | 6.42 | 17.93 | 0 | 45 | 84.17 | -27.07 | 0 | 0 | 0 | Battery-supported
2025-12-21 19:00 | 355 | 12 | Summer | 19 | 24 | -4.8 | 13.87 | 39.5 | 281 | 16.86 | 120 | 136.86 | 4.8 | 47.01 | 95 | 29.42 | 0 | 0 | 0 | Normal
2025-12-21 20:00 | 355 | 12 | Summer | 20 | 24 | -5 | 6.95 | 76.9 | 138.8 | 8.33 | 5.75 | 14.08 | 5 | 53.75 | 79.13 | -39.67 | 0 | 0 | 0 | Battery-supported
2025-12-21 21:00 | 355 | 12 | Summer | 21 | 24 | -0.6 | 6.3 | 59.2 | 139.6 | 8.38 | 3.07 | 11.45 | 0.6 | 45 | 65.71 | -33.55 | 0 | 0 | 0 | Battery-supported
2025-12-21 22:00 | 355 | 12 | Summer | 22 | 24 | -0.6 | 12.4 | 90.8 | 54.2 | 3.25 | 98.67 | 101.92 | 0.6 | 45 | 86.66 | 56.92 | 0 | 0 | 0 | Normal
2025-12-21 23:00 | 355 | 12 | Summer | 23 | 24 | -0.1 | 0.62 | 36.3 | 62.3 | 3.74 | 0 | 3.74 | 0.1 | 45 | 70.15 | -41.26 | 0 | 0 | 0 | Battery-supported
2025-12-22 | 356 | 12 | Summer | 0 | 24 | -2.4 | 7.25 | 78 | 0 | 0 | 7.38 | 7.38 | 2.4 | 45 | 55.11 | -37.62 | 0 | 0 | 0 | Battery-supported
2025-12-22 01:00 | 356 | 12 | Summer | 1 | 24 | -3.6 | 6.95 | 15.2 | 75.8 | 4.55 | 5.75 | 10.3 | 3.6 | 45 | 41.23 | -34.7 | 0 | 0 | 0 | Battery-supported
2025-12-22 02:00 | 356 | 12 | Summer | 2 | 24 | -2 | 4.82 | 40.6 | 118.1 | 7.09 | 0.32 | 7.41 | 2 | 45 | 26.19 | -37.59 | 0 | 0 | 0 | Battery-supported
2025-12-22 03:00 | 356 | 12 | Summer | 3 | 24 | -3.4 | 6.21 | 39.7 | 176.3 | 10.58 | 2.79 | 13.37 | 3.4 | 45 | 15 | -27.98 | 3.65 | 1.363 | 0 | Diesel-backup
2025-12-22 04:00 | 356 | 12 | Summer | 4 | 24 | 0.7 | 17.79 | 41.9 | 224.9 | 13.49 | 120 | 133.49 | 0 | 45 | 47.56 | 88.49 | 0 | 0 | 0 | Normal
2025-12-22 05:00 | 356 | 12 | Summer | 5 | 24 | -3.8 | 1.07 | 48.7 | 253.6 | 15.22 | 0 | 15.22 | 3.8 | 45 | 35.65 | -29.78 | 0 | 0 | 0 | Battery-supported
2025-12-22 06:00 | 356 | 12 | Summer | 6 | 24 | -3.4 | 3.86 | 65.2 | 237.1 | 14.23 | 0.01 | 14.24 | 3.4 | 45 | 23.35 | -30.76 | 0 | 0 | 0 | Battery-supported
2025-12-22 07:00 | 356 | 12 | Summer | 7 | 24 | 2 | 4.35 | 61.4 | 280.9 | 16.85 | 0.09 | 16.94 | 0 | 45 | 15 | -20.87 | 7.19 | 2.648 | 0 | Diesel-backup
2025-12-22 08:00 | 356 | 12 | Summer | 8 | 24 | -3.9 | 6.62 | 87.1 | 196.9 | 11.81 | 4.25 | 16.06 | 3.9 | 45.29 | 15 | 0 | 29.23 | 9.944 | 0 | Diesel-backup
2025-12-22 09:00 | 356 | 12 | Summer | 9 | 24 | -2.2 | 5.96 | 47.7 | 389.3 | 23.36 | 2.08 | 25.44 | 2.2 | 45 | 15 | 0 | 19.56 | 6.896 | 0 | Diesel-backup
2025-12-22 10:00 | 356 | 12 | Summer | 10 | 24 | -1.9 | 7.95 | 38 | 453.2 | 27.19 | 12.33 | 39.52 | 1.9 | 45 | 15 | 0 | 5.48 | 2.031 | 0 | Diesel-backup
2025-12-22 11:00 | 356 | 12 | Summer | 11 | 24 | -1.5 | 1.52 | 0 | 650.3 | 39.02 | 0 | 39.02 | 1.5 | 51.33 | 15 | 0 | 12.31 | 4.454 | 0 | Diesel-backup
2025-12-22 12:00 | 356 | 12 | Summer | 12 | 24 | -2.1 | 7.87 | 80.1 | 261.7 | 15.7 | 11.68 | 27.38 | 2.1 | 45 | 15 | 0 | 17.62 | 6.256 | 0 | Diesel-backup
2025-12-22 13:00 | 356 | 12 | Summer | 13 | 24 | -2 | 17.71 | 68.3 | 317.2 | 19.03 | 120 | 139.03 | 2 | 49.24 | 48.04 | 89.79 | 0 | 0 | 0 | Normal
2025-12-22 14:00 | 356 | 12 | Summer | 14 | 24 | -1.8 | 7.25 | 27.3 | 504 | 30.24 | 7.38 | 37.62 | 1.8 | 46.07 | 44.66 | -8.45 | 0 | 0 | 0 | Battery-supported
2025-12-22 15:00 | 356 | 12 | Summer | 15 | 24 | -2.9 | 6.09 | 27.3 | 482.1 | 28.93 | 2.43 | 31.36 | 2.9 | 48.2 | 37.93 | -16.84 | 0 | 0 | 0 | Battery-supported
2025-12-22 16:00 | 356 | 12 | Summer | 16 | 24 | -0.5 | 6.72 | 72.4 | 259.5 | 15.57 | 4.67 | 20.24 | 0.5 | 45 | 28.02 | -24.76 | 0 | 0 | 0 | Battery-supported
2025-12-22 17:00 | 356 | 12 | Summer | 17 | 24 | 3.5 | 5.59 | 49.5 | 327.4 | 19.64 | 1.28 | 20.92 | 0 | 45 | 18.39 | -24.08 | 0 | 0 | 0 | Battery-supported
2025-12-22 18:00 | 356 | 12 | Summer | 18 | 24 | 2 | 10.77 | 57.3 | 264.3 | 15.86 | 53.78 | 69.64 | 0 | 45 | 27.46 | 24.64 | 0 | 0 | 0 | Normal
2025-12-22 19:00 | 356 | 12 | Summer | 19 | 24 | 0.1 | 8.64 | 55.1 | 234.4 | 14.06 | 19.01 | 33.07 | 0 | 45 | 22.69 | -11.93 | 0 | 0 | 0 | Battery-supported
2025-12-22 20:00 | 356 | 12 | Summer | 20 | 24 | 1.4 | 8.29 | 70.7 | 154.1 | 9.25 | 15.38 | 24.63 | 0 | 45 | 15 | -19.22 | 1.15 | 0.434 | 0 | Diesel-backup
2025-12-22 21:00 | 356 | 12 | Summer | 21 | 24 | -2.5 | 13.84 | 57.3 | 143.1 | 8.59 | 120 | 128.59 | 2.5 | 45 | 45.76 | 83.59 | 0 | 0 | 0 | Normal
2025-12-22 22:00 | 356 | 12 | Summer | 22 | 24 | -1.3 | 10.84 | 17.4 | 147.7 | 8.86 | 55.35 | 64.21 | 1.3 | 45 | 52.83 | 19.21 | 0 | 0 | 0 | Normal
2025-12-22 23:00 | 356 | 12 | Summer | 23 | 24 | 1.1 | 1.07 | 37.6 | 61.5 | 3.69 | 0 | 3.69 | 0 | 45 | 36.31 | -41.31 | 0 | 0 | 0 | Battery-supported
2025-12-23 | 357 | 12 | Summer | 0 | 24 | 2.1 | 5.51 | 57.5 | 0 | 0 | 1.14 | 1.14 | 0 | 45 | 18.76 | -43.86 | 0 | 0 | 0 | Battery-supported
2025-12-23 01:00 | 357 | 12 | Summer | 1 | 24 | -3.2 | 2.87 | 32.3 | 64.9 | 3.89 | 0 | 3.89 | 3.2 | 45 | 15 | -9.41 | 31.7 | 10.685 | 0 | Diesel-backup
2025-12-23 02:00 | 357 | 12 | Summer | 2 | 24 | -3 | 4.24 | 59 | 94.7 | 5.68 | 0.06 | 5.74 | 3 | 45 | 15 | 0 | 39.26 | 12.852 | 0 | Diesel-backup
2025-12-23 03:00 | 357 | 12 | Summer | 3 | 24 | 2.5 | 4.87 | 64.6 | 129.4 | 7.76 | 0.36 | 8.12 | 0 | 45 | 15 | 0 | 36.88 | 12.185 | 0 | Diesel-backup
2025-12-23 04:00 | 357 | 12 | Summer | 4 | 24 | -2.5 | 4.15 | 60.3 | 179.7 | 10.78 | 0.04 | 10.82 | 2.5 | 45 | 15 | 0 | 34.18 | 11.411 | 0 | Diesel-backup
2025-12-23 05:00 | 357 | 12 | Summer | 5 | 24 | 1 | 11.1 | 78 | 165.7 | 9.94 | 61.44 | 71.38 | 0 | 45 | 24.71 | 26.38 | 0 | 0 | 0 | Normal
2025-12-23 06:00 | 357 | 12 | Summer | 6 | 24 | -2.8 | 10.07 | 41.2 | 320.5 | 19.23 | 39.69 | 58.92 | 2.8 | 45 | 29.83 | 13.92 | 0 | 0 | 0 | Normal
2025-12-23 07:00 | 357 | 12 | Summer | 7 | 24 | -2.8 | 5.49 | 20.5 | 440.6 | 26.44 | 1.1 | 27.54 | 2.8 | 45 | 22.85 | -17.46 | 0 | 0 | 0 | Battery-supported
2025-12-23 08:00 | 357 | 12 | Summer | 8 | 24 | -4.1 | 9.85 | 75.4 | 246.7 | 14.8 | 35.84 | 50.64 | 4.1 | 50.51 | 22.89 | 0.13 | 0 | 0 | 0 | Normal
2025-12-23 09:00 | 357 | 12 | Summer | 9 | 24 | -1.3 | 9.12 | 24.2 | 495.8 | 29.75 | 24.84 | 54.59 | 1.3 | 53.76 | 23.2 | 0.83 | 0 | 0 | 0 | Normal
2025-12-23 10:00 | 357 | 12 | Summer | 10 | 24 | -0.2 | 7.6 | 66.5 | 317.5 | 19.05 | 9.65 | 28.7 | 0.2 | 45 | 16.68 | -16.3 | 0 | 0 | 0 | Battery-supported
2025-12-23 11:00 | 357 | 12 | Summer | 11 | 24 | -5.3 | 6.46 | 43 | 440.5 | 26.43 | 3.63 | 30.06 | 5.3 | 58.3 | 15 | -4.2 | 24.04 | 8.338 | 0 | Diesel-backup
2025-12-23 12:00 | 357 | 12 | Summer | 12 | 24 | -3.5 | 2.06 | 60.6 | 358 | 21.48 | 0 | 21.48 | 3.5 | 46.29 | 15 | 0 | 24.81 | 8.58 | 0 | Diesel-backup
2025-12-23 13:00 | 357 | 12 | Summer | 13 | 24 | -0.3 | 11.77 | 91.8 | 202.7 | 12.16 | 79.16 | 91.32 | 0.3 | 47.23 | 31.23 | 44.09 | 0 | 0 | 0 | Normal
2025-12-23 14:00 | 357 | 12 | Summer | 14 | 24 | -2.2 | 6.94 | 42.6 | 431.2 | 25.87 | 5.7 | 31.57 | 2.2 | 45 | 25.85 | -13.43 | 0 | 0 | 0 | Battery-supported
2025-12-23 15:00 | 357 | 12 | Summer | 15 | 24 | -2.6 | 8.13 | 33.7 | 452.8 | 27.17 | 13.89 | 41.06 | 2.6 | 45 | 24.28 | -3.94 | 0 | 0 | 0 | Battery-supported
2025-12-23 16:00 | 357 | 12 | Summer | 16 | 24 | 1 | 7.8 | 62.4 | 302.2 | 18.13 | 11.13 | 29.26 | 0 | 45 | 17.98 | -15.74 | 0 | 0 | 0 | Battery-supported
2025-12-23 17:00 | 357 | 12 | Summer | 17 | 24 | 1.6 | 4.99 | 94.5 | 151.7 | 9.1 | 0.46 | 9.56 | 0 | 48.18 | 15 | -7.45 | 31.17 | 10.525 | 0 | Diesel-backup
2025-12-23 18:00 | 357 | 12 | Summer | 18 | 24 | -1.6 | 4.81 | 55.3 | 271.4 | 16.28 | 0.31 | 16.59 | 1.6 | 45 | 15 | 0 | 28.41 | 9.694 | 0 | Diesel-backup
2025-12-23 19:00 | 357 | 12 | Summer | 19 | 24 | 0 | 6.2 | 19.1 | 342.2 | 20.53 | 2.75 | 23.28 | 0 | 46.63 | 15 | 0 | 23.35 | 8.119 | 0 | Diesel-backup
2025-12-23 20:00 | 357 | 12 | Summer | 20 | 24 | -3.1 | 10.99 | 47.9 | 210.1 | 12.61 | 58.81 | 71.42 | 3.1 | 47.52 | 23.8 | 23.9 | 0 | 0 | 0 | Normal
2025-12-23 21:00 | 357 | 12 | Summer | 21 | 24 | -2.4 | 6.6 | 52.4 | 152.4 | 9.14 | 4.17 | 13.31 | 2.4 | 45 | 15 | -21.99 | 9.7 | 3.543 | 0 | Diesel-backup
2025-12-23 22:00 | 357 | 12 | Summer | 22 | 24 | -0.4 | 1.8 | 29.5 | 132.2 | 7.93 | 0 | 7.93 | 0.4 | 45 | 15 | 0 | 37.07 | 12.239 | 0 | Diesel-backup
2025-12-23 23:00 | 357 | 12 | Summer | 23 | 24 | -0.8 | 8.6 | 92.2 | 26.4 | 1.58 | 18.57 | 20.15 | 0.8 | 45 | 15 | 0 | 24.85 | 8.593 | 0 | Diesel-backup
2025-12-24 | 358 | 12 | Summer | 0 | 24 | -3.2 | 5.12 | 72 | 0 | 0 | 0.6 | 0.6 | 3.2 | 45 | 15 | 0 | 44.4 | 14.242 | 0 | Diesel-backup
2025-12-24 01:00 | 358 | 12 | Summer | 1 | 24 | -3 | 4.11 | 8.2 | 80.3 | 4.82 | 0.03 | 4.85 | 3 | 45 | 15 | 0 | 40.15 | 13.097 | 0 | Diesel-backup
2025-12-24 02:00 | 358 | 12 | Summer | 2 | 24 | -4.2 | 10.38 | 51.2 | 104.6 | 6.28 | 45.58 | 51.86 | 4.2 | 45 | 17.52 | 6.86 | 0 | 0 | 0 | Normal
2025-12-24 03:00 | 358 | 12 | Summer | 3 | 24 | -1.2 | 10.34 | 33.7 | 187.6 | 11.26 | 44.79 | 56.05 | 1.2 | 45 | 21.59 | 11.05 | 0 | 0 | 0 | Normal
2025-12-24 04:00 | 358 | 12 | Summer | 4 | 24 | -6.9 | 7.62 | 22.9 | 271.6 | 16.3 | 9.79 | 26.09 | 6.9 | 45 | 15 | -16.48 | 2.43 | 0.911 | 0 | Diesel-backup
2025-12-24 05:00 | 358 | 12 | Summer | 5 | 24 | -5.1 | 5.92 | 42.5 | 272 | 16.32 | 1.98 | 18.3 | 5.1 | 45 | 15 | 0 | 26.7 | 9.169 | 0 | Diesel-backup
2025-12-24 06:00 | 358 | 12 | Summer | 6 | 24 | -7.2 | 5.26 | 11.1 | 425.3 | 25.52 | 0.76 | 26.28 | 7.2 | 45 | 15 | 0 | 18.72 | 6.62 | 0 | Diesel-backup
2025-12-24 07:00 | 358 | 12 | Summer | 7 | 24 | -2.4 | 2.89 | 42.9 | 352.9 | 21.17 | 0 | 21.17 | 2.4 | 45 | 15 | 0 | 23.83 | 8.271 | 0 | Diesel-backup
2025-12-24 08:00 | 358 | 12 | Summer | 8 | 24 | -7.3 | 1.09 | 23.5 | 468 | 28.08 | 0 | 28.08 | 7.3 | 52.51 | 15 | 0 | 24.43 | 8.461 | 0 | Diesel-backup
2025-12-24 09:00 | 358 | 12 | Summer | 9 | 24 | -3.2 | 5.49 | 35.1 | 446.5 | 26.79 | 1.1 | 27.89 | 3.2 | 45.27 | 15 | 0 | 17.38 | 6.176 | 0 | Diesel-backup
2025-12-24 10:00 | 358 | 12 | Summer | 10 | 24 | 0.5 | 5.57 | 36.3 | 460.9 | 27.65 | 1.24 | 28.89 | 0 | 45 | 15 | 0 | 16.11 | 5.751 | 0 | Diesel-backup
2025-12-24 11:00 | 358 | 12 | Summer | 11 | 24 | 0.8 | 15.51 | 60.4 | 355.9 | 21.35 | 120 | 141.35 | 0 | 45.26 | 50.36 | 96.09 | 0 | 0 | 0 | Normal
2025-12-24 12:00 | 358 | 12 | Summer | 12 | 24 | -6.6 | 3.93 | 84.1 | 242.1 | 14.53 | 0.01 | 14.54 | 6.6 | 48.94 | 36.6 | -34.4 | 0 | 0 | 0 | Battery-supported
2025-12-24 13:00 | 358 | 12 | Summer | 13 | 24 | -1.6 | 13.76 | 64.3 | 336.6 | 20.2 | 120 | 140.2 | 1.6 | 45 | 71.63 | 95.2 | 0 | 0 | 0 | Normal
2025-12-24 14:00 | 358 | 12 | Summer | 14 | 24 | -4 | 5.01 | 51.3 | 389.9 | 23.39 | 0.48 | 23.87 | 4 | 48.84 | 61.65 | -24.97 | 0 | 0 | 0 | Battery-supported
2025-12-24 15:00 | 358 | 12 | Summer | 15 | 24 | -4.1 | 7.57 | 89.8 | 197.8 | 11.87 | 9.44 | 21.31 | 4.1 | 48.11 | 50.93 | -26.8 | 0 | 0 | 0 | Battery-supported
2025-12-24 16:00 | 358 | 12 | Summer | 16 | 24 | -1.3 | 8.5 | 65.6 | 288.5 | 17.31 | 17.5 | 34.81 | 1.3 | 52.35 | 43.91 | -17.54 | 0 | 0 | 0 | Battery-supported
2025-12-24 17:00 | 358 | 12 | Summer | 17 | 24 | 1.9 | 9.19 | 67.1 | 258.7 | 15.52 | 25.78 | 41.3 | 0 | 46.64 | 41.77 | -5.34 | 0 | 0 | 0 | Battery-supported
2025-12-24 18:00 | 358 | 12 | Summer | 18 | 24 | 0.8 | 4.61 | 89.6 | 152.1 | 9.13 | 0.19 | 9.32 | 0 | 45 | 27.5 | -35.68 | 0 | 0 | 0 | Battery-supported
2025-12-24 19:00 | 358 | 12 | Summer | 19 | 24 | -2 | 5.82 | 60.3 | 218.8 | 13.13 | 1.75 | 14.88 | 2 | 46.32 | 15 | -31.26 | 0.18 | 0.069 | 0 | Diesel-backup
2025-12-24 20:00 | 358 | 12 | Summer | 20 | 24 | 1.2 | 7.13 | 31 | 251.8 | 15.11 | 6.69 | 21.8 | 0 | 45 | 15 | 0 | 23.2 | 8.071 | 0 | Diesel-backup
2025-12-24 21:00 | 358 | 12 | Summer | 21 | 24 | -5.3 | 4.63 | 87 | 87.2 | 5.23 | 0.2 | 5.43 | 5.3 | 45 | 15 | 0 | 39.57 | 12.937 | 0 | Diesel-backup
2025-12-24 22:00 | 358 | 12 | Summer | 22 | 24 | -2.2 | 13.02 | 57 | 97.2 | 5.83 | 120 | 125.83 | 2.2 | 45 | 44.75 | 80.83 | 0 | 0 | 0 | Normal
2025-12-24 23:00 | 358 | 12 | Summer | 23 | 24 | -2.6 | 22.04 | 54.8 | 50.4 | 3.02 | 120 | 123.02 | 2.6 | 45 | 73.46 | 78.02 | 0 | 0 | 0 | Normal
2025-12-25 | 359 | 12 | Summer | 0 | 24 | -0.9 | 8.35 | 96.2 | 0 | 0 | 15.97 | 15.97 | 0.9 | 45 | 61.84 | -29.03 | 0 | 0 | 0 | Battery-supported
2025-12-25 01:00 | 359 | 12 | Summer | 1 | 24 | -1.8 | 8.3 | 55.7 | 49.8 | 2.99 | 15.48 | 18.47 | 1.8 | 45 | 51.23 | -26.53 | 0 | 0 | 0 | Battery-supported
2025-12-25 02:00 | 359 | 12 | Summer | 2 | 24 | -2.1 | 12.48 | 26.9 | 135.5 | 8.13 | 101.35 | 109.48 | 2.1 | 45 | 74.96 | 64.48 | 0 | 0 | 0 | Normal
2025-12-25 03:00 | 359 | 12 | Summer | 3 | 24 | -2.5 | 10.99 | 17.4 | 218.3 | 13.1 | 58.81 | 71.91 | 2.5 | 45 | 84.86 | 26.91 | 0 | 0 | 0 | Normal
2025-12-25 04:00 | 359 | 12 | Summer | 4 | 24 | -2.5 | 6.93 | 40.4 | 228.5 | 13.71 | 5.65 | 19.36 | 2.5 | 45 | 74.61 | -25.64 | 0 | 0 | 0 | Battery-supported
2025-12-25 05:00 | 359 | 12 | Summer | 5 | 24 | -1.6 | 16.98 | 32.9 | 300.8 | 18.05 | 120 | 138.05 | 1.6 | 45 | 95 | 55.41 | 0 | 0 | 0 | Normal
2025-12-25 06:00 | 359 | 12 | Summer | 6 | 24 | -2.7 | 4.77 | 62.9 | 245 | 14.7 | 0.29 | 14.99 | 2.7 | 45 | 83 | -30.01 | 0 | 0 | 0 | Battery-supported
2025-12-25 07:00 | 359 | 12 | Summer | 7 | 24 | -3.9 | 10.42 | 73.9 | 232.1 | 13.93 | 46.38 | 60.31 | 3.9 | 45 | 88.63 | 15.31 | 0 | 0 | 0 | Normal
2025-12-25 08:00 | 359 | 12 | Summer | 8 | 24 | -2.4 | 5.78 | 13.9 | 508.8 | 30.53 | 1.66 | 32.19 | 2.4 | 45 | 83.51 | -12.81 | 0 | 0 | 0 | Battery-supported
2025-12-25 09:00 | 359 | 12 | Summer | 9 | 24 | -1.4 | 8.92 | 21.2 | 509.6 | 30.58 | 22.28 | 52.86 | 1.4 | 50.82 | 84.26 | 2.04 | 0 | 0 | 0 | Normal
2025-12-25 10:00 | 359 | 12 | Summer | 10 | 24 | -4.3 | 5.42 | 28.5 | 498 | 29.88 | 0.99 | 30.87 | 4.3 | 52.16 | 75.74 | -21.29 | 0 | 0 | 0 | Battery-supported
2025-12-25 11:00 | 359 | 12 | Summer | 11 | 24 | -3 | 16.67 | 74 | 289.3 | 17.36 | 120 | 137.36 | 3 | 48.13 | 95 | 52.33 | 0 | 0 | 0 | Normal
2025-12-25 12:00 | 359 | 12 | Summer | 12 | 24 | 0 | 12.83 | 43.8 | 440.4 | 26.42 | 113.67 | 140.09 | 0 | 45 | 95 | 0 | 0 | 0 | 0 | Normal
2025-12-25 13:00 | 359 | 12 | Summer | 13 | 24 | -4.6 | 8.66 | 74.7 | 285.9 | 17.15 | 19.23 | 36.38 | 4.6 | 51.88 | 88.8 | -15.5 | 0 | 0 | 0 | Battery-supported
2025-12-25 14:00 | 359 | 12 | Summer | 14 | 24 | 2.2 | 11.09 | 46.5 | 412.5 | 24.75 | 61.2 | 85.95 | 0 | 50.56 | 95 | 16.85 | 0 | 0 | 0 | Normal
2025-12-25 15:00 | 359 | 12 | Summer | 15 | 24 | -4.3 | 3.93 | 50.7 | 375.5 | 22.53 | 0.01 | 22.54 | 4.3 | 46.24 | 85.52 | -23.7 | 0 | 0 | 0 | Battery-supported
2025-12-25 16:00 | 359 | 12 | Summer | 16 | 24 | -1.8 | 2.54 | 34.4 | 421.3 | 25.28 | 0 | 25.28 | 1.8 | 50.64 | 75.38 | -25.36 | 0 | 0 | 0 | Battery-supported
2025-12-25 17:00 | 359 | 12 | Summer | 17 | 24 | -2.8 | 4.65 | 44.5 | 346.6 | 20.8 | 0.21 | 21.01 | 2.8 | 49.77 | 63.87 | -28.76 | 0 | 0 | 0 | Battery-supported
2025-12-25 18:00 | 359 | 12 | Summer | 18 | 24 | 4.3 | 16.4 | 68.9 | 224.3 | 13.46 | 120 | 133.46 | 0 | 48.02 | 95 | 84.59 | 0 | 0 | 0 | Normal
2025-12-25 19:00 | 359 | 12 | Summer | 19 | 24 | -1.4 | 5.41 | 59.2 | 221.9 | 13.31 | 0.98 | 14.29 | 1.4 | 47.55 | 81.7 | -33.26 | 0 | 0 | 0 | Battery-supported
2025-12-25 20:00 | 359 | 12 | Summer | 20 | 24 | -1.4 | 11.5 | 52.5 | 198.9 | 11.93 | 71.66 | 83.59 | 1.4 | 45 | 95 | 36.15 | 0 | 0 | 0 | Normal
2025-12-25 21:00 | 359 | 12 | Summer | 21 | 24 | -1.1 | 6.1 | 30.8 | 193.1 | 11.59 | 2.46 | 14.05 | 1.1 | 45 | 82.62 | -30.95 | 0 | 0 | 0 | Battery-supported
2025-12-25 22:00 | 359 | 12 | Summer | 22 | 24 | -0.3 | 6.33 | 36.7 | 123 | 7.38 | 3.17 | 10.55 | 0.3 | 45 | 68.84 | -34.45 | 0 | 0 | 0 | Battery-supported
2025-12-25 23:00 | 359 | 12 | Summer | 23 | 24 | -1.4 | 5.46 | 91.9 | 26.6 | 1.6 | 1.05 | 2.65 | 1.4 | 45 | 51.9 | -42.35 | 0 | 0 | 0 | Battery-supported
2025-12-26 | 360 | 12 | Summer | 0 | 24 | -1.2 | 5.22 | 84.8 | 0 | 0 | 0.71 | 0.71 | 1.2 | 45 | 34.18 | -44.29 | 0 | 0 | 0 | Battery-supported
2025-12-26 01:00 | 360 | 12 | Summer | 1 | 24 | -9.1 | 11.01 | 71.4 | 39.8 | 2.39 | 59.28 | 61.67 | 9.1 | 45 | 40.32 | 16.67 | 0 | 0 | 0 | Normal
2025-12-26 02:00 | 360 | 12 | Summer | 2 | 24 | -1.6 | 5.28 | 20.6 | 143.6 | 8.62 | 0.79 | 9.41 | 1.6 | 45 | 26.08 | -35.59 | 0 | 0 | 0 | Battery-supported
2025-12-26 03:00 | 360 | 12 | Summer | 3 | 24 | -2.1 | 5.19 | 75.3 | 109.3 | 6.56 | 0.68 | 7.24 | 2.1 | 45 | 15 | -27.71 | 10.05 | 3.667 | 0 | Diesel-backup
2025-12-26 04:00 | 360 | 12 | Summer | 4 | 24 | -0.2 | 6.97 | 69.3 | 157.5 | 9.45 | 5.85 | 15.3 | 0.2 | 45 | 15 | 0 | 29.7 | 10.086 | 0 | Diesel-backup
2025-12-26 05:00 | 360 | 12 | Summer | 5 | 24 | 0.1 | 5.81 | 18.3 | 344.6 | 20.68 | 1.73 | 22.41 | 0 | 45 | 15 | 0 | 22.59 | 7.877 | 0 | Diesel-backup
2025-12-26 06:00 | 360 | 12 | Summer | 6 | 24 | -3.4 | 4.15 | 48.5 | 295 | 17.7 | 0.04 | 17.74 | 3.4 | 45 | 15 | 0 | 27.26 | 9.342 | 0 | Diesel-backup
2025-12-26 07:00 | 360 | 12 | Summer | 7 | 24 | -1.4 | 10.33 | 90.8 | 166.2 | 9.97 | 44.59 | 54.56 | 1.4 | 45 | 18.52 | 9.56 | 0 | 0 | 0 | Normal
2025-12-26 08:00 | 360 | 12 | Summer | 8 | 24 | -5.6 | 7.93 | 80.3 | 225.9 | 13.55 | 12.17 | 25.72 | 5.6 | 47.11 | 15 | -8.8 | 12.59 | 4.553 | 0 | Diesel-backup
2025-12-26 09:00 | 360 | 12 | Summer | 9 | 24 | -1.5 | 5.07 | 21.2 | 509.5 | 30.57 | 0.54 | 31.11 | 1.5 | 45 | 15 | 0 | 13.89 | 4.998 | 0 | Diesel-backup
2025-12-26 10:00 | 360 | 12 | Summer | 10 | 24 | -4.3 | 4.15 | 21.9 | 529.5 | 31.77 | 0.04 | 31.81 | 4.3 | 46.78 | 15 | 0 | 14.97 | 5.366 | 0 | Diesel-backup
2025-12-26 11:00 | 360 | 12 | Summer | 11 | 24 | -5.4 | 12.6 | 91.3 | 205.1 | 12.31 | 105.47 | 117.78 | 5.4 | 51.5 | 39.39 | 66.28 | 0 | 0 | 0 | Normal
2025-12-26 12:00 | 360 | 12 | Summer | 12 | 24 | -2.9 | 3.1 | 59.1 | 365.2 | 21.91 | 0 | 21.91 | 2.9 | 46.35 | 29.62 | -24.44 | 0 | 0 | 0 | Battery-supported
2025-12-26 13:00 | 360 | 12 | Summer | 13 | 24 | 1 | 1.14 | 21 | 547.8 | 32.87 | 0 | 32.87 | 0 | 45 | 24.76 | -12.13 | 0 | 0 | 0 | Battery-supported
2025-12-26 14:00 | 360 | 12 | Summer | 14 | 24 | -1.3 | 9.56 | 73.8 | 283 | 16.98 | 31.15 | 48.13 | 1.3 | 50.68 | 23.74 | -2.55 | 0 | 0 | 0 | Battery-supported
2025-12-26 15:00 | 360 | 12 | Summer | 15 | 24 | 2 | 1.74 | 42.6 | 412.5 | 24.75 | 0 | 24.75 | 0 | 45 | 15.64 | -20.25 | 0 | 0 | 0 | Battery-supported
2025-12-26 16:00 | 360 | 12 | Summer | 16 | 24 | -2.6 | 7.39 | 28.5 | 446.5 | 26.79 | 8.24 | 35.03 | 2.6 | 50.15 | 15 | -1.61 | 13.51 | 4.869 | 0 | Diesel-backup
2025-12-26 17:00 | 360 | 12 | Summer | 17 | 24 | 1.7 | 7.51 | 47.6 | 334.5 | 20.07 | 9.02 | 29.09 | 0 | 45 | 15 | 0 | 15.91 | 5.684 | 0 | Diesel-backup
2025-12-26 18:00 | 360 | 12 | Summer | 18 | 24 | -1.8 | 2.73 | 71.5 | 214.9 | 12.89 | 0 | 12.89 | 1.8 | 54.91 | 15 | 0 | 42.02 | 13.607 | 0 | Diesel-backup
2025-12-26 19:00 | 360 | 12 | Summer | 19 | 24 | 0.2 | 2.89 | 6.6 | 379.4 | 22.76 | 0 | 22.76 | 0 | 45 | 15 | 0 | 22.24 | 7.765 | 0 | Diesel-backup
2025-12-26 20:00 | 360 | 12 | Summer | 20 | 24 | 0.3 | 7.66 | 82.4 | 125.4 | 7.52 | 10.08 | 17.6 | 0 | 45 | 15 | 0 | 27.4 | 9.385 | 0 | Diesel-backup
2025-12-26 21:00 | 360 | 12 | Summer | 21 | 24 | 1.2 | 2.83 | 99.3 | 64.1 | 3.85 | 0 | 3.85 | 0 | 45 | 15 | 0 | 41.15 | 13.371 | 0 | Diesel-backup
2025-12-26 22:00 | 360 | 12 | Summer | 22 | 24 | 0.1 | 14.11 | 38.2 | 121.1 | 7.27 | 120 | 127.27 | 0 | 45 | 45.28 | 82.27 | 0 | 0 | 0 | Normal
2025-12-26 23:00 | 360 | 12 | Summer | 23 | 24 | -2.3 | 5.11 | 29.3 | 66.8 | 4.01 | 0.58 | 4.59 | 2.3 | 45.89 | 28.76 | -41.3 | 0 | 0 | 0 | Battery-supported
2025-12-27 | 361 | 12 | Summer | 0 | 24 | 1.1 | 15.46 | 17.6 | 0 | 0 | 120 | 120 | 0 | 45 | 56.36 | 75 | 0 | 0 | 0 | Normal
2025-12-27 01:00 | 361 | 12 | Summer | 1 | 24 | 2.6 | 13.6 | 26.8 | 68.4 | 4.1 | 120 | 124.1 | 0 | 45 | 85.46 | 79.1 | 0 | 0 | 0 | Normal
2025-12-27 02:00 | 361 | 12 | Summer | 2 | 24 | -2.9 | 6.47 | 1.9 | 167.4 | 10.04 | 3.67 | 13.71 | 2.9 | 45 | 72.95 | -31.29 | 0 | 0 | 0 | Battery-supported
2025-12-27 03:00 | 361 | 12 | Summer | 3 | 24 | -6.1 | 7.8 | 90.1 | 81.3 | 4.88 | 11.13 | 16.01 | 6.1 | 45 | 61.35 | -28.99 | 0 | 0 | 0 | Battery-supported
2025-12-27 04:00 | 361 | 12 | Summer | 4 | 24 | -1.3 | 12.16 | 89.8 | 107.1 | 6.43 | 90.9 | 97.33 | 1.3 | 45 | 80.61 | 52.33 | 0 | 0 | 0 | Normal
2025-12-27 05:00 | 361 | 12 | Summer | 5 | 24 | -3.4 | 3.45 | 39.5 | 281 | 16.86 | 0 | 16.86 | 3.4 | 45 | 69.35 | -28.14 | 0 | 0 | 0 | Battery-supported
2025-12-27 06:00 | 361 | 12 | Summer | 6 | 24 | -3.2 | 5.39 | 50.8 | 287 | 17.22 | 0.94 | 18.16 | 3.2 | 45 | 58.62 | -26.84 | 0 | 0 | 0 | Battery-supported
2025-12-27 07:00 | 361 | 12 | Summer | 7 | 24 | -1.9 | 15.25 | 46.6 | 338.6 | 20.32 | 120 | 140.32 | 1.9 | 45 | 93.7 | 95.32 | 0 | 0 | 0 | Normal
2025-12-27 08:00 | 361 | 12 | Summer | 8 | 24 | -4.1 | 11.37 | 30.5 | 438 | 26.28 | 68.22 | 94.5 | 4.1 | 47.78 | 95 | 3.55 | 0 | 0 | 0 | Normal
2025-12-27 09:00 | 361 | 12 | Summer | 9 | 24 | -3.7 | 5.99 | 80.4 | 240.6 | 14.44 | 2.16 | 16.6 | 3.7 | 45 | 83.64 | -28.4 | 0 | 0 | 0 | Battery-supported
2025-12-27 10:00 | 361 | 12 | Summer | 10 | 24 | -3.2 | 7.84 | 20.9 | 534.4 | 32.06 | 11.44 | 43.5 | 3.2 | 45.92 | 82.67 | -2.42 | 0 | 0 | 0 | Battery-supported
2025-12-27 11:00 | 361 | 12 | Summer | 11 | 24 | 0.5 | 4.55 | 16.3 | 570.9 | 34.25 | 0.16 | 34.41 | 0 | 47.59 | 77.4 | -13.18 | 0 | 0 | 0 | Battery-supported
2025-12-27 12:00 | 361 | 12 | Summer | 12 | 24 | -2.3 | 5.68 | 61.7 | 352.5 | 21.15 | 1.45 | 22.6 | 2.3 | 45 | 68.44 | -22.4 | 0 | 0 | 0 | Battery-supported
2025-12-27 13:00 | 361 | 12 | Summer | 13 | 24 | -4.7 | 9.46 | 41.4 | 448.5 | 26.91 | 29.63 | 56.54 | 4.7 | 50.97 | 70.49 | 5.57 | 0 | 0 | 0 | Normal
2025-12-27 14:00 | 361 | 12 | Summer | 14 | 24 | -4.3 | 5.69 | 20.3 | 537.3 | 32.24 | 1.47 | 33.71 | 4.3 | 46.43 | 65.4 | -12.72 | 0 | 0 | 0 | Battery-supported
2025-12-27 15:00 | 361 | 12 | Summer | 15 | 24 | -0.9 | 10.33 | 39.2 | 428.1 | 25.69 | 44.59 | 70.28 | 0.9 | 45 | 74.7 | 25.28 | 0 | 0 | 0 | Normal
2025-12-27 16:00 | 361 | 12 | Summer | 16 | 24 | -3.4 | 2.82 | 91.2 | 179.7 | 10.78 | 0 | 10.78 | 3.4 | 47.79 | 59.9 | -37.01 | 0 | 0 | 0 | Battery-supported
2025-12-27 17:00 | 361 | 12 | Summer | 17 | 24 | -4 | 9.4 | 33.9 | 388.2 | 23.29 | 28.75 | 52.04 | 4 | 46.93 | 61.78 | 5.11 | 0 | 0 | 0 | Normal
2025-12-27 18:00 | 361 | 12 | Summer | 18 | 24 | 1.1 | 3.72 | 71.7 | 214.2 | 12.85 | 0 | 12.85 | 0 | 48.45 | 47.54 | -35.6 | 0 | 0 | 0 | Battery-supported
2025-12-27 19:00 | 361 | 12 | Summer | 19 | 24 | 1.3 | 6.36 | 86 | 141.8 | 8.51 | 3.27 | 11.78 | 0 | 45 | 34.25 | -33.22 | 0 | 0 | 0 | Battery-supported
2025-12-27 20:00 | 361 | 12 | Summer | 20 | 24 | -0.9 | 4.37 | 32.2 | 248.9 | 14.93 | 0.09 | 15.02 | 0.9 | 49.06 | 20.64 | -34.04 | 0 | 0 | 0 | Battery-supported
2025-12-27 21:00 | 361 | 12 | Summer | 21 | 24 | 0.5 | 9.42 | 5.4 | 240.8 | 14.45 | 29.04 | 43.49 | 0 | 45 | 20.03 | -1.51 | 0 | 0 | 0 | Battery-supported
2025-12-27 22:00 | 361 | 12 | Summer | 22 | 24 | 0.1 | 3.03 | 54.4 | 100.5 | 6.03 | 0 | 6.03 | 0 | 45 | 15 | -12.58 | 26.39 | 9.072 | 0 | Diesel-backup
2025-12-27 23:00 | 361 | 12 | Summer | 23 | 24 | 0.7 | 10.4 | 25.9 | 69 | 4.14 | 45.98 | 50.12 | 0 | 45 | 16.88 | 5.12 | 0 | 0 | 0 | Normal
2025-12-28 | 362 | 12 | Summer | 0 | 24 | 0.5 | 6.91 | 91 | 0 | 0 | 5.55 | 5.55 | 0 | 45 | 15 | -4.71 | 34.74 | 11.573 | 0 | Diesel-backup
2025-12-28 01:00 | 362 | 12 | Summer | 1 | 24 | -6.9 | 6.03 | 77.3 | 36 | 2.16 | 2.27 | 4.43 | 6.9 | 45.68 | 15 | 0 | 41.25 | 13.398 | 0 | Diesel-backup
2025-12-28 02:00 | 362 | 12 | Summer | 2 | 24 | -2.1 | 4.75 | 94.3 | 49.7 | 2.98 | 0.27 | 3.25 | 2.1 | 45 | 15 | 0 | 41.75 | 13.534 | 0 | Diesel-backup
2025-12-28 03:00 | 362 | 12 | Summer | 3 | 24 | -0.8 | 5.32 | 66.5 | 125.8 | 7.55 | 0.84 | 8.39 | 0.8 | 45 | 15 | 0 | 36.61 | 12.108 | 0 | Diesel-backup
2025-12-28 04:00 | 362 | 12 | Summer | 4 | 24 | -3.2 | 13.41 | 46 | 214.9 | 12.89 | 120 | 132.89 | 3.2 | 45 | 47.34 | 87.89 | 0 | 0 | 0 | Normal
2025-12-28 05:00 | 362 | 12 | Summer | 5 | 24 | -2.6 | 4.69 | 55.7 | 232.5 | 13.95 | 0.24 | 14.19 | 2.6 | 45 | 35.02 | -30.81 | 0 | 0 | 0 | Battery-supported
2025-12-28 06:00 | 362 | 12 | Summer | 6 | 24 | -1.2 | 13.47 | 47.5 | 298.5 | 17.91 | 120 | 137.91 | 1.2 | 45 | 69.21 | 92.91 | 0 | 0 | 0 | Normal
2025-12-28 07:00 | 362 | 12 | Summer | 7 | 24 | -2.8 | 15.9 | 77.1 | 219.3 | 13.16 | 120 | 133.16 | 2.8 | 45 | 95 | 70.08 | 0 | 0 | 0 | Normal
2025-12-28 08:00 | 362 | 12 | Summer | 8 | 24 | 0.2 | 5.94 | 19.6 | 484.5 | 29.07 | 2.03 | 31.1 | 0 | 45 | 89.44 | -13.9 | 0 | 0 | 0 | Battery-supported
2025-12-28 09:00 | 362 | 12 | Summer | 9 | 24 | -0.5 | 2.53 | 76.4 | 258.8 | 15.53 | 0 | 15.53 | 0.5 | 45 | 77.65 | -29.47 | 0 | 0 | 0 | Battery-supported
2025-12-28 10:00 | 362 | 12 | Summer | 10 | 24 | -3.1 | 11.65 | 89.3 | 209.3 | 12.56 | 75.77 | 88.33 | 3.1 | 49.55 | 91.92 | 38.78 | 0 | 0 | 0 | Normal
2025-12-28 11:00 | 362 | 12 | Summer | 11 | 24 | -3.1 | 11.57 | 73.6 | 291.6 | 17.5 | 73.56 | 91.06 | 3.1 | 45 | 95 | 8.36 | 0 | 0 | 0 | Normal
2025-12-28 12:00 | 362 | 12 | Summer | 12 | 24 | -8.6 | 13.58 | 63.1 | 345.6 | 20.74 | 120 | 140.74 | 8.6 | 47.69 | 95 | 0 | 0 | 0 | 0 | Normal
2025-12-28 13:00 | 362 | 12 | Summer | 13 | 24 | -2.7 | 6.62 | 32.4 | 492.5 | 29.55 | 4.25 | 33.8 | 2.7 | 45 | 90.52 | -11.2 | 0 | 0 | 0 | Battery-supported
2025-12-28 14:00 | 362 | 12 | Summer | 14 | 24 | -4.5 | 8.29 | 77 | 267.8 | 16.07 | 15.38 | 31.45 | 4.5 | 48.57 | 83.67 | -17.12 | 0 | 0 | 0 | Battery-supported
2025-12-28 15:00 | 362 | 12 | Summer | 15 | 24 | -0.7 | 5.28 | 25 | 492.3 | 29.54 | 0.79 | 30.33 | 0.7 | 45 | 77.8 | -14.67 | 0 | 0 | 0 | Battery-supported
2025-12-28 16:00 | 362 | 12 | Summer | 16 | 24 | -0.5 | 5.14 | 68.3 | 277 | 16.62 | 0.62 | 17.24 | 0.5 | 45 | 66.7 | -27.76 | 0 | 0 | 0 | Battery-supported
2025-12-28 17:00 | 362 | 12 | Summer | 17 | 24 | 1 | 8.05 | 39.4 | 366.7 | 22 | 13.18 | 35.18 | 0 | 45 | 62.77 | -9.82 | 0 | 0 | 0 | Battery-supported
2025-12-28 18:00 | 362 | 12 | Summer | 18 | 24 | 2.8 | 12.2 | 12.3 | 421.1 | 25.27 | 92.17 | 117.44 | 0 | 45 | 89.43 | 72.44 | 0 | 0 | 0 | Normal
2025-12-28 19:00 | 362 | 12 | Summer | 19 | 24 | -0.2 | 10.73 | 22.4 | 332.3 | 19.94 | 52.9 | 72.84 | 0.2 | 45 | 95 | 15.14 | 0 | 0 | 0 | Normal
2025-12-28 20:00 | 362 | 12 | Summer | 20 | 24 | 4.9 | 7.09 | 12.4 | 297.5 | 17.85 | 6.48 | 24.33 | 0 | 45 | 86.73 | -20.67 | 0 | 0 | 0 | Battery-supported
2025-12-28 21:00 | 362 | 12 | Summer | 21 | 24 | 0.4 | 12.77 | 27.4 | 199.5 | 11.97 | 111.49 | 123.46 | 0 | 45 | 95 | 22.47 | 0 | 0 | 0 | Normal
2025-12-28 22:00 | 362 | 12 | Summer | 22 | 24 | -3.2 | 3.07 | 97 | 46.3 | 2.78 | 0 | 2.78 | 3.2 | 45 | 78.11 | -42.22 | 0 | 0 | 0 | Battery-supported
2025-12-28 23:00 | 362 | 12 | Summer | 23 | 24 | -1.7 | 23.11 | 62.5 | 45.5 | 2.73 | 120 | 122.73 | 1.7 | 45 | 95 | 45.89 | 0 | 0 | 0 | Normal
2025-12-29 | 363 | 12 | Summer | 0 | 24 | -1.6 | 3.29 | 72 | 0 | 0 | 0 | 0 | 1.6 | 45 | 77 | -45 | 0 | 0 | 0 | Battery-supported
2025-12-29 01:00 | 363 | 12 | Summer | 1 | 24 | 0.2 | 6.74 | 1.3 | 84.8 | 5.09 | 4.76 | 9.85 | 0 | 45 | 62.94 | -35.15 | 0 | 0 | 0 | Battery-supported
2025-12-29 02:00 | 363 | 12 | Summer | 2 | 24 | -3.6 | 7.96 | 19.6 | 144.8 | 8.69 | 12.42 | 21.11 | 3.6 | 45 | 53.38 | -23.89 | 0 | 0 | 0 | Battery-supported
2025-12-29 03:00 | 363 | 12 | Summer | 3 | 24 | -2.6 | 8.14 | 45.8 | 164.8 | 9.89 | 13.98 | 23.87 | 2.6 | 45 | 44.93 | -21.13 | 0 | 0 | 0 | Battery-supported
2025-12-29 04:00 | 363 | 12 | Summer | 4 | 24 | -2.6 | 12.05 | 65.3 | 167.4 | 10.04 | 87.48 | 97.52 | 2.6 | 45 | 64.26 | 52.52 | 0 | 0 | 0 | Normal
2025-12-29 05:00 | 363 | 12 | Summer | 5 | 24 | -3.6 | 4.07 | 41.3 | 275.8 | 16.55 | 0.03 | 16.58 | 3.6 | 45 | 52.89 | -28.42 | 0 | 0 | 0 | Battery-supported
2025-12-29 06:00 | 363 | 12 | Summer | 6 | 24 | -1 | 8.45 | 34.4 | 344.3 | 20.66 | 16.98 | 37.64 | 1 | 45 | 49.95 | -7.36 | 0 | 0 | 0 | Battery-supported
2025-12-29 07:00 | 363 | 12 | Summer | 7 | 24 | -1.5 | 10.23 | 37.5 | 374 | 22.44 | 42.66 | 65.1 | 1.5 | 45 | 57.34 | 20.1 | 0 | 0 | 0 | Normal
2025-12-29 08:00 | 363 | 12 | Summer | 8 | 24 | -0.4 | 13.02 | 24.2 | 465 | 27.9 | 120 | 147.9 | 0.4 | 45 | 95 | 102.33 | 0 | 0 | 0 | Normal
2025-12-29 09:00 | 363 | 12 | Summer | 9 | 24 | -3.7 | 5.9 | 49.6 | 380.4 | 22.82 | 1.93 | 24.75 | 3.7 | 45.21 | 86.82 | -20.46 | 0 | 0 | 0 | Battery-supported
2025-12-29 10:00 | 363 | 12 | Summer | 10 | 24 | -0.2 | 7.54 | 79.6 | 255.5 | 15.33 | 9.23 | 24.56 | 0.2 | 51.36 | 76.1 | -26.8 | 0 | 0 | 0 | Battery-supported
2025-12-29 11:00 | 363 | 12 | Summer | 11 | 24 | -5.6 | 6.96 | 80.4 | 258.1 | 15.49 | 5.8 | 21.29 | 5.6 | 49.94 | 64.64 | -28.65 | 0 | 0 | 0 | Battery-supported
2025-12-29 12:00 | 363 | 12 | Summer | 12 | 24 | -5.3 | 9.95 | 53.4 | 393.2 | 23.59 | 37.56 | 61.15 | 5.3 | 50.22 | 68.66 | 10.93 | 0 | 0 | 0 | Normal
2025-12-29 13:00 | 363 | 12 | Summer | 13 | 24 | -4.6 | 9.99 | 12.4 | 589.9 | 35.39 | 38.26 | 73.65 | 4.6 | 45 | 79.2 | 28.65 | 0 | 0 | 0 | Normal
2025-12-29 14:00 | 363 | 12 | Summer | 14 | 24 | -1.5 | 5.75 | 35.3 | 465.8 | 27.95 | 1.59 | 29.54 | 1.5 | 45 | 73.02 | -15.46 | 0 | 0 | 0 | Battery-supported
2025-12-29 15:00 | 363 | 12 | Summer | 15 | 24 | 1.5 | 6.88 | 25.3 | 491.1 | 29.47 | 5.4 | 34.87 | 0 | 45 | 68.97 | -10.13 | 0 | 0 | 0 | Battery-supported
2025-12-29 16:00 | 363 | 12 | Summer | 16 | 24 | -2.1 | 7.18 | 41.2 | 392.7 | 23.56 | 6.98 | 30.54 | 2.1 | 45 | 63.18 | -14.46 | 0 | 0 | 0 | Battery-supported
2025-12-29 17:00 | 363 | 12 | Summer | 17 | 24 | -1.5 | 3.65 | 76.3 | 222.6 | 13.36 | 0 | 13.36 | 1.5 | 45.29 | 50.41 | -31.93 | 0 | 0 | 0 | Battery-supported
2025-12-29 18:00 | 363 | 12 | Summer | 18 | 24 | -0.7 | 8.72 | 77.5 | 194.2 | 11.65 | 19.91 | 31.56 | 0.7 | 45 | 45.03 | -13.44 | 0 | 0 | 0 | Battery-supported
2025-12-29 19:00 | 363 | 12 | Summer | 19 | 24 | 1.2 | 8.53 | 51.9 | 243.8 | 14.63 | 17.81 | 32.44 | 0 | 45 | 40.01 | -12.56 | 0 | 0 | 0 | Battery-supported
2025-12-29 20:00 | 363 | 12 | Summer | 20 | 24 | -1.1 | 3.68 | 29.5 | 255.3 | 15.32 | 0 | 15.32 | 1.1 | 45 | 28.14 | -29.68 | 0 | 0 | 0 | Battery-supported
2025-12-29 21:00 | 363 | 12 | Summer | 21 | 24 | -1.2 | 9.05 | 7.2 | 237.4 | 14.24 | 23.93 | 38.17 | 1.2 | 45 | 25.41 | -6.83 | 0 | 0 | 0 | Battery-supported
2025-12-29 22:00 | 363 | 12 | Summer | 22 | 24 | -3.2 | 24.9 | 62.6 | 90 | 5.4 | 120 | 125.4 | 3.2 | 45 | 54.99 | 80.4 | 0 | 0 | 0 | Normal
2025-12-29 23:00 | 363 | 12 | Summer | 23 | 24 | -1.7 | 4.36 | 21.4 | 71.9 | 4.31 | 0.09 | 4.4 | 1.7 | 45 | 38.75 | -40.6 | 0 | 0 | 0 | Battery-supported
2025-12-30 | 364 | 12 | Summer | 0 | 24 | 1.9 | 3.65 | 7.6 | 0 | 0 | 0 | 0 | 0 | 45 | 20.75 | -45 | 0 | 0 | 0 | Battery-supported
2025-12-30 01:00 | 364 | 12 | Summer | 1 | 24 | -0.9 | 10.14 | 26.3 | 68.7 | 4.12 | 40.97 | 45.09 | 0.9 | 45 | 20.79 | 0.09 | 0 | 0 | 0 | Normal
2025-12-30 02:00 | 364 | 12 | Summer | 2 | 24 | -3.1 | 5.72 | 59 | 94.6 | 5.68 | 1.53 | 7.21 | 3.1 | 45 | 15 | -14.46 | 23.33 | 8.111 | 0 | Diesel-backup
2025-12-30 03:00 | 364 | 12 | Summer | 3 | 24 | 0.9 | 12.06 | 38 | 179.6 | 10.78 | 87.79 | 98.57 | 0 | 45 | 34.71 | 53.57 | 0 | 0 | 0 | Normal
2025-12-30 04:00 | 364 | 12 | Summer | 4 | 24 | -3.5 | 6.68 | 35.5 | 240.6 | 14.44 | 4.5 | 18.94 | 3.5 | 45 | 24.29 | -26.06 | 0 | 0 | 0 | Battery-supported
2025-12-30 05:00 | 364 | 12 | Summer | 5 | 24 | 0.6 | 4.91 | 41.1 | 276.3 | 16.58 | 0.39 | 16.97 | 0 | 45 | 15 | -23.22 | 4.81 | 1.785 | 0 | Diesel-backup
2025-12-30 06:00 | 364 | 12 | Summer | 6 | 24 | 0.3 | 6.62 | 66.6 | 232.3 | 13.94 | 4.25 | 18.19 | 0 | 45 | 15 | 0 | 26.81 | 9.203 | 0 | Diesel-backup
2025-12-30 07:00 | 364 | 12 | Summer | 7 | 24 | -2.8 | 9.97 | 35.5 | 381.9 | 22.91 | 37.91 | 60.82 | 2.8 | 45 | 20.82 | 15.82 | 0 | 0 | 0 | Normal
2025-12-30 08:00 | 364 | 12 | Summer | 8 | 24 | -6.2 | 9.78 | 13.2 | 511.8 | 30.71 | 34.66 | 65.37 | 6.2 | 52.7 | 25.48 | 12.67 | 0 | 0 | 0 | Normal
2025-12-30 09:00 | 364 | 12 | Summer | 9 | 24 | 2.1 | 2.85 | 44.6 | 403.1 | 24.19 | 0 | 24.19 | 0 | 45 | 17.16 | -20.81 | 0 | 0 | 0 | Battery-supported
2025-12-30 10:00 | 364 | 12 | Summer | 10 | 24 | -1.9 | 9.96 | 52.9 | 382.4 | 22.94 | 37.73 | 60.67 | 1.9 | 45 | 22.93 | 15.67 | 0 | 0 | 0 | Normal
2025-12-30 11:00 | 364 | 12 | Summer | 11 | 24 | -3.2 | 7.29 | 48.1 | 415.7 | 24.94 | 7.62 | 32.56 | 3.2 | 45 | 17.95 | -12.44 | 0 | 0 | 0 | Battery-supported
2025-12-30 12:00 | 364 | 12 | Summer | 12 | 24 | -0.1 | 7.64 | 82.3 | 251.1 | 15.07 | 9.93 | 25 | 0.1 | 45 | 15 | -7.38 | 12.62 | 4.562 | 0 | Diesel-backup
2025-12-30 13:00 | 364 | 12 | Summer | 13 | 24 | -0.3 | 8.71 | 52.3 | 395.3 | 23.72 | 19.79 | 43.51 | 0.3 | 45 | 15 | 0 | 1.49 | 0.56 | 0 | Diesel-backup
2025-12-30 14:00 | 364 | 12 | Summer | 14 | 24 | 1.4 | 3.61 | 40.4 | 441.5 | 26.49 | 0 | 26.49 | 0 | 45 | 15 | 0 | 18.51 | 6.551 | 0 | Diesel-backup
2025-12-30 15:00 | 364 | 12 | Summer | 15 | 24 | -2.5 | 2.77 | 41.3 | 418.3 | 25.1 | 0 | 25.1 | 2.5 | 49.39 | 15 | 0 | 24.29 | 8.417 | 0 | Diesel-backup
2025-12-30 16:00 | 364 | 12 | Summer | 16 | 24 | 0 | 2.91 | 48.4 | 361.8 | 21.71 | 0 | 21.71 | 0 | 45 | 15 | 0 | 23.29 | 8.1 | 0 | Diesel-backup
2025-12-30 17:00 | 364 | 12 | Summer | 17 | 24 | -3 | 11.65 | 15.9 | 458.2 | 27.49 | 75.77 | 103.26 | 3 | 45 | 36.44 | 58.26 | 0 | 0 | 0 | Normal
2025-12-30 18:00 | 364 | 12 | Summer | 18 | 24 | 1.3 | 11.6 | 73.3 | 208.9 | 12.53 | 74.38 | 86.91 | 0 | 47.8 | 50.83 | 39.11 | 0 | 0 | 0 | Normal
2025-12-30 19:00 | 364 | 12 | Summer | 19 | 24 | -0.1 | 1.32 | 18 | 345.5 | 20.73 | 0 | 20.73 | 0.1 | 45 | 41.12 | -24.27 | 0 | 0 | 0 | Battery-supported
2025-12-30 20:00 | 364 | 12 | Summer | 20 | 24 | 0.7 | 6.86 | 93.8 | 97.3 | 5.84 | 5.31 | 11.15 | 0 | 47.64 | 26.53 | -36.49 | 0 | 0 | 0 | Battery-supported
2025-12-30 21:00 | 364 | 12 | Summer | 21 | 24 | -0.3 | 5.18 | 11.6 | 229.2 | 13.75 | 0.66 | 14.41 | 0.3 | 45 | 15 | -28.82 | 1.77 | 0.664 | 0 | Diesel-backup
2025-12-30 22:00 | 364 | 12 | Summer | 22 | 24 | -0.7 | 3.9 | 13 | 153.2 | 9.19 | 0.01 | 9.2 | 0.7 | 45 | 15 | 0 | 35.8 | 11.878 | 0 | Diesel-backup
2025-12-30 23:00 | 364 | 12 | Summer | 23 | 24 | -2.3 | 12.92 | 52.1 | 52.2 | 3.13 | 116.99 | 120.12 | 2.3 | 45 | 42.64 | 75.12 | 0 | 0 | 0 | Normal
2025-12-31 | 365 | 12 | Summer | 0 | 24 | 1.1 | 14.33 | 21.8 | 0 | 0 | 120 | 120 | 0 | 45 | 70.24 | 75 | 0 | 0 | 0 | Normal
2025-12-31 01:00 | 365 | 12 | Summer | 1 | 24 | 2.3 | 7.84 | 6.5 | 81.5 | 4.89 | 11.44 | 16.33 | 0 | 45 | 58.78 | -28.67 | 0 | 0 | 0 | Battery-supported
2025-12-31 02:00 | 365 | 12 | Summer | 2 | 24 | -2.6 | 4.98 | 75.2 | 74 | 4.44 | 0.45 | 4.89 | 2.6 | 45 | 42.73 | -40.11 | 0 | 0 | 0 | Battery-supported
2025-12-31 03:00 | 365 | 12 | Summer | 3 | 24 | -0.6 | 5.54 | 59.7 | 138.6 | 8.32 | 1.19 | 9.51 | 0.6 | 45 | 28.54 | -35.49 | 0 | 0 | 0 | Battery-supported
2025-12-31 04:00 | 365 | 12 | Summer | 4 | 24 | -1.2 | 3.49 | 73.2 | 147.9 | 8.87 | 0 | 8.87 | 1.2 | 45 | 15 | -33.84 | 2.29 | 0.858 | 0 | Diesel-backup
2025-12-31 05:00 | 365 | 12 | Summer | 5 | 24 | -2.4 | 5.48 | 10.2 | 368.7 | 22.12 | 1.09 | 23.21 | 2.4 | 45 | 15 | 0 | 21.79 | 7.62 | 0 | Diesel-backup
2025-12-31 06:00 | 365 | 12 | Summer | 6 | 24 | -6.1 | 4.22 | 42.2 | 317.1 | 19.03 | 0.05 | 19.08 | 6.1 | 45 | 15 | 0 | 25.92 | 8.927 | 0 | Diesel-backup
2025-12-31 07:00 | 365 | 12 | Summer | 7 | 24 | -5.7 | 13.81 | 18.9 | 446.7 | 26.8 | 120 | 146.8 | 5.7 | 49.43 | 50.83 | 97.37 | 0 | 0 | 0 | Normal
2025-12-31 08:00 | 365 | 12 | Summer | 8 | 24 | -4.6 | 2.11 | 78.4 | 234 | 14.04 | 0 | 14.04 | 4.6 | 45 | 38.45 | -30.96 | 0 | 0 | 0 | Battery-supported
2025-12-31 09:00 | 365 | 12 | Summer | 9 | 24 | -7.6 | 10.91 | 33.7 | 452.9 | 27.17 | 56.95 | 84.12 | 7.6 | 57.07 | 48.4 | 27.05 | 0 | 0 | 0 | Normal
2025-12-31 10:00 | 365 | 12 | Summer | 10 | 24 | 0.4 | 4.05 | 34.5 | 469.5 | 28.17 | 0.02 | 28.19 | 0 | 45 | 41.68 | -16.81 | 0 | 0 | 0 | Battery-supported
2025-12-31 11:00 | 365 | 12 | Summer | 11 | 24 | -1.6 | 9.9 | 64.7 | 334.7 | 20.08 | 36.69 | 56.77 | 1.6 | 46.78 | 45.35 | 9.99 | 0 | 0 | 0 | Normal
2025-12-31 12:00 | 365 | 12 | Summer | 12 | 24 | -2.2 | 6.45 | 1.6 | 648.1 | 38.89 | 3.59 | 42.48 | 2.2 | 49.45 | 42.57 | -6.97 | 0 | 0 | 0 | Battery-supported
2025-12-31 13:00 | 365 | 12 | Summer | 13 | 24 | -6.6 | 11 | 36.1 | 474.1 | 28.45 | 59.05 | 87.5 | 6.6 | 49.67 | 56.49 | 37.83 | 0 | 0 | 0 | Normal
2025-12-31 14:00 | 365 | 12 | Summer | 14 | 24 | -5.4 | 3 | 34.9 | 467.8 | 28.07 | 0 | 28.07 | 5.4 | 45 | 49.72 | -16.93 | 0 | 0 | 0 | Battery-supported
2025-12-31 15:00 | 365 | 12 | Summer | 15 | 24 | -1 | 4.85 | 15.1 | 537.3 | 32.24 | 0.34 | 32.58 | 1 | 45 | 44.75 | -12.42 | 0 | 0 | 0 | Battery-supported
2025-12-31 16:00 | 365 | 12 | Summer | 16 | 24 | 3.7 | 5.74 | 51.8 | 347.2 | 20.83 | 1.57 | 22.4 | 0 | 45 | 35.71 | -22.6 | 0 | 0 | 0 | Battery-supported
2025-12-31 17:00 | 365 | 12 | Summer | 17 | 24 | -1.9 | 7.24 | 9.2 | 484.5 | 29.07 | 7.32 | 36.39 | 1.9 | 48.51 | 30.86 | -12.12 | 0 | 0 | 0 | Battery-supported
2025-12-31 18:00 | 365 | 12 | Summer | 18 | 24 | 1.8 | 7.18 | 45.8 | 304.5 | 18.27 | 6.98 | 25.25 | 0 | 45 | 22.96 | -19.75 | 0 | 0 | 0 | Battery-supported
2025-12-31 19:00 | 365 | 12 | Summer | 19 | 24 | -1 | 3.47 | 58.9 | 222.9 | 13.37 | 0 | 13.37 | 1 | 45 | 15 | -19.9 | 11.73 | 4.253 | 0 | Diesel-backup
2025-12-31 20:00 | 365 | 12 | Summer | 20 | 24 | 0.2 | 2.86 | 69.3 | 157.6 | 9.46 | 0 | 9.46 | 0 | 45 | 15 | 0 | 35.54 | 11.803 | 0 | Diesel-backup
2025-12-31 21:00 | 365 | 12 | Summer | 21 | 24 | 2.7 | 5.95 | 45.3 | 165.6 | 9.94 | 2.06 | 12 | 0 | 45 | 15 | 0 | 33 | 11.067 | 0 | Diesel-backup
2025-12-31 22:00 | 365 | 12 | Summer | 22 | 24 | -0.9 | 6.71 | 94.5 | 49.4 | 2.96 | 4.63 | 7.59 | 0.9 | 45 | 15 | 0 | 37.41 | 12.335 | 0 | Diesel-backup
2025-12-31 23:00 | 365 | 12 | Summer | 23 | 24 | -1.9 | 5.76 | 41.9 | 58.7 | 3.52 | 1.62 | 5.14 | 1.9 | 45 | 15 | 0 | 39.86 | 13.017 | 0 | Diesel-backup

## Monthly_Summary
Month | Avg Solar Gen (kW) | Avg Wind Gen (kW) | Avg Total Load (kW) | Avg Diesel Gen (kW) | Total Fuel Consumed (L) | Hours with Energy Deficit
1 | 15.6421 | 25.8967 | 45.8125 | 8.0078 | 2024.947 | 0
2 | 11.6113 | 30.9083 | 46.2984 | 6.7069 | 1513.864 | 0
3 | 8.2711 | 31.6086 | 48.3914 | 11.29 | 2792.466 | 0
4 | 6.1744 | 42.1104 | 52.4254 | 7.9536 | 1886.114 | 0
5 | 4.2575 | 47.0843 | 58.0265 | 10.3497 | 2511.41 | 0
6 | 0 | 55.0242 | 62.6158 | 11.0565 | 2591.234 | 0
7 | 1.0211 | 55.1614 | 64.7055 | 11.4954 | 2783.667 | 0
8 | 6.049 | 57.7126 | 62.3671 | 4.9402 | 1209.996 | 0
9 | 6.8035 | 50.9653 | 58.0562 | 5.2104 | 1243.944 | 0
10 | 10.4823 | 42.2706 | 52.879 | 5.1916 | 1288.16 | 0
11 | 14.4592 | 33.8364 | 48.2767 | 4.8634 | 1188.665 | 0
12 | 15.7381 | 28.5988 | 46.2784 | 5.6224 | 1423.316 | 0
Annual | 8.3758 | 41.7648 | 53.8444 | 7.724 | 22457.783 | 0

## Data_Dictionary
Column | Unit | Description
Timestamp | datetime | Hour of the year, 1 Jan 2025 00:00 to 31 Dec 2025 23:00
Day_of_Year | 1-365 | Julian day number
Month | 1-12 | Calendar month
Season | text | Southern-hemisphere season (Summer/Autumn/Winter/Spring)
Hour | 0-23 | Hour of day, local
Daylight_Hours | hours | Hours of daylight that day, from solar-declination formula at the station's latitude (0 in polar night, 24 in polar day)
Temperature_C | deg C | Ambient air temperature, seasonal sinusoid + diurnal + random noise
Wind_Speed_mps | m/s | Wind speed, seasonally-varying stochastic model (higher/gustier in winter)
Cloud_Cover_pct | % | Cloud cover fraction, random
Solar_Irradiance_Wm2 | W/m2 | Surface solar irradiance after cloud attenuation; 0 during polar night
Solar_Generation_kW | kW | PV output from irradiance, panel efficiency, and snow/frost derate; capped at installed capacity
Wind_Generation_kW | kW | Turbine output from wind speed via a standard cubic power curve
Total_Renewable_kW | kW | Solar_Generation_kW + Wind_Generation_kW
Heating_Load_kW | kW | Electrical-equivalent heating demand, rises as temperature drops below 0C
Total_Load_kW | kW | Base load + heating load + daytime research/equipment load + noise
Battery_SOC_pct | % | Battery state of charge at end of hour, 0-100%
Battery_Charge_Discharge_kW | kW | Positive = charging from surplus renewables, negative = discharging to cover load
Diesel_Generation_kW | kW | Diesel generator output, dispatched only after renewables + battery are exhausted
Fuel_Consumption_L | litres | Diesel fuel burned that hour, from a specific-fuel-consumption curve with a part-load penalty
Energy_Deficit_kW | kW | Unmet load after renewables + battery + diesel (should be near 0; nonzero flags an undersized system)
System_Status | text | Normal / Battery-supported / Diesel-backup / Critical-load-only / Load-shed-risk — label your AI system could learn to reproduce or pre-empt